Part 1

Compliance

Section  1.1.   General

1.1.1. Application of this Code

1.1.1.1. Application of this Code

1)   This Code applies to any one or more of the following:

a) the design and construction of a new building,

b) the occupancy of any building,

c) a change in occupancy of any building,

d) an alteration of any building,

e) an addition to any building,

f) the demolition of any building,

g) the reconstruction of any building that has been damaged by fire, earthquake or other cause,

h) the correction of an unsafe condition in or about any building,

i) all parts of any building that are affected by a change in occupancy,

j) the work necessary to ensure safety in parts of a building

i) that remain after a demolition,

ii) that are affected by but that are not directly involved in alterations, or

iii) that are affected by but not directly involved in additions,

k) except as permitted by the British Columbia Fire Code, the installation, replacement, or alteration of materials or equipment regulated by this Code,

l) the work necessary to ensure safety in a relocated building during and after relocation,

m) safety during construction of a building, including protection of the public,

n) the design, installation, extension, alteration, renewal or repair of plumbing systems, and

o) the alteration, rehabilitation and change of occupancy of heritage buildings.

2)   This Code does not apply to the following:

a) sewage, water, electrical, telephone, rail or similar public infrastructure systems located in a street or a public transit right of way,

b) utility towers and poles, and television, radio and other communication aerials and towers, except for loads resulting from their being located on or attached to buildings,

c) mechanical or other equipment and appliances not specifically regulated in these regulations,

d) flood control and hydro electric dams and structures,

e) accessory buildings less than 10 m2  in building area that do not create a hazard,

f) with the permission of the authority having jurisdiction, temporary buildings including

i) construction site offices,

ii) seasonal storage buildings,

iii) special events facilities,

iv) emergency facilities, and

v) similar structures,

g) factory built housing and components complying with CSA-Z240 MH Series standard, but this exemption does not extend to on site preparations (siting, foundations, mountings), connection to services and installation of appliances, and

h) areas that are specifically exempted from provincial building regulations by provincial or federal enactments.

3) This Code applies to both site-built and factory-constructed buildings. (See Note A-1.1.1.1.(3).)

4) Farm buildings shall conform to the requirements in the National Farm Building Code of Canada 1995.

5) For heritage buildings, the Alternate Compliance Methods for Heritage Buildings in Table 1.1.1.1.(5) may be substituted for requirements contained elsewhere in this Code. (See Note A-1.1.1.1.(5).)

| Table 1.1.1.1.(5) Alternate Compliance Methods for Heritage Buildings Forming part of Sentence 1.1.1.1.(5) |  |  |
| --- | --- | --- |
| No. | Code Requirement in Division B | Alternate Compliance Method |
| 1 | Fire Separations Sentence 3.1.3.1.(1), Table 3.1.3.1., Subsection 9.10.9. 2 h fire separation required between some major occupancies. | Except for F1 occupancies, 1 h fire separation is acceptable, provided the building is sprinklered. |
| 2 | Fire Separations Sentence 3.1.3.1.(1), Table 3.1.3.1., Subsection 9.10.9. 1 h fire separation required between some major occupancies. | 30 min fire separation is acceptable if the building is sprinklered. |
| 3 | Noncombustible Construction Subsection 3.1.5., Article 9.10.6.1. All materials used in noncombustible construction must be noncombustible unless otherwise permitted. | 1. Roofs may be of combustible construction provided the building is sprinklered. 2. Up to 10% gross floor area to a maximum of 10% of any one floor area may be of combustible construction provided the building is sprinklered. |
| 4 | Fire-resistance Rating Sentence 3.1.7.1.(1), Article 9.10.3.1. Where a material, assembly of materials or structural member is required to have a fire-resistance rating it shall be tested in accordance with CAN/ULC-S101, "Fire Endurance Tests of Building Construction Materials." | A fire-resistance rating may also be used based on: (a) HUD No. 8 Guideline on Fire Ratings of Archaic Materials and Assemblies., (b) Fire Endurance of Protected Steel Columns and Beams, DBR Technical Paper No. 194., (c) Fire Endurance of Unit Masonry Walls, DBR Technical Paper No. 207., (d) Fire Endurance of Light-Framed and Miscellaneous Assemblies, DBR Technical Paper No. 222. |
| 5 | Rating of Supporting Construction Article 3.1.7.5., Article 9.10.8.3. Supporting assemblies to have fire-resistance rating at least equivalent to that of the supported floor. | Heavy timber construction is permitted to have a fire-resistance rating less than would be required by the Code provided the building: (a) is sprinklered, and (b) does not exceed 6 storeys in building height. |
| 6 | Continuity of Fire Separations Sentence 3.1.8.3.(1), Sentence 3.1.8.3.(2), Article 9.10.9.2. Fire separations are required to be continuous above the ceiling space. | Fire separations are not required to be continuous above a ceiling space where (a) the ceiling space is noncombustible construction, (b) both fire compartments are sprinklered, or (c) the ceiling has a minimum rating of 30 minutes. |
| 7 | Wired Glass Sentence 3.1.8.5.(1), Sentence 3.1.8.14.(2), Article 9.10.13.1., Article 9.10.13.5. 6 mm wired glass in steel frame required in fire separations. | For fixed transoms or sidelights, 6 mm wired glass fixed to a wood frame of at least 50 mm thickness with steel stops is permitted in a required fire separation. |
| 8 | Mezzanines Sentence 3.2.1.1.(4) and Sentence 3.2.1.1.(7), Article 9.10.4.1. Mezzanines enclosing more than 10% above the horizontal plane are considered as storey in building height. | Enclosed mezzanines may be up to 40% of the storey in which they occur and not be considered a storey in building height if the building is sprinklered. |
| 9 | Building Height Article 3.2.2.20. to Article 3.2.2.90. Noncombustible construction required for some buildings. | Buildings may be of combustible construction up to 6 storeys provided: (a) the building is sprinklered, (b) the building contains Group C, D, E, F, Division 2 or F, Division 3 occupancies, and (c) floor assemblies not required to exceed 1 h fire separation requirements may be of heavy timber construction. |
| 10 | Spatial Separation Subsection 3.2.3., Subsection 9.10.14. The area of unprotected opening shall not exceed the limits in Tables 3.2.3.1.A to Table 3.2.3.1.E | The area of unprotected opening is not limited provided: (a) the limiting distance is a minimum 1 m, (b) the building has a supervised sprinkler system in conformance with Sentence 3.2.4.9.(3), and (c) the sprinkler system is connected to the fire department in conformance with Sentence 3.2.4.7.(4). |
| 11 | Construction of Exposing Building Face Article 3.2.3.7., Article 9.10.14.5. The exposing building face is required to have a fire-resistance rating and/or be of noncombustible construction. | Exposing building face is not required to have a fire-resistance rating if the building is sprinklered. Also, the exposing building face is not required to be of noncombustible construction if it is protected by an exterior sprinkler system conforming to NFPA 13, “Installation of Sprinkler Systems.” |
| 12 | Roof Covering Rating Sentence 3.1.15.2.(1) Class A, B or C roof covering in conformance with CAN/ULC-S107, “Fire Tests of Roof Coverings” required. | For existing roofs not covered by a Class A, B or C roofing a manually operated deluge system in accordance with NFPA 13, “Installation of Sprinkler Systems” is permitted. |
| 13 | Smoke Alarms Sentence 3.2.4.20.(7), Sentence 9.10.19.4.(1) Smoke alarms are required to be connected to an electric circuit. | Smoke alarms may be battery operated in single family homes only. |
| 14 | Interconnected Floor Space Subsection 3.2.8., Sentence 9.10.1.3.(6) | 1. Open stairs in buildings of maximum 4 storeys in building height need not comply with Subsection 3.2.8., provided (a) the building contains a Group C or D occupancy, (b) the building is sprinklered with fast-response sprinklers, (c) corridors opening into the interconnected floor space are separated from the interconnected floor space by a fire separation with the rating required for the corridor, and (d) smoke detectors are installed in the rooms opening into the interconnected floor space and the smoke detectors are connected to the fire alarm system. 2. Open stairs in buildings of maximum 3 storeys in building height, or first 2 storeys and basement, need not comply with Subsection 3.2.8. of Division B, provided: (a) the building contains a Group C or D occupancy, (b) the building is sprinklered with fast response sprinklers, (c) smoke detectors are installed in the rooms opening into the interconnected floor space and the smoke detectors are connected to the fire alarm system, and (d) at least one means of egress is not through the interconnected floor space. |
| 15 | Separation of Suites Article 3.3.1.1., Article 9.10.9.13., Article 9.10.9.14. Suites are required to be separated from adjoining suites by a fire separation having a fire resistance rating of 45 min or 1 hr. | Existing fire separations of 30 min, such as wood lath and plaster in good condition, are acceptable in sprinklered buildings not exceeding 6 storeys in building height. |
| 16 | Corridor fire separation Article 3.3.1.4., Article 9.10.9.15. Public corridors are required to be separated from the remainder of the building by a fire separation having a fire-resistance rating of at least 45 min. | Existing corridors with 30 min fire resistance ratings, such as wood lath and plaster in good condition, are acceptable in residential occupancies provided the building: (a) does not exceed 6 storeys in building height, and (b) is fully sprinklered with fast response sprinklers. |
| 17 | Corridor Width Article 3.3.1.9., Subsection 3.4.3., Article 9.9.3.3. Public corridors and exit corridors are permitted to have a minimum width of 1 100 mm. | Public corridors and exit corridors are permitted with a minimum width of 800 mm provided: (a) the occupant load of the building is maximum 20 people, and (b) the building does not exceed 3 storeys in building height. |
| 18 | Door Swing Article 3.3.1.10., Article 3.4.6.12., Article 9.9.6.5. Doors required to swing in the direction of exit travel. | 2nd egress door from a room is not required to swing in the direction of exit travel provided: (a) the building is sprinklered and the system is supervised in conformance with Sentence 3.2.4.9.(3), and (b) the occupant load of the building is maximum 100 people. |
| 19 | Stairs, Ramps, Handrails and Guards Article 3.3.1.14., Article 3.3.1.16., Article 3.3.1.18., Articles 3.4.6.5 to 3.4.6.79., Section 9.8. | Existing conditions that do not comply fully with the requirements are permitted if they are acceptable to the authority having jurisdiction. |
| 20 | Transparent Doors and Panels Article 3.3.1.19., Article 9.6.1.4. Safety glass required. | Existing glass or transparent panels that do not comply fully with the requirements are permitted if sufficiently discernible or guards are provided in hazardous situations. |
| 21 | Dead-end Corridors Sentence 3.3.1.9.(7), Article 9.9.7.3. Dead-end corridors are permitted to a maximum length of 6 m. | 1. Dead-end corridors are permitted to a maximum length of 10 m in Group C occupancies provided: (a) the building is sprinklered with fast response sprinklers, and (b) smoke detectors are installed in the corridor system. 2. Dead-end corridors are permitted to a maximum of 15 m in length in Group D, E, F, Division 2 and F, Division 3 occupancies provided: (a) the building is sprinklered with fast response sprinklers, and (b) smoke detectors are installed in the corridor system. |
| 22 | Exits Article 3.4.2.1., Article 9.9.8.2. Floor areas shall be served by not fewer than 2 exits except as permitted by Sentence 3.4.2.1.(2). | Floor areas may be served by a single exit within the limits of Sentence 3.4.2.1.(2) provided: (a) the building does not exceed 3 storeys in building height, (b) the building is sprinklered with fast response sprinklers, and (c) all floor areas are protected by a system of smoke detectors connected to a fire alarm system. |
| 23 | Reduction of Exit Width Sentence 3.4.3.3.(2), Article 9.9.6.1. Swinging doors in their swing shall not reduce the effective width of exit stairs and landings to less than 750 mm. | Existing swinging doors in their swing are permitted to reduce the effective width of exit stairs and landings to a minimum of 550 mm provided: (a) they serve Group C or D occupancies, (b) the building does not exceed 4 storeys in building height, and (c) the building is sprinklered. |
| 24 | Fire Separation of Exits Article 3.4.4.1., Subsection 9.9.4. Exits are required to be separated from the remainder of the floor area by a fire separation having a fire-resistance rating of not less than required by Subsection 3.2.2. , but not less than 45 min. | 1. Buildings of 3 storeys or less may have exits that are separated by a fire separation that does not have a fire-resistance rating provided: (a) the building is sprinklered with fast response sprinklers, and (b) the sprinkler system is supervised in accordance with Sentence3.2 .4.9.(3). 2. Buildings not exceeding 6 storeys in building height may have exits that are separated by a fire separation having a fire resistance rating of not less than 45 min provided the building is sprinklered. |
| 25 | Exits Through Lobbies Article 3.4.4.2., Article 9.9.8.5. Rooms adjacent to the lobby are required to be separated by a fire separation. | Rooms adjacent to the lobby are not required to be separated by a fire separation provided: (a) the floor area is sprinklered with fast response sprinklers, and (b) smoke detectors are installed in the adjacent rooms. |
| 26 | Rooms Opening into Exit Sentence 3.4.4.4.(7), Article 9.9.5.9. Service rooms and ancillary rooms are not permitted to open directly into an exit. | Service rooms and ancillary rooms may open directly into an exit provided: (a) the room is sprinklered with fast response sprinklers, and (b) weatherstripping is installed on the door to prevent the passage of smoke. |
| 27 | Illumination of Exit Signs Sentence 3.4.5.1.(3) and 3.4.5.1.(4), Sentence 9.9.11.3.(3) and 9.9.11.3.(4) Exit signs are required to be illuminated continuously while the building is occupied. | Where exit signage may compromise historic appearances, or authenticity of displays, exit signs may be installed to light only on an emergency condition, such as by the fire alarm system or due to power failure. |
| 28 | Clearance from Exit Doors Sentence 3.4.6.11.(1), Article 9.9.6.6. Stair risers shall not be closer than 300 mm from an exit door. | Except as permitted in Sentences 3.4.6.11.(3) or 9.6.6.(2), existing exit doors shall not extend beyond the first riser. |
| 29 | Fire Escapes Subsection 3.4.7., Sentence 9.9.2.1.(2) Fire escapes are required to conform to Subsection 3.4.7. | Existing fire escapes that do not completely conform to Subsection 3.4.7.are acceptable provided: (a) the fire escapes are acceptable and (b) the building is sprinklered. |
| 30 | Fire Escape Construction Article 3.4.7.2., Sentence 9.9.2.1.(2) | Existing combustible fire escapes are permitted if the building is permitted to be of combustible construction by Part 3, Part 9 or by this Table. |
| 31 | Protection of Fire Escapes Article 3.4.7.4., Sentence 9.9.2.1.(2) Openings in the exterior wall adjacent to the fire escape are required to be protected by closures. | Existing openings in the exterior wall adjacent to the fire escape are not required to be protected by closures provided: (a) the building is sprinklered, and (b) a sprinkler head is located within 1.5 m of the opening required to be protected by Article 3.4.7.4. |
| 32 | Vertical Service Space Article 3.6.3.1. Vertical service spaces are required to be separated from the adjacent floor area by a rated fire separation. | Existing vertical service spaces that do not completely conform to the rated fire separation requirements are acceptable provided the vertical service spaces are sprinklered. |
| 33 | Height of Rooms Subsection 3.7.1., Section 9.5. The height of rooms is required to comply to minimum dimension requirements. | Existing rooms are not required to comply to the minimum dimension requirements of Subsection 3.7.1. or Subsection 9.5.3. |
| 34 | Washroom Requirements Subsection 3.7.2., Section 9.31. Buildings are required to be provided with a minimum number of washroom fixtures. | Existing facilities are not required to completely comply to the requirements of Subsection 3.7.2. or Section 9.31. provided it is acceptable to the authority having jurisdiction. |
| 35 | Access for Persons with Disabilities Section 3.8. of Division B | Article 3.8.4.5. shall apply to existing buildings. |
| 36 | Seismic Anchorage of Exterior Decoration Subsection 4.1.8. | Existing exterior decorations are not required to fully comply to the anchorage requirements of Subsection 4.1.8. provided: (a) adequate means of protection is provided, or (b) there is no exposure to the public. |
| 37 | Mechanical and Plumbing Systems Part 6 and Part 7 | Existing mechanical and plumbing systems in buildings are not required to fully comply to the requirements of Parts 6 or Part 7 provided: (a) it is not an unsafe condition and (b) it is acceptable to the authority having jurisdiction. |

6) For the design and construction of alterations to existing buildings to add a secondary suite, not including the design and construction of new additions or new buildings, the Alternate Compliance Methods for Alterations to Existing Buildings to Add a Secondary Suite in Table 1.1.1.1.(6) may be substituted for requirements contained elsewhere in this Code. (See Note A-1.1.1.1.(6).)

| Table 1.1.1.1.(6) Alternate Compliance Methods for Alterations to Existing Buildings to Add a Secondary Suite Forming part of Sentence 1.1.1.1.(6) |  |  |
| --- | --- | --- |
| No. | Code Requirement in Division B | Alternate Compliance Method (References to Division B) |
| 1 | Reinforcement for Grab Bars Sentence 3.8.5.1.(2) One bathroom in a secondary suite shall have walls adjacent the water closer and shower or bathtub location reinforced to accommodate the future installation of grab bars. | Reinforcement to accommodate the future installation of grab bars is not required in existing bathrooms serving a secondary suite. |
| 2 | Ceiling Heights of Rooms or Spaces Sentence 9.5.3.1.(1) and Table 9.5.3.1. Ceiling height shall be not less than 2.1 m over the minimum area required in Table 9.5.3.1. | Except as required by Sentence 9.9.3.4.(3), the minimum ceiling heights in a secondary suite over the required area as indicated in Table 9.5.3.1. shall be not less than 1.95 m. It shall be possible to travel from the required area of one room to the required areas of all other rooms within the secondary suite without reduction of the ceiling height to less than 1.95 m. Except as required by Sentence 9.9.3.4.(3), the minimum clear height under beams and ducting, including where located over stairs, in a secondary suite shall be not less than 1.85 m. |
| 3 | Doorway Opening Sizes Sentence 9.5.5.1.(1) and Table 9.5.5.1. Doorway openings shall be designed to accommodate swing-type and folding doors not less than 1 980 mm high. | Except for exit doors and for doors serving public corridors and exit corridors that serve a house with a secondary suite, doorway openings within a secondary suite shall be designed to accommodate swing-type and folding doors not less than 1 890 mm high. |
| 4 | Height over Stairs Sentence 9.8.2.2.(3) The clear height over stairs shall be not less than 1950 mm. | Except for stairs in a public corridor or exit corridor that serve a house with a secondary suite, the clear height over stairs that are located under existing beams and existing ducting in a house with a secondary suite shall be not less than 1 850 mm. |
| 5 | Openings Near Unenclosed Exterior Exit Stairs and Ramps Sentence 9.9.4.4.(1) Unprotected openings in exterior walls that are within 3 m horizontally and less than 10 m below or less than 5 m above an unenclosed exterior exit stair or ramp of a house with a secondary suite shall be protected where the unenclosed exterior exit stair or ramp provides the only means of egress from a suite and is exposed to fire from unprotected openings in the exterior walls of another dwelling unit, ancillary space or common space. | Protection of the unprotected openings as described in Sentence 9.9.4.4.(1) is not required when all smoke alarms within a house with a secondary suite are of photo-electric type and interconnected as described in Clause 9.10.19.5.(2)(a). |
| 6 | Openings Near Exit Doors Sentence 9.9.4.6.(1) Where an exterior exit door in one fire compartment is within 3 m horizontally of an unprotected opening in another fire compartment and the exterior walls of these fire compartments intersect at an exterior angle of less than 135°, the opening shall be protected. | Protection of the unprotected openings as described in Sentence 9.9.4.6.(1) is not required when all smoke alarms within a house with a secondary suite are of photo-electric type and interconnected as described in Clause 9.10.19.5.(2)(a). |
| 7 | Fire-Resistance and Fire-Protection Ratings Sentence 9.10.3.1.(3) In a house with a secondary suite, where a minimum fire-resistance rating of 30 min is permitted, it is permitted to use wood-frame construction where stud and joist spaces are filled with absorptive material, resilient metal channel spaced 400 or 600 mm o.c. is on one side and not less than 12.7 mm thick gypsum board is installed on ceilings and on both sides of walls. | Adding resilient metal channel spaced 400 or 600 mm o.c. and an additional layer of not less than 12.7 mm gypsum board to one side of an existing finished wall assembly that has not less than 12.7 mm gypsum board on each side or an existing finished floor-ceiling assembly that has not less than 12.7 mm gypsum on the ceiling side is permitted to be used where a 30 min fire-resistance rating is required. |
| 8 | Fire-Resistance Ratings for Walls, Columns and Arches Sentence 9.10.8.3.(1) Loadbearing walls, columns and arches in the storey immediately below a floor or roof assembly shall have a fire-resistance rating of not less than that required for the supported floor or roof assembly. | Except for heavy timber elements and those of masonry or concrete construction, light frame walls, columns, arches and beams as well as loadbearing steel elements that support floors between dwelling units in a house with a secondary suite including their common spaces shall be protected by not less than 12.7 mm thick gypsum board. |
| 9 | Sound Transmission Sentence 9.11.1.1.(2) Each dwelling unit shall be separated from every other space in a house with a secondary suite in which noise may be transmitted by construction having joist and stud spaces filled with sound-absorbing material, resilient channel on one side of the separation, and 12.7 mm thick gypsum board on ceilings and on both sides of walls, or by either construction providing an STC rating of not less than 43, or by using a separating assembly and adjoining construction providing an ASTC rating of not less than 40. | The assemblies and adjoining constructions that separate the dwelling units in a house with a secondary suite including their common spaces need not comply with Clause 9.11.1.1.(2)(a) where resilient metal channel spaced 400 or 600 mm o.c. and an additional layer of not less than 12.7 mm gypsum board is added to one side of an existing finished assembly. |

1.1.1.2. Application to Existing Buildings

1) Where a building is altered, rehabilitated, renovated or repaired, or there is a change in occupancy, the level of life safety and building performance shall not be decreased below a level that already exists. (See Note A-1.1.1.2.(1).)

1.1.2. Internal References to this Code

1.1.2.1. Book I (General) and Book II (Plumbing Systems) of the Code

1) This is the first of the two Books, Book I (General) and Book II (Plumbing Systems), that together form the British Columbia Building Code.

1.1.2.2. Internal References to the Code

1) Unless a Book is specified, references to “the British Columbia Building Code,” “the Code,” “this Code” and the like shall be read as references to the Book in which they appear.

1.1.3. Appendices, Notes and Annotations

1.1.3.1. Appendices, Notes and References to Appendices and Notes have No Legal Effect

1) Except for Notes A-Table 9.23.3.5.-B and A-9.23.13., including Table A-9.23.13. in Division B, Notes to Parts of this Code have no legal effect.

Section  1.2.   Compliance

1.2.1. Compliance with this Code

1.2.1.1. Compliance with this Code

1)   Compliance with this Code shall be achieved by

a)   complying with the applicable acceptable solutions in Division B (see Note A-1.2.1.1.(1)(a)), or

b)   except as required by Sentence (3), using alternative solutions, accepted by the authority having jurisdiction under Section 2.3 of Division C, that will achieve at least the minimum level of performance required by Division B in the areas defined by the objectives and functional statements attributed to the applicable acceptable solutions (see Note A-1.2.1.1.(1)(b)).

2)   For the purposes of compliance with this Code as required in Clause 1.2.1.1.(1)(b), the objectives and functional statements attributed to the acceptable solutions in Division B shall be the objectives and functional statements referred to in Subsection 1.1.2. of Division B.

3) An alternative solution shall not be used in place of an acceptable solution if the acceptable solution expressly requires conformance to a provincial enactment other than Book I (General) or Book II (Plumbing Systems) of the British Columbia Building Code.

1.2.1.2. Responsibility of Owner

1) Unless otherwise specified in this Code, the owner of a building shall be the person responsible for carrying out the provisions of this Code in relation to that building.

2) The owner of a building is in no way relieved of full responsibility for complying with this Code by the authority having jurisdiction

a) granting a building permit,

b) approving drawings or specifications, or

c) carrying out inspections.

1.2.2. Materials, Appliances, Systems and Equipment

1.2.2.1. Characteristics of Materials, Appliances, Systems and Equipment

1)   All materials, appliances, systems and equipment installed to meet the requirements of this Code shall possess the necessary characteristics to perform their intended functions when installed in a building.

1.2.2.2. Storage on the Building Site

1)   All building materials, appliances and equipment on the building site shall be stored in such a way as to prevent the deterioration or impairment of their essential properties.

1.2.2.3. Used Materials, Appliances and Equipment

1)   Unless otherwise specified, used materials, appliances and equipment are permitted to be reused when they meet the requirements of this Code for new materials and are satisfactory for the intended use.

1.2.3. Installation of Plumbing Systems

1.2.3.1. Personnel Performing Plumbing Work

1)   Personnel performing the installation, alteration, renewal or repair of a plumbing system shall

a) possess a Canadian tradesperson’s qualification certification as a plumber,

b) be an indentured apprentice supervised by a journeyperson who meets the criteria set out in Clause (a), or

c) be the registered owner and occupant or intended occupant of the single detached dwelling in which plumbing work will occur.

Section  1.3.   Divisions A, B and C of this Code

1.3.1. General

1.3.1.1. Scope of Division A

1)   Division A contains the compliance and application provisions, objectives and functional statements of this Code.

1.3.1.2. Scope of Division B

1)   Division B contains the acceptable solutions of this Code.

1.3.1.3. Scope of Division C

1)   Division C contains the administrative provisions of this Code.

1.3.1.4. Internal Cross-references

1)   Where the Division of a referenced provision is not specified in this Code, it shall mean that the referenced provision is in the same Division as the referencing provision.

1.3.2. Application of Division A

1.3.2.1. Application of Parts 1, 2 and 3

1)   Parts 1, 2 and 3 of Division A apply to all buildings covered in this Code. (See Article 1.1.1.1.)

1.3.3. Application of Division B

1.3.3.1. Application of Parts 1, 7, 8 and 10

1)   Parts 1, 7, 8 and 10  of Division B apply to all buildings covered in this Code. (See Article 1.1.1.1.)

1.3.3.2. Application of Parts 3, 4, 5 and 6

1)   Parts 3, 4, 5, and 6 of Division B apply to all buildings described in Article 1.1.1.1. and

a)   classified as post-disaster buildings,

b)   used for major occupancies classified as

i)   Group A, assembly occupancies,

ii)   Group B, care, treatment or detention occupancies, or

iii)   Group F, Division 1, high-hazard industrial occupancies, or

c)   exceeding 600 m2 in building area or exceeding 3 storeys in building height used for major occupancies classified as

i)   Group C, residential occupancies,

ii)   Group D, business and personal services occupancies,

iii)   Group E, mercantile occupancies, or

iv)   Group F, Divisions 2 and 3, medium- and low-hazard industrial occupancies.

1.3.3.3. Application of Part 9

1)   Part 9 of Division B applies to all buildings described in Article 1.1.1.1. of 3 storeys or less in building height, having a building area not exceeding 600 m2, and used for major occupancies classified as

a)   reserved,

b)   Group C, residential occupancies (see Note A-9.1.1.1.(1) of Division B),

c)   Group D, business and personal services occupancies,

d)   Group E, mercantile occupancies, or

e)   Group F, Divisions 2 and 3, medium- and low-hazard industrial occupancies.

1.3.3.4. Building Size Determination

1)   Where a firewall divides a building, each portion of the building so divided shall be considered as a separate building, except when this requirement is specifically modified in other parts of this Code. (See Note A-1.3.3.4.(1).)

2)   Except as permitted in Sentence (3), where portions of a building are completely separated by a vertical fire separation that has a fire-resistance rating of not less than 1 h and extends through all storeys and service spaces of the separated portions, each separated portion is permitted to be considered as a separate building for the purpose of determining building height, provided

a)   each separated portion is not more than 4 storeys in building height and is used only for assembly, residential, and business and personal services occupancies, and

b)   the unobstructed path of travel for a firefighter from the nearest street to one entrance of each separated portion is not more than 45 m.

(See Note A-1.3.3.4.(2).)

3)   The vertical fire separation referred to in Sentence (2) may terminate at the floor assembly immediately above a basement provided the basement conforms to Article 3.2.1.2. of Division B.

1.3.4. Application of Division C

1.3.4.1. Application of Parts 1 and 2

1)   Parts 1 and 2 of Division C apply to all buildings covered in this Code. (See Article 1.1.1.1.)

Section  1.4.   Terms and Abbreviations

1.4.1. Definitions of Words and Phrases

1.4.1.1. Non-defined Terms

1)   Words and phrases used in this Code that are not included in the list of definitions in Article 1.4.1.2. shall have the meanings that are commonly assigned to them in the context in which they are used, taking into account the specialized use of terms by the various trades and professions to which the terminology applies.

2)   Where objectives and functional statements are referred to in this Code, they shall be the objectives and functional statements described in Parts 2 and 3.

3)   Where acceptable solutions are referred to in this Code, they shall be the provisions stated in Parts 2 to 9 of Division B.

4)   Where alternative solutions are referred to in this Code, they shall be the alternative solutions mentioned in Clause 1.2.1.1.(1)(b).

1.4.1.2. Defined Terms

1)   The words and terms in italics in this Code shall have the following meanings:

Access or Accessible means an area and its facilities, or both, as required by this Code, which is easy to approach, enter, exit, operate, participate in, pass to and from, and use safely and independently by persons with disabilities.

Access to exit means that part of a means of egress within a floor area that provides access to an exit serving the floor area.

Adaptable dwelling unit means a dwelling unit designed and constructed with some accessible features and which accommodates the future modification to provide more accessible features.

Adfreezing means the adhesion of soil to a foundation unit resulting from the freezing of soil water. (Also referred to as “frost grip.”)

Air barrier system means the assembly installed to provide a continuous barrier to the movement of air.

Air-supported structure means a structure consisting of a pliable membrane that achieves and maintains its shape and support by internal air pressure.

Alarm signal means an audible signal transmitted throughout a zone or zones or throughout a building to advise occupants that a fire emergency exists.

Alert signal means an audible signal to advise designated persons of a fire emergency.

Alteration means a change or extension to any matter or thing or to any occupancy regulated by this Code.

Apparent sound transmission class (ASTC) means a single number rating of the airborne sound attenuation of building assemblies separating two adjoining spaces, taking into account both the direct and flanking sound transmission paths. (See Note A-1.4.1.2.(1).) (See also Note A-9.11. of Division B.)

Appliance means a device to convert fuel into energy and includes all components, controls, wiring and piping required to be part of the device by the applicable standard referred to in this Code.

Artesian groundwater means a confined body of water under pressure in the ground.

Assembly occupancy (Group A) means the occupancy or the use of a building or part thereof by a gathering of persons for civic, political, travel, religious, social, educational, recreational or like purposes, or for the consumption of food or drink.

Attic or roof space means the space between the roof and the ceiling of the top storey or between a dwarf wall and a sloping roof.

Authority having jurisdiction means the governmental body responsible for the enforcement of any part of this Code or the official or agency designated by that body to exercise such a function.  Notwithstanding this definition, the Chief Inspector of Mines has the sole responsibility for administration and enforcement in respect to all buildings, structures and site services used at a mine, as defined in the Mines Act.

Basement means a storey or storeys of a building located below the first storey.

Bearing surface means the contact surface between a foundation unit and the soil or rock upon which it bears.

Boiler means an appliance intended to supply hot water or steam for space heating, processing or power purposes.

Braced wall band means an imaginary continuous straight band extending vertically and horizontally through the building or part of the building, within which braced wall panels are constructed.

Braced wall panel means a portion of a wood-frame wall where bracing, sheathing, cladding or interior finish is designed and installed to provide the required resistance to lateral loads due to wind or earthquake.

Breeching means a flue pipe or chamber for receiving flue gases from one or more flue connections and for discharging these gases through a single flue connection.

Building means any structure used or intended for supporting or sheltering any use or occupancy.

Building area means the greatest horizontal area of a building above grade within the outside surface of exterior walls or within the outside surface of exterior walls and the centre line of firewalls.

Building height (in storeys) means the number of storeys contained between the roof and the floor of the first storey.

Business and personal services occupancy (Group D) means the occupancy or use of a building or part thereof for the transaction of business or the rendering or receiving of professional or personal services.

Caisson (see Pile).

Care means the provision of services other than treatment by or through care facility management to residents who require these services because of cognitive, physical or behavioural limitations.

Care occupancy (Group B, Division 3) means the occupancy or use of a building or part thereof, other than a home-type care occupancy, where care is provided to residents. (See Note A-1.4.1.2.(1).)

Cavity wall means a construction of masonry units laid with a cavity between the wythes. The wythes are tied together with metal ties or bonding units, and are relied on to act together in resisting lateral loads.

Chimney means a primarily vertical shaft enclosing at least one flue for conducting flue gases to the outdoors.

Chimney liner means a conduit containing a chimney flue used as a lining of a masonry or concrete chimney.

Closure means a device or assembly for closing an opening through a fire separation or an exterior wall, such as a door, a shutter, a damper, wired glass or glass block, and includes all components such as hardware, closing devices, frames and anchors.

Combustible means that a material fails to meet the acceptance criteria of CAN/ULC-S114, “Standard Method of Test for Determination of Non-Combustibility in Building Materials.”

Combustible construction means that type of construction that does not meet the requirements for noncombustible construction or encapsulated mass timber construction.

Combustible dusts means dusts and particles that are ignitable and liable to produce an explosion.

Combustible fibres means finely divided, combustible vegetable or animal fibres and thin sheets or flakes of such materials which, in a loose, unbaled condition, present a flash fire hazard, including cotton, wool, hemp, sisal, jute, kapok, paper and cloth.

Combustible liquid means a liquid having a flash point at or above 37.8°C and below 93.3°C.

Conditioned space means any space within a building, the temperature of which is controlled to limit variation in response to the exterior ambient temperature by the provision, either directly or indirectly, of heating or cooling over substantial portions of the year.

Constructor means a person who contracts with an owner or their authorized agent to undertake a project, and includes an owner who contracts with more than one person for the work on a project or undertakes the work on a project or any part thereof.

Contained use area means a supervised area containing one or more rooms in which occupant movement is restricted to a single room by security measures not under the control of the occupant.

Cooktop means a cooking surface having one or more burners or heating elements.

Dangerous goods means products, materials or substances that are

(a)   regulated by TC SOR/2001-286, “Transportation of Dangerous Goods Regulations (TDGR)” (see Table 3.2.7.1. of Division B of the NFC), or

(b)   classified as controlled products under HC SOR/2015-17, “Hazardous Products Regulations” (see Note A-Table 3.2.7.1. of Division B of the NFC).

(See Note A-1.4.1.2.(1).)

Dead load means the weight of all permanent structural and non-structural components of a building.

Deep foundation means a foundation unit that provides support for a building by transferring loads either by end-bearing to soil or rock at considerable depth below the building, or by adhesion or friction, or both, in the soil or rock in which it is placed. Piles are the most common type of deep foundation.

Designer means the person responsible for the design.

Detention occupancy (Group B, Division 1) means the occupancy by persons who are restrained from or are incapable of evacuating to a safe location without the assistance of another person because of security measures not under their control.

Direct-vented (as applying to a fuel-fired space- or water-heating appliance) means an appliance and its venting system in which all the combustion air is supplied directly from the outdoors and the products of combustion are vented directly to the outdoors via independent, totally enclosed passageways connected directly to the appliance.

Distilled beverage alcohol means a beverage that is produced by fermentation and contains more than 20% by volume of water-miscible alcohol.

Distillery means a process plant where distilled beverage alcohols are produced, concentrated or otherwise processed, and includes facilities on the same site where the concentrated products may be blended, mixed, stored or packaged.

Dwelling unit means a suite operated as a housekeeping unit, used or intended to be used by one or more persons and usually containing cooking, eating, living, sleeping and sanitary facilities.

Encapsulated mass timber construction means that type of construction in which a degree of fire safety is attained by the use of encapsulated mass timber elements with an encapsulation rating and minimum dimensions for structural members and other building assemblies.

Encapsulation rating means the time in minutes that a material or assembly of materials will delay the ignition and combustion of encapsulated mass timber elements when it is exposed to fire under specified conditions of test and performance criteria, or as otherwise prescribed by this Code.

Excavation means the space created by the removal of soil, rock or fill for the purposes of construction.

Exhaust duct means a duct through which air is conveyed from a room or space to the outdoors.

Exit means that part of a means of egress, including doorways, that leads from the floor area it serves to a separate building, an open public thoroughfare, or an exterior open space protected from fire exposure from the building and having access to an open public thoroughfare. (See Note A-1.4.1.2.(1).)

Exit level means the level of an exit stairway at which an exterior exit door or exit passageway leads to the exterior.

Exit storey (as applying to Subsection 3.2.6. of Division B) means a storey having an exterior exit door.

Exposing building face means that part of the exterior wall of a building that faces one direction and is located between ground level and the ceiling of its top storey or, where a building is divided into fire compartments, the exterior wall of a fire compartment that faces one direction.

Factory-built chimney means a chimney consisting entirely of factory-made parts, each designed to be assembled with the other without requiring fabrication on site.

Farm building means a building or part thereof that contains an agricultural occupancy. (See Note A-1.4.1.2.(1).)

Field review means a review of the work

- at a building site, and

- where applicable, at locations where building components are fabricated for use at the building site

that a registered professional in thier professional discretion considers necessary to ascertain whether the work substantially complies in all material respects with the plans and supporting documents prepared by a registered professional.

Fill means soil, rock, rubble, industrial waste such as slag, organic material or a combination of these that is transported and placed on the natural surface of soil or rock or organic terrain. It may or may not be compacted.

Fire block means a material, component or system that restricts the spread of fire within a concealed space or from a concealed space to an adjacent space.

Fire compartment means an enclosed space in a building that is separated from all other parts of the building by enclosing construction providing a fire separation having a required fire-resistance rating.

Fire damper means a closure consisting of a damper that is installed in an air distribution system or a wall or floor assembly and that is normally held open but designed to close automatically in the event of a fire in order to maintain the integrity of the fire separation.

Fire detector means a device that detects a fire condition and automatically initiates an electrical signal to actuate an alert signal or alarm signal and includes heat detectors and smoke detectors.

Fire load (as applying to an occupancy) means the combustible contents of a room or floor area expressed in terms of the average weight of combustible materials per unit area, from which the potential heat liberation may be calculated based on the calorific value of the materials, and includes the furnishings, finished floor, wall and ceiling finishes, trim and temporary and movable partitions.

Fire-protection rating means the time in minutes or hours that a closure will withstand the passage of flame when exposed to fire under specified conditions of test and performance criteria, or as otherwise prescribed in this Code.

Fire-resistance rating means the time in minutes or hours that a material or assembly of materials will withstand the passage of flame and the transmission of heat when exposed to fire under specified conditions of test and performance criteria, or as determined by extension or interpretation of information derived therefrom as prescribed in this Code. (See Sentence D-1.2.1.(2) in Appendix D of Division B.)

Fire-retardant-treated wood means wood or a wood product that has had its surface-burning characteristics, such as flame spread, rate of fuel contribution and density of smoke developed, reduced by impregnation with fire-retardant chemicals.

Fire separation means a construction assembly that acts as a barrier against the spread of fire. (See Note A-1.4.1.2.(1).)

Firestop means a system consisting of a material, component and means of support used to fill gaps between fire separations or between fire separations and other assemblies, or used around items that wholly or partially penetrate a fire separation.

Fire stop flap means a device intended for use in horizontal assemblies required to have a fire-resistance rating and incorporating protective ceiling membranes that operates to close off a duct opening through the membrane in the event of a fire.

Firewall means a type of fire separation of noncombustible construction that subdivides a building or separates adjoining buildings to resist the spread of fire and that has a fire-resistance rating as prescribed in this Code and has structural stability to remain intact under fire conditions for the required fire-rated time.

First storey means the uppermost storey having its floor level not more than 2 m above grade.

Flame-spread rating means an index or classification indicating the extent of spread-of-flame on the surface of a material or an assembly of materials as determined in a standard fire test as prescribed in this Code.

Flammable liquid means a liquid having a flash point below 37.8°C and having a vapour pressure not more than 275.8 kPa (absolute) at 37.8°C as determined by ASTM D323, “Standard Test Method for Vapor Pressure of Petroleum Products (Reid Method).”

Flash point means the minimum temperature at which a liquid within a container gives off vapour in sufficient concentration to form an ignitable mixture with air near the surface of the liquid.

Flight means a series of steps between landings. (See Note A-1.4.1.2.(1).)

Floor area means the space on any storey of a building between exterior walls and required firewalls, including the space occupied by interior walls and partitions, but not including exits, vertical service spaces, and their enclosing assemblies.

Flue means an enclosed passageway for conveying flue gases.

Flue collar means the portion of a fuel-fired appliance designed for the attachment of the flue pipe or breeching.

Flue pipe means the pipe connecting the flue collar of an appliance to a chimney.

Forced-air furnace means a furnace equipped with a fan that provides the primary means for the circulation of air.

Foundation means a system or arrangement of foundation units through which the loads from a building are transferred to supporting soil or rock.

Foundation unit means one of the structural members of the foundation of a building such as a footing, raft or pile.

Frost action means the phenomenon that occurs when water in soil is subjected to freezing which, because of the water/ice phase change or ice lens growth, results in a total volume increase or the build-up of expansive forces under confined conditions or both, and the subsequent thawing that leads to loss of soil strength and increased compressibility.

Furnace means a space-heating appliance using warm air as the heating medium and usually having provision for the attachment of ducts.

Gas vent means that portion of a venting system designed to convey vent gases to the outdoors from the vent connector of a gas-fired appliance or directly from the appliance when a vent connector is not used.

Grade means the lowest of the average levels of finished ground adjoining each exterior wall of a building, except that localized depressions need not be considered in the determination of average levels of finished ground. (See First storey and Note A-1.4.1.2.(1).)

Greenhouse agricultural occupancy (Group G, Division 3) means an agricultural occupancy where plants are grown in a building or part thereof that is primarily constructed of roofs and walls designed to transmit natural light.

Groundwater means a free standing body of water in the ground.

Groundwater level (groundwater table) means the top surface of a free standing body of water in the ground.

Guard means a protective barrier around openings in floors or at the open sides of stairs, landings, balconies, mezzanines, galleries, raised walkways or other locations to prevent accidental falls from one level to another. Such a barrier may or may not have openings through it.

Heat detector means a fire detector designed to operate at a predetermined temperature or rate of temperature rise.

Heavy timber construction means that type of combustible construction in which a degree of fire safety is attained by placing limitations on the sizes of wood structural members and on the thickness and composition of wood floors and roofs and by the avoidance of concealed spaces under floors and roofs.

Heritage building is a building which is legally protected or officially recognized as a heritage property by the Provincial government or a local government.  (See Note A-1.1.1.1.(5).)

High-hazard agricultural occupancy (Group G, Division 1) means an agricultural occupancy containing sufficient quantities of highly combustible and flammable or explosive materials which, because of their inherent characteristics, constitute a special fire hazard.

High-hazard industrial occupancy (Group F, Division 1) means an industrial occupancy containing sufficient quantities of highly combustible and flammable or explosive materials which, because of their inherent characteristics, constitute a special fire hazard.

Home-type care occupancy (Group B, Division 4) means the occupancy or use of a building consisting of a single detached housekeeping unit where care is provided to residents and may include the living space of the caregiver and their family. (See Note A-1.4.1.2.(1).)

Horizontal exit means an exit from one building to another by means of a doorway, vestibule, walkway, bridge or balcony.

Horizontal service space means a space such as an attic, duct, ceiling, roof or crawl space oriented essentially in a horizontal plane, concealed and generally inaccessible, through which building service facilities such as pipes, ducts and wiring may pass.

Impeded egress zone means a supervised area in which occupants have free movement but require the release, by security personnel, of security doors at the boundary before they are able to leave the area, but does not include a contained use area.

Indirect service water heater means a service water heater that derives its heat from a heating medium such as warm air, steam or hot water.

Industrial occupancy (Group F) means the occupancy or use of a building or part thereof for the assembling, fabricating, manufacturing, processing, repairing or storing of goods and materials.

Interconnected floor space means superimposed floor areas or parts of floor areas in which floor assemblies that are required to be fire separations are penetrated by openings that are not provided with closures.

Limiting distance means the distance from an exposing building face to a property line, the centre line of a street, lane or public thoroughfare, or to an imaginary line between 2 buildings or fire compartments on the same property, measured at right angles to the exposing building face.

Live load means a variable load due to the intended use and occupancy that is to be assumed in the design of the structural members of a building. It includes loads due to cranes and the pressure of liquids in containers.

Loadbearing (as applying to a building element) means subjected to or designed to carry loads in addition to its own dead load, excepting a wall element subjected only to wind or earthquake loads in addition to its own dead load.

Low-hazard industrial occupancy (Group F, Division 3) means an industrial occupancy in which the combustible content is not more than 50 kg/m2 or 1 200 MJ/m2 of floor area.

Major occupancy means the principal occupancy for which a building or part thereof is used or intended to be used, and shall be deemed to include the subsidiary occupancies that are an integral part of the principal occupancy. The major occupancy classifications used in this Code are as follows:

A1 – Assembly occupancies intended for the production and viewing of the performing arts

A2 – Assembly occupancies not elsewhere classified in Group A

A3 – Assembly occupancies of the arena type

A4 – Assembly occupancies in which the occupants are gathered in the open air

B1 – Detention occupancies in which persons are under restraint or are incapable of self-preservation because of security measures not under their control

B2 – Treatment occupancies

B3 – Care occupancies

C – Residential occupancies

D – Business and personal services occupancies

E – Mercantile occupancies

F1 – High-hazard industrial occupancies

F2 – Medium-hazard industrial occupancies

F3 – Low-hazard industrial occupancies

Masonry or concrete chimney means a chimney of brick, stone, concrete or masonry units constructed on site.

Means of egress means a continuous path of travel provided for the escape of persons from any point in a building or contained open space to a separate building, an open public thoroughfare, or an exterior open space protected from fire exposure from the building and having access to an open public thoroughfare. Means of egress includes exits and access to exits.

Mechanically vented (as applying to a fuel-fired space- or water-heating appliance) means an appliance and its combustion venting system in which the products of combustion are entirely exhausted to the outdoors by a mechanical device, such as a fan, blower or aspirator, upstream or downstream from the combustion zone of the appliance, and the portion of the combustion venting system that is downstream of the fan, blower or aspirator is sealed and does not include draft hoods or draft control devices. (See Note A-1.4.1.2.(1).)

Medium-hazard industrial occupancy (Group F, Division 2) means an industrial occupancy in which the combustible content is more than 50 kg/m2 or 1 200 MJ/m 2 of floor area and not classified as a high-hazard industrial occupancy.

Mercantile occupancy (Group E) means the occupancy or use of a building or part thereof for the displaying or selling of retail goods, wares or merchandise.

Mezzanine means an intermediate floor assembly between the floor and ceiling of any room or storey and includes an interior balcony.

Noncombustible means that a material meets the acceptance criteria of CAN/ULC-S114, “Standard Method of Test for Determination of Non-Combustibility in Building Materials.”

Noncombustible construction means that type of construction in which a degree of fire safety is attained by the use of noncombustible materials for structural members and other building assemblies.

Occupancy means the use or intended use of a building or part thereof for the shelter or support of persons, animals or property.

Occupant load means the number of persons for which a building or part thereof is designed.

Open-air storey means a storey in which at least 25% of the total area of its perimeter walls is open to the outdoors in a manner that will provide cross-ventilation to the entire storey.

Owner means any person, firm or corporation controlling the property under consideration during that period of the application of Sentence 1.1.1.1.(1) of this Code.

Partition means an interior wall 1 storey or part-storey in height that is not loadbearing.

Party wall means a wall jointly owned and jointly used by 2 parties under easement agreement or by right in law, and erected at or upon a line separating 2 parcels of land each of which is, or is capable of being, a separate real-estate entity.

Perched groundwater means a free standing body of water in the ground extending to a limited depth.

Persons with disabilities means persons who have a permanent or temporary physical, mental, intellectual or sensory impairment which, in interaction with various barriers, may hinder their full and effective participation in society on an equal basis with others.

Pile means a slender deep foundation unit made of materials such as wood, steel or concrete or a combination thereof, that is either premanufactured and placed by driving, jacking, jetting or screwing, or cast-in-place in a hole formed by driving, excavating or boring. (Cast-in-place bored piles are often referred to as caissons in Canada.)

Plenum means a chamber forming part of an air duct system.

Plumbing system means a drainage system, a venting system and a water system or parts thereof.

Post-disaster building means a building that the authority having jurisdiction has determined is necessary for the provision of essential services to the general public in the event of a disaster and includes buildings meeting these criteria but not limited to

•   hospitals, emergency treatment facilities and blood banks,

•   telephone exchanges,

•   power generating stations and electrical substations,

•   control centres for natural gas distribution,

•   control centres for air, land and marine transportation,

•   water treatment facilities,

•   water storage facilities,

•   water and sewage pumping stations,

•   sewage treatment facilities,

•   buildings having critical national defence functions, and

•   buildings of the following types, unless exempted from this designation by the authority having jurisdiction:

•   emergency response facilities,

•   fire, rescue and police stations and housing for vehicles, aircraft or boats used for such purposes, and

•   communications facilities, including radio and television stations.

(See Note A-1.4.1.2.(1).)

Private sewage disposal system means a privately owned plant for the treatment and disposal of sewage (such as a septic tank with an absorption field).

Process plant means an industrial occupancy where materials, including flammable liquids, combustible liquids or gases, are produced or used in a process. (See Table 3.2.7.1. of Division B of the British Columbia Fire Code.)

Protected floor space means that part of a floor area protected from the effects of fire and used as part of a means of egress from an interconnected floor space.

Public corridor means a corridor that provides access to exit from more than one suite. (See Note A-1.4.1.2.(1).)

Public way means a sidewalk, street, highway, square or other open space to which the public has access, as of right or by invitation, expressed or implied.

Ramp means a path of travel having a slope steeper than 1 in 20.

Registered professional means

- a person who is registered as an Architect with the Architectural Institute of British Columbia under the Professional Governance Act, or

- a person who is registered as a professional engineer or professional licensee engineering with the Association of Professional Engineers and Geoscientists of the Province of British Columbia under the Professional Governance Act.

Registered professional of record means a registered professional retained to undertake design work and field review in accordance with Subsection 2.2.7. of Division C.

Repair garage means a building or part thereof where facilities are provided for the repair or servicing of motor vehicles.

Residential occupancy (Group C) means the occupancy or use of a building or part thereof by persons for whom sleeping accommodation is provided but who are not harboured for the purpose of receiving care or treatment and are not involuntarily detained.

Return duct means a duct for conveying air from a space being heated, ventilated or air-conditioned back to the heating, ventilating or air-conditioning appliance.

Rim joist means the outermost member in floor framing, other than blocking, be it parallel, perpendicular or on an angle to the floor joists. (See Note A-1.4.1.2.(1).)

Rock means that portion of the earth's crust that is consolidated, coherent and relatively hard and is a naturally formed, solidly bonded, mass of mineral matter that cannot readily be broken by hand.

Run means the horizontal distance between two adjacent tread nosings on a stair. (See Figure A-9.8.4.-B in Note A-9.8.4. of Division B.)

Sanitary drainage system means a drainage system that conducts sewage.

Secondary suite means a self-contained dwelling unit located within a building or portion of a building

- completely separated from other parts of the building by a vertical fire separation that has a fire-resistance rating of not less than 1 h and extends from ground or lowermost assembly continuously through or adjacent to all storeys and spaces including service spaces of the separated portions,

- of only residential occupancy that contains only one other dwelling unit and common spaces, and

- where both dwelling units constitute a single real estate entity.
 (See Note A-1.4.1.2.(1) of Division B.)

Service room means a room provided in a building to contain equipment associated with building services. (See Note A-1.4.1.2.(1).)

Service space means space provided in a building to facilitate or conceal the installation of building service facilities such as chutes, ducts, pipes, shafts or wires.

Service water heater means a device for heating water for plumbing services.

Shallow foundation means a foundation unit that derives its support from soil or rock located close to the lowest part of the building that it supports.

Smoke alarm means a combined smoke detector and audible alarm device designed to sound an alarm within the room or suite in which it is located upon the detection of smoke within that room or suite.

Smoke detector means a fire detector designed to operate when the concentration of airborne combustion products exceeds a predetermined level.

Soil means that portion of the earth's crust that is fragmentary, or such that some individual particles of a dried sample may be readily separated by agitation in water; it includes boulders, cobbles, gravel, sand, silt, clay and organic matter.

Solid masonry means a single wythe or multi-wythe construction made of solid masonry units or semi-solid, cored, or hollow masonry units, the cells of which may or may not be filled with mortar or grout. In multi-wythe masonry construction, the space between the wythes consists of a mortar-filled collar joint or grout-filled space and the wythes may or may not be constructed of the same masonry materials.

Solid masonry unit means a concrete block or brick unit, a clay brick unit, or calcium silicate brick unit whose net solid area is at least 75% of its gross area. (See Note A-1.4.1.2.(1).)

Sound transmission class (STC) means a single number rating of the airborne sound attenuation of a building assembly separating two adjoining spaces, taking into account the direct sound transmission path. (See Note A-1.4.1.2.(1).) (See also Note A-9.11. of Division B.)

Space heater means a space-heating appliance for heating the room or space within which it is located, without the use of ducts.

Space-heating appliance means an appliance intended for the supplying of heat to a room or space directly, such as a space heater, fireplace or unit heater, or to rooms or spaces of a building through a heating system such as a central furnace or boiler.

Sprinklered (as applying to a building or part thereof) means that the building or part thereof is equipped with a system of automatic sprinklers.

Stage means a space that is designed primarily for theatrical performances with provision for quick change scenery and overhead lighting, including environmental control for a wide range of lighting and sound effects and that is traditionally, but not necessarily, separated from the audience by a proscenium wall and curtain opening.

Storage garage means a building or part thereof intended for the storage or parking of motor vehicles and containing no provision for the repair or servicing of such vehicles. (See Note A-1.4.1.2.(1).)

Storage-type service water heater means a service water heater with an integral hot water storage tank.

Storey means that portion of a building that is situated between the top of any floor and the top of the floor next above it, and if there is no floor above it, that portion between the top of such floor and the ceiling above it.

Stove means an appliance intended for cooking and space heating.

Street means any highway, road, boulevard, square or other improved thoroughfare 9 m or more in width, that has been dedicated or deeded for public use and is accessible to fire department vehicles and equipment.

Subsurface investigation means the appraisal of the general subsurface conditions at a building site by analysis of information gained by such methods as geological surveys, in situ testing, sampling, visual inspection, laboratory testing of samples of the subsurface materials and groundwater observations and measurements.

Suite means a single room or series of rooms of complementary use, operated under a single tenancy, and includes dwelling units, individual guest rooms in motels, hotels, boarding houses, rooming houses and dormitories as well as individual stores and individual or complementary rooms for business and personal services occupancies. (See Note A-1.4.1.2.(1).)

Supply duct means a duct for conveying air from a heating, ventilating or air-conditioning appliance to a space to be heated, ventilated or air-conditioned.

Tapered tread means a tread with non-parallel edges that increases or decreases its run uniformly over its width.

Theatre means a place of public assembly intended for the production and viewing of the performing arts or the screening and viewing of motion pictures, and consisting of an auditorium with permanently fixed seats intended solely for a viewing audience.

Treatment means the provision of medical or other health-related intervention to persons, where the administration or lack of administration of these interventions may render them incapable of evacuating to a safe location without the assistance of another person. (See Note A-1.4.1.2.(1).)

Treatment occupancy (Group B, Division 2) means the occupancy or use of a building or part thereof for the provision of treatment, and where overnight accommodation is available to facilitate the treatment. (See Note A-1.4.1.2.(1).)

Unit heater means a suspended space heater with an integral air-circulating fan.

Unprotected opening (as applying to exposing building face) means a doorway, window or opening other than one equipped with a closure having the required fire-protection rating, or any part of a wall forming part of the exposing building face that has a fire-resistance rating less than that required for the exposing building face.

Unsafe condition means any condition that could cause undue hazard to the life, limb or health of any person authorized or expected to be on or about the premises.

Unstable liquid means a liquid, including flammable liquids and combustible liquids, that is chemically reactive to the extent that it will vigorously react or decompose at or near normal temperature and pressure conditions or that is chemically unstable when subjected to impact.

Vapour barrier means the elements installed to control the diffusion of water vapour. (See Note A-1.4.1.2.(1).)

Vent connector (as applying to heating or cooling systems) means the part of a venting system that conducts the flue gases or vent gases from the flue collar of a gas appliance to the chimney or gas vent, and may include a draft control device.

Vertical service space means a shaft oriented essentially vertically that is provided in a building to facilitate the installation of building services including mechanical, electrical and plumbing installations and facilities such as elevators, refuse chutes and linen chutes.

Walkway means a covered or roofed pedestrian thoroughfare used to connect 2 or more buildings.

1.4.2. Symbols and Other Abbreviations

1.4.2.1. Symbols and Other Abbreviations

1)   The symbols and other abbreviations in this Code shall have the meanings assigned to them in this Article and Article 1.3.2.1. of Division B.

1 in 2    slope of 1 vertical to 2 horizontal

cm    centimetre(s)

°    degree(s)

°C    degree(s) Celsius

dBA    A-weighted sound level

diam    diameter

g    gram(s)

h    hour(s)

HDD    heating degree-day(s)

HVAC    heating, ventilating and air-conditioning

Hz    hertz

J    joule(s)

K    degree(s) Kelvin

kg    kilogram(s)

kN    kilonewton(s)

kPa    kilopascal(s)

kW    kilowatt(s)

kWh    kilowatt hour(s)

L    litre(s)

lx    lux

m    metre(s)

M    metric nomenclature for reinforcing bars

max.    maximum

min.    minimum

min    minute(s)

MJ    megajoule(s)

mm    millimetre(s)

MPa    megapascal(s)

N    newton

n/a    not applicable

ng    nanogram(s)

No.    number(s)

o.c.    on centre

OSB    oriented strandboard

PM    particulate matter

ppb    part(s) per billion

ppm    part(s) per million

R    thermal resistance value (imperial unit)

RSI    thermal resistance value (metric unit)

s    second(s)

W    watt(s)

%    percent

µg    microgram(s)

µm    micrometre(s)

U-value    overall thermal transmittance

Section  1.5.   Referenced Documents and Organizations

1.5.1. Referenced Documents

1.5.1.1. Application of Referenced Documents

1)   Except as provided in Sentence (2), the provisions of documents referenced in this Code, and of any documents referenced within those documents, apply only to the extent that they relate to

a)   buildings, and

b)   the objectives and functional statements attributed to the applicable acceptable solutions in Division B where the documents are referenced.

(See Note A-1.5.1.1.(1).)

2)   Where a provision of this Code references the British Columbia Fire Code, the NECB, or Book II (Plumbing Systems) of this Code the applicable objectives and functional statements shall include those found in that referenced document. (See Note A-2.1.1.2.(6).)

1.5.1.2. Conflicting Requirements

1)   In case of conflict between the provisions of this Code and those of a referenced document, the provisions of this Code shall govern.

1.5.1.3. Applicable Editions

1)   Where documents are referenced in this Code, they shall be the editions designated in Subsection 1.3.1. of Division B.

1.5.2. Organizations

1.5.2.1. Abbreviations of Proper Names

1)   The abbreviations of proper names in this Code shall have the meanings assigned to them in Article 1.3.2.1. of Division B.

Notes to Part 1

Compliance

A-1.1.1.1.(3)   Factory-Constructed Buildings. The British Columbia Building Code applies the same requirements to site-built and factory-constructed buildings. However, it can often be difficult to determine whether a factory-constructed building complies with the Code once it has been delivered to the construction site because many of the wall, roof and floor assemblies are closed in and so their components cannot be inspected. CSA A277, “Procedure for certification of prefabricated buildings, modules, and panels,” was developed to address this problem with regard to residential, commercial and industrial buildings. This standard describes a procedure whereby an independent certification agency can review the quality control procedures of a factory and make periodic unannounced inspections of its products. The standard is not a building code, only a procedure for certifying compliance of factory-constructed components with a building code or other standard. If a factory-constructed building bears the label of an accredited certification agency indicating that compliance with the National Building Code has been certified using the CSA A277 procedure, the accepting authority will have some assurance that the concealed components do not require re-inspection on site.

On the other hand, standards in the CSA Z240 MH Series, “Manufactured homes,” do resemble a building code. Most of the individual standards in the series contain requirements regarding many issues also covered in this Code. Some of these Z240 MH Series provisions are performance requirements with no quantitative criteria, some simply reference the applicable British Columbia Building Code requirements, while others contain requirements that differ from those in the British Columbia Building Code. One of the individual standards in the Z240 MH Series deals with special requirements for manufactured homes related to the fact that these houses must be moved over roads, which is an issue the British Columbia Building Code does not address. Therefore, labeling that indicates that a factory-constructed house complies with the Z240 MH Series standards can NOT be taken as an indication that the house necessarily complies with the building code in effect for the location where the house will be sited.

The British Columbia Building Code does reference CSA Z240.10.1, “Site preparation, foundation, and installation of buildings,” which is not actually part of the CSA Z240 MH Series. This standard contains requirements for surface foundations where buildings—not just houses—comply with the deformation resistance test provided in CSA Z240.2.1, “Structural requirements for manufactured homes.”

A-1.1.1.1.(5)   Heritage Buildings. Many local governments have identified conservation of selected heritage properties, or protection of the heritage character of certain areas, as being community planning objectives. The Province’s planning objectives and growth strategy encourage and support local government in this effort. The key is to find ways to make restoration and rehabilitation of heritage buildings economically viable for the properties’ owners.

It is generally recognized that the present British Columbia Building Code was primarily written for new construction and provides for a performance level that is significantly higher than what exists with many older buildings. To apply present Code provisions to existing buildings is, in many cases, impractical and with heritage buildings may compromise historic appearances or authenticity. Therefore, the Table of Alternate Compliance Methods for Heritage Buildings was developed to provide alternate methods for complying with the performance level intended by the Code. The use of sprinklers is advocated as one of the primary methods in assuring this performance level for heritage buildings. Sprinkler systems not only control the fire, which aids evacuation, but also provides the added benefit of protecting the building from possible destruction by fire.

The Table of Alternative Compliance Methods for Heritage Buildings represents some of the ways that restoration and rehabilitation of heritage buildings can be facilitated without compromising the objectives of the Code. Only buildings which have been identified by the provincial or a local government are included in the definition of “heritage building.” For these buildings, conservation is also a public objective. Heritage buildings often offer unique problems and opportunities, and each situation must be assessed individually.

The use of the Alternate Compliance Methods in Table A-1.1.1.1.(5) is not mandatory, and an owner may choose

- to apply acceptable solutions in Division B,

- to apply alternate solutions under Clause 1.2.1.1.(1)(b),

- to apply alternate compliance methods in Table A-1.1.1.1.(5), or

- to combined these options.

A-1.1.1.1.(6) Alternate Compliance Methods for Alterations to Existing Buildings to Add a Secondary Suite. The requirements in Division B for the construction of secondary suites was written primarily for new construction and provides for a performance level that is higher than what may exist in existing buildings. To apply present Code provisions to existing buildings is in many cases impractical. The Table of Alternate Compliance Methods for Alterations to Existing Buildings to Add a Secondary Suite was developed to provide alternate methods, when dealing with existing construction, without compromising the objectives of the Code. Table 1.1.1.1.(6) may be considered when assessing an existing additional dwelling unit located in a single family dwelling building (house), however is not intended to be applied as a retroactive code to these existing units, nor be applied to buildings of new construction where there are no existing assemblies to act as practical barriers to compliance with Division B of this Code. Figure A-1.1.1.1.(6) illustrates the application of Table 1.1.1.1.(6) to existing buildings.

Figure A-1.1.1.1.(6)
Application of Alternative Compliance Methods in Table 1.1.1.1.(6)

Table A-1.1.1.1.(6) is not mandatory, and an owner may choose to

- apply acceptable solutions in Division B,

- apply alternative solutions under Clause 1.2.1.1.(1)(b),

- apply alternate compliance methods in Table A-1.1.1.1.(6), or

- combined these options.

A-1.1.1.2.(1)   Application to Existing Buildings. This Code is most often applied to existing or relocated buildings when an owner wishes to rehabilitate a building, change its use, or build an addition, or when an enforcement authority decrees that a building or class of buildings be altered for reasons of public safety. It is not intended that the British Columbia Building Code be used to enforce the retrospective application of new requirements to existing buildings or existing portions of relocated buildings, unless specifically required by local regulations or bylaws. For example, although the British Columbia Fire Code could be interpreted to require the installation of fire alarm, standpipe and hose, and automatic sprinkler systems in an existing building for which there were no requirements at the time of construction, it is not intented that the British Columbia Fire Code be applied in this manner to these buildings unless the authority having jurisdiction has determined that there is an inherent threat to occupant safety and has issued an order to eliminate the unsafe condition, or where substantial changes or additions are being made to an existing building or the occupancy has been changed. (See also Note A-1.1.1.1.(1) of Division A of the British Columbia Fire Code.)

Relocated buildings that have been in use in another location for a number of years can be considered as existing buildings, in part, and the same analytical process can be applied as for existing buildings. It should be noted, however, that a change in occupancy may affect some requirements (e.g. loads and fire separations) and relocation to an area with different wind, snow or earthquake loads will require the application of current code requirements. Depending on the construction of the building and the changes in load, structural modifications may be required. Similarly, parts of a relocated or existing building that are reconstructed, such as foundations and basements, or parts being modified are required to be built to current codes.

Whatever the reason, Code application to existing or relocated buildings requires careful consideration of the level of safety needed for that building. This consideration involves an analytical process similar to that required to assess alternative design proposals for new construction. See Clause 1.2.1.1.(1)(b) for information on achieving compliance with the Code using alternative solutions.

In developing Code requirements for new buildings, consideration has been given to the cost they impose on a design in relation to the perceived benefits in terms of safety. The former is definable; the latter difficult to establish on a quantitative basis. In applying the Code requirements to an existing building, the benefits derived are the same as in new buildings. On the other hand, the increased cost of implementing in an existing building a design solution that would normally be intended for a new building may be prohibitive.

The successful application of Code requirements to existing construction becomes a matter of balancing the cost of implementing a requirement with the relative importance of that requirement to the overall Code objectives. The degree to which any particular requirement can be relaxed without affecting the intended level of safety of the Code requires considerable judgment on the part of both the designer and the authority having jurisdiction.

Further information on the application of Code requirements to existing or relocated buildings can be found in the following publications:

•   “User's Guide – NBC 1995 Fire Protection, Occupant Safety and Accessibility (Part 3)”

•   “Guidelines for Application of Part 3 of the National Building Code of Canada to Existing Buildings”

•   Commentary entitled “Application of NBC Part 4 of Division B for the Structural Evaluation and Upgrading of Existing Buildings” of the “Structural Commentaries (User's Guide – NBC 2020: Part 4 of Division B)”

•   “User's Guide – NBC 1995, Application of Part 9 to Existing Buildings”

•   CBD 230, “Applying building codes to existing buildings”

These publications can be accessed through the NRC Publications Archive at https://nrc-publications.canada.ca.

A-1.2.1.1.(1)(a)   Code Compliance via Acceptable Solutions. If a building design (e.g. material, component, assembly or system) can be shown to meet all provisions of the applicable acceptable solutions in Division B (e.g. it complies with the applicable provisions of a referenced standard), it is deemed to have satisfied the objectives and functional statements linked to those provisions and thus to have complied with that part of the Code. In fact, if it can be determined that a design meets all the applicable acceptable solutions in Division B, there is no need to consult the objectives and functional statements in Division A to determine its compliance.

A-1.2.1.1.(1)(b)   Code Compliance via Alternative Solutions. Where a design differs from the acceptable solutions in Division B, then it should be treated as an “alternative solution.” A proponent of an alternative solution must demonstrate that the alternative solution addresses the same issues as the applicable acceptable solutions in Division B and their attributed objectives and functional statements. However, because the objectives and functional statements are entirely qualitative, demonstrating compliance with them in isolation is not possible. Therefore, Clause 1.2.1.1.(1)(b) identifies the principle that Division B establishes the quantitative performance targets that alternative solutions must meet. In many cases, these targets are not defined very precisely by the acceptable solutions—certainly far less precisely than would be the case with a true performance code, which would have quantitative performance targets and prescribed methods of performance measurement for all aspects of building performance. Nevertheless, Clause 1.2.1.1.(1)(b) makes it clear that an effort must be made to demonstrate that an alternative solution will perform as well as a design that would satisfy the applicable acceptable solutions in Division B—not “well enough” but “as well as.”

In this sense, it is Division B that defines the boundaries between acceptable risks and the “unacceptable” risks referred to in the statements of the Code's objectives, i.e. the risk remaining once the applicable acceptable solutions in Division B have been implemented represents the residual level of risk deemed to be acceptable by the broad base of Canadians who have taken part in the consensus process used to develop the Code.

Level of Performance

Where Division B offers a choice between several possible designs, it is likely that these designs may not all provide exactly the same level of performance. Among a number of possible designs satisfying acceptable solutions in Division B, the design providing the lowest level of performance should generally be considered to establish the minimum acceptable level of performance to be used in evaluating alternative solutions for compliance with the Code.

Sometimes a single design will be used as an alternative solution to several sets of acceptable solutions in Division B. In this case, the level of performance required of the alternative solution should be at least equivalent to the overall level of performance established by all the applicable sets of acceptable solutions taken as a whole.

Each provision in Division B has been analyzed to determine what it is intended to achieve. The resultant intent statements clarify what undesirable results each provision seeks to preclude. These statements are not a legal component of the Code, but are advisory in nature, and can help Code users establish performance targets for alternative solutions. They are published as a separate electronic document entitled “Supplement to the NBC 2020: Intent Statements,” which is available on the NRC's website.  These intent statements should be cross referenced with the associated requirements of the British Columbia Building Code.

Areas of Performance

A subset of the acceptable solutions in Division B may establish criteria for particular types of designs (e.g. certain types of materials, components, assemblies, or systems). Often such subsets of acceptable solutions are all attributed to the same objective: OS1, Fire Safety, for example. In some cases, the designs that are normally used to satisfy this subset of acceptable solutions might also provide some benefits that could be related to some other objective: OP1, Fire Protection of the Building, for example. However, if none of the applicable acceptable solutions are linked to Objective OP1, it is not necessary that alternative solutions proposed to replace these acceptable solutions provide a similar benefit related to Fire Protection of the Building. In other words, the acceptable solutions in Division B establish acceptable levels of performance for compliance with the Code only in those areas defined by the objectives and functional statements attributed to the acceptable solutions.

Applicable Acceptable Solutions

In demonstrating that an alternative solution will perform as well as a design that would satisfy the applicable acceptable solutions in Division B, its evaluation should not be limited to comparison with the acceptable solutions to which an alternative is proposed. It is possible that acceptable solutions elsewhere in the Code also apply. The proposed alternative solution may be shown to perform as well as the most apparent acceptable solution which it is replacing but may not perform as well as other relevant acceptable solutions. For example, an innovative sheathing material may perform adequately as sheathing in a wall system that is braced by other means but may not perform adequately as sheathing in a wall system where the sheathing must provide the structural bracing. All applicable acceptable solutions should be taken into consideration in demonstrating the compliance of an alternative solution.

A-1.2.1.2.(1) Responsibility of Owner. Sentence 1.1.1.1.(1) is not intended to imply that a person who becomes the owner of a building must bring the entire building into compliance with the Code. The Code applies only in the cases and to the extent specified by Article 1.1.1.1., and the owner of a building is therefore made responsible for ensuring the building complies with the Code by Sentence 1.2.1.2.(1) only in the cases and to the extent specified by Article 1.1.1.1. If none of the provisions in Sentence 1.1.1.1.(1) apply to the building, the owner is not required to make any changes to the building.

A-1.3.3.4.(1)   Buildings Divided by Firewalls. This concept relates to the provisions directly regulated by this Code and does not apply to electrical service entrance requirements, which are regulated by other documents.

A-1.3.3.4.(2)   Buildings on Sloping Sites. Application of the definition of grade to stepped buildings on sloping sites often results in such buildings being designated as being greater than 4 storeys in building height even though there may be only 2, 3 or 4 storeys at any one location. Figure A-1.3.3.4.(2) illustrates this application compared to a similar building on a flat site.

Under Sentence 1.3.3.4.(2), Building A can be considered as being 4 storeys in building height instead of 7 storeys in building height. Both Building A and B are comparable with regard to fire safety and egress.

This relaxation applies to the determination of building height only. All other requirements continue to apply as appropriate.

Figure A-1.3.3.4.(2)

Application of the definition of grade

A-1.4.1.2.(1)   Defined Terms.

ASTC and STC

The higher the ASTC or STC rating, the more the assembly or the system of assemblies protects occupants from noise in adjacent spaces.

These ratings, which are determined in accordance with ASTM E413, “Classification for Rating Sound Insulation,” roughly describe the noise reduction provided by the separating floor or wall, or in the case of the ASTC rating, by the system of separating and adjoining walls and floors.

Care Occupancy

Support services rendered by or through care facility management refer to services provided by the organization that is responsible for the care for a period exceeding 24 consecutive hours. They do not refer to services provided by residents of dwelling units or suites, or to services arranged directly by residents of dwelling units or suites with outside agencies.

In the context of care occupancies, these services may include a daily assessment of the resident's functioning, awareness of their whereabouts, the making of appointments for residents and reminding them of those appointments, the ability and readiness to intervene if a crisis arises for a resident, supervision in areas of nutrition or medication, and provision of transient medical services. Services may also include activities of daily living such as bathing, dressing, feeding, and assistance in the use of washroom facilities, etc. No actual treatment is provided by or through care facility management.

Dangerous Goods

In previous editions of the British Columbia Building Code, the terminology used to identify dangerous goods came from “Transportation of Dangerous Goods Regulations (TDGR).” The TDGR apply solely to the adequate identification of hazards related to dangerous goods in the contexts of transportation and emergency response.

Dangerous goods in the workplace are identified in accordance with the “Workplace Hazardous Materials Information System (WHMIS),” established in accordance with the “Hazardous Products Act.” The WHMIS identification system is specifically designed with the users of the product in mind.

This edition of the British Columbia Building Code identifies dangerous goods as products regulated by the TDGR or classified under the WHMIS. In order to harmonize these two nomenclatures for dangerous goods, class descriptors were developed taking into consideration both the TDGR and WHMIS classification systems. The NBC nomenclature uses a descriptive approach to classifying dangerous goods, which is similar to the one used by the Globally Harmonized System of Classification and Labelling of Chemicals (GHS) developed by the United Nations (UN). Canada has actively participated in the development of the GHS and has committed to its implementation through the TDGR and WHMIS regulations.

The British Columbia Building Code 2018 nomenclature takes a common sense approach that corresponds more closely to how people refer to dangerous goods on a daily basis, blending TDGR and WHMIS terminology without using nondescript numbers and letters as previously found in the British Columbia Building Code, TDGR and WHMIS.

Table A-1.4.1.2.(1)

TDGR, WHMIS and British Columbia Building Code Class Descriptors for Dangerous Goods

| TDGR |  | WHMIS | British Columbia Building Code |
| --- | --- | --- | --- |
| Class | Descriptor |  |  |
| 1 | Explosives | Explosives | Explosives |
| 2 | Gases | Gases under pressure | Compressed gases |
| 2.1 | Flammable gases | Flammable gases; Flammable aerosols | Flammable gases; Flammable aerosols |
| 2.2 | Non-flammable, non-toxic gases | Gases under pressure | Non-flammable, non-toxic gases |
| 2.2 (5.1) | — | Oxidizing gases | Oxidizing gases |
| 2.3 | Toxic gases | — | Toxic gases |
| 3 | Flammable liquids | Flammable liquids | Flammable liquids |
| 4.1 | Flammable solids | Flammable solids | Flammable solids |
| 4.2 | Substances liable to spontaneous combustion | Pyrophoric liquids; pyrophoric solids | Pyrophoric materials |
| 4.3 | Water-reactive substances | Substances and mixtures which, in contact with water, emit flammable gases | Water-reactive substances |
| 5.1 | Oxidizing substances | Oxidizing liquids; oxidizing solids | Oxidizers |
| 5.2 | Organic peroxides | Organic peroxides | Organic peroxides |
| 6.1 | Toxic substances | (1) | Toxic substances |
| 6.2 | Infectious substances | (1) | Infectious materials |
| 7 | Radioactive materials | Not covered by WHMIS | Radioactive materials |
| 8 | Corrosives | (2) | Corrosives |
| 9 | Miscellaneous products, substances, or organisms | (2) | Miscellaneous dangerous goods |
| — | — | Previously Class F | Dangerously reactive materials |

Notes to Table A-1.4.1.2.(1):

(1) The WHMIS has various descriptors for this Class of products based on their toxicity.

(2) The WHMIS has various descriptors for this Class of products based on the nature of the danger presented by the product.

Exit

Exits include doors or doorways leading directly into an exit stair or directly to the outside. In the case of an exit leading to a separate building, exits also include vestibules, walkways, bridges or balconies.

Farm Building

Farm buildings as defined in Article 1.4.1.2. include, but are not limited to, produce storage and packing facilities, livestock and poultry housing, milking centres, manure storage facilities, grain bins, silos, feed preparation centres, farm workshops, greenhouses, farm retail centres, and horse riding, exercise and training facilities. Farm buildings may be classified as low or high human occupancy, depending on the occupant load.

Examples of farm buildings that may be classified as low human occupancy are livestock and poultry housing, manure and machinery storage facilities and horse exercise and training facilities where no bleachers or viewing area are provided.

Examples of farm buildings that may be classified as other than low human occupancy include farm retail centres for feeds, horticultural and livestock produce, auction barns and show areas where bleachers or other public facilities are provided. Farm work centres where the number of workers frequently exceeds the limit for low human occupancy will also be in this category.

It is possible to have areas of both high and low human occupancy in the same building provided that the structural safety and fire separation requirements for high human occupancy are met in the part thus designated.

Fire Separation

It is generally understood that the term “fire” refers to all products of combustion, including heat and smoke. Although a fire separation is not always required to have a fire-resistance rating, it should act as a barrier to the spread of smoke and fire until some type of response is initiated. If the fire-resistance rating of a fire separation is permitted to be waived on the basis of the presence of an automatic sprinkler system, it is nonetheless the intent of the Code that the fire separation be constructed so that it will remain in place and act as a barrier against the spread of smoke until the sprinklers have actuated.

Flight

Figure A-1.4.1.2.(1)-A

Flight

Grade

Localized depressions that need not be considered in the determination of the elevation of grade include such features as vehicle and pedestrian entrances and other minor depressions that do not affect accessibility for firefighting or evacuation.

Mechanically Vented

The definition of this term is intended to include all types of appliances and venting systems that rely entirely on fans to evacuate the products of combustion. Systems variously referred to as “forced draft,” “power vented” and “induced draft” in standards and industry terminology may be covered by this definition. The key characteristic of such systems is that they are more resistant to depressurization-induced spillage of combustion products into the building in which they are housed because the combustion venting system downstream of the fan is “sealed,” i.e. includes no draft hood or draft control device.

Post-Disaster Building

There may be circumstances where the authority having jurisdiction would choose to exempt certain types of buildings or parts thereof from being designated as post-disaster buildings. Such is the case in the following examples: a volunteer paramedic's residence where an ambulance is stored, or a police station in a shopping mall or in a residential complex.

Some municipalities have emergency management plans that specify which buildings are to be used for the provision of essential services after a disaster. Municipalities normally coordinate their requirements with provincial or territorial emergency management protocols, which may or may not be mandatory. If in doubt about whether a building should be designated as a post-disaster building, designers should consult with the authority having jurisdiction.

The inclusion of control centres for natural gas distribution as examples of post-disaster buildings is intended to ensure that, following a disaster, control is maintained over large fuel distribution networks that supply a commodity essential to the health and safety of a significant proportion of the Canadian population. In contrast, the localized failure of a single fuel supply point does not jeopardize the entire fuel distribution system.

Buildings with rooftop telecommunication or cellular network equipment need not be designated as post-disaster buildings.

Public Corridor

A covered mall is considered to be a public corridor and, as such, is subject to the same requirements as a public corridor.

Rim Joist

In the field, rim joists may also be referred to as rim boards, headers or header joists.

Secondary Suite

A secondary suite is a self-contained dwelling unit that is part of a house containing not more than two dwelling units (including the secondary suite) and any common spaces such as common storage, common service rooms, common laundry facilities or common areas used for egress. Secondary suites are typically created within an existing single dwelling unit—commonly called a “house”—either constructed as an addition or an alteration to an existing house or incorporated during the construction of a new house. A secondary suite may have more than one storey and may be on the same level as the other dwelling unit of the house or be above or below it.

Examples of buildings where secondary suites are permitted include individual detached houses, or where the secondary suite is located in a portion of a building, semi-detached houses (half of a double and also known as a side-by-side) and row houses where a vertical fire separation separates the portion from the remainder of the building.

Where a building has multiple vertically separated occupancies, the secondary suite can only be created in a vertically separated portion of the building that is of residential occupancy. A vertical fire separation extends continuously through all crawlspaces, storeys and attic spaces of the building. Apartment buildings have dwelling units above and below others that share a horizontal assembly and are therefore not permitted to have secondary suites. Figure A-1.4.1.2.(1)-C shows building types where secondary suites are permitted as well as building types where other dwelling units or other occupancies are located above or below such that secondary suites are not permitted.

Figure A-1.4.1.2.(1)-C
Building Types where Secondary Suites are Permitted

Neither dwelling unit in a house can be strata-titled or otherwise subdivided from the remainder of the house under provincial or territorial legislation. This means that both dwelling units are registered under the same title.

Service Room

Typical examples of service rooms include boiler rooms, furnace rooms, incinerator rooms, garbage handling rooms and rooms to accommodate air-conditioning or heating appliances, pumps, compressors and electrical equipment. Rooms such as elevator machine rooms and common laundry rooms are not considered to be service rooms.

Solid Masonry Units

The net solid area of a masonry unit is calculated by determining the gross area of the bed face of the unit (L × T) and subtracting the cumulative areas of the hollow portions. As long as the total area of the hollow portions is 25% or less of the gross area, the unit is considered to be a solid masonry unit.

Figure A-1.4.1.2.(1)-B

Net solid area of masonry unit

Storage Garage

Entrances at which vehicles stop for a short time beneath an unenclosed canopy to pick up and drop off passengers are not considered as storage garages. As a subsidiary use, storage garages may also contain space for parking or storing other vehicles (bicycles, boat, etc.).

Suite

Tenancy in the context of the term “suite” applies to both rental and ownership tenure. In a condominium arrangement, for example, dwelling units are considered separate suites even though they are individually owned. In order to be of complementary use, a series of rooms that constitute a suite must be in reasonably close proximity to each other and have access to each other either directly by means of a common doorway or indirectly by a corridor, vestibule or other similar arrangement.

The term “suite” does not apply to rooms such as service rooms, common laundry rooms and common recreational rooms that are not leased or under a separate tenure in the context of the Code. Similarly, the term “suite” is not normally applied in the context of buildings such as schools and hospitals, since the entire building is under a single tenure. However, a room that is individually rented is considered a suite. A warehousing unit in a mini-warehouse is a suite. A rented room in a nursing home could be considered as a suite if the room was under a separate tenure. A hospital bedroom on the other hand is not considered to be under a separate tenure, since the patient has little control of that space, even though he pays the hospital a per diem rate for the privilege of using the hospital facilities, which include the sleeping areas.

For certain requirements in the Code, the expression “room or suite” is used (e.g., travel distance). This means that the requirement applies within the rooms of suites as well as to the suite itself and to rooms that may be located outside the suite. In other places the expression “suite, and rooms not located within a suite” is used (e.g., for the installation of smoke and heat detectors). This means that the requirement applies to individual suites as defined, but not to each room within the suite. The rooms “not within a suite” would include common laundry rooms, common recreational rooms and service rooms, which are not considered as tenant-occupied space.

Tapered Tread

The definition of tapered tread includes treads in curved stairs and treads in winder stairs, However, requirements for winders differ from those for other tapered treads. Requirements for tapered treads are found in Articles 3.3.1.16., 3.4.6.9., and 9.8.4.3. of Division B. Requirements for winders are found in Article 9.8.4.6. of Division B.

Treatment

The ability to evacuate unassisted implies that a person is capable of recognizing and responding to an emergency given their physical, cognitive and behavioural abilities, and able to move to a safe location without the assistance of another person. For example, such persons must be able to arise and walk, or transfer from a bed or chair to a means of mobility, and leave the building or move to a safe location on their own.

Treatment Occupancy

“Treatments” may include such things as surgery, intensive care, and emergency medical intervention. Treatment services differ from the services provided by care occupancies like personal care assistance or the administration of medication, and from those provided by business and personal services occupancies like dentistry or day procedures.

Vapour Barrier

It is important to understand the difference between the functions of a vapour barrier and an air barrier. Vapour barrier materials and assemblies are intended to restrict the movement of water vapour due to vapour pressure differentials, while air barrier materials and assemblies are intended to restrict the movement of air due to air pressure differentials.

Note that a vapour barrier is also referred to as a “vapour diffusion retarder.”

A-1.5.1.1.(1)   Application of Referenced Documents. Documents referenced in the British Columbia Building Code may contain provisions covering a wide range of issues, including issues that are unrelated to the objectives and functional statements stated in Parts 2 and 3 of Division A respectively; e.g. aesthetic issues such as colour-fastness or uniformity. Sentence 1.5.1.1.(1) is intended to make it clear that, whereas referencing a document in the Code generally has the effect of making the provisions of that document part of the Code, provisions that are unrelated to buildings or to the objectives and functional statements attributed to the provisions in Division B where the document is referenced are excluded.

Furthermore, many documents referenced in the Code contain references to other documents, which may also, in turn, refer to other documents. These secondary and tertiary referenced documents may contain provisions that are unrelated to buildings or to the objectives and functional statements of the Code: such provisions—no matter how far down the chain of references they occur—are not included in the intent of Sentence 1.5.1.1.(1).

Part 2

Objectives

Section  2.1.   Application

2.1.1. Application

2.1.1.1. Application

1)   This Part applies to all buildings covered in this Code. (See Article 1.1.1.1.)

2.1.1.2. Application of Objectives

(See Note A-2.2.1.1.(1).)

1)   Except as provided in Sentences (2) to (6), the objectives described in this Part apply

a)   to all buildings covered in this Code (see Article 1.1.1.1.), and

b)   only to the extent that they relate to compliance with this Code as required in Article 1.2.1.1.

2)   Objective OS4, Resistance to Unwanted Entry, applies only to dwelling units in buildings covered in Part 9 of Division B. (See Article 1.3.3.3.)

3)   Objective OH3, Noise Protection, applies only to dwelling units.

4)   Objective OH5, Hazardous Substances Containment, applies only to the extent defined in

a)   Book II (Plumbing Systems) of this Code, and

b)   the British Columbia Fire Code.

5)   Objective OA, Accessibility (including Objectives OA1, Accessible Path of Travel, and OA2, Accessible Facilities), does not apply to

a)   detached houses, semi-detached houses, houses with a secondary suite, duplexes, triplexes, townhouses, row houses and boarding houses (see Note A-1.4.1.2.(1), Secondary Suite),

b)   buildings of Group F, Division 1 major occupancy, and

c)   buildings that are not intended to be occupied on a daily or full-time basis, including automatic telephone exchanges, pumphouses and substations.

6)   Objective OE, Environment, applies only to

a)   buildings of residential occupancy to which Part 9 of Division B applies,

b)   buildings containing business and personal services, mercantile or low-hazard industrial occupancies to which Part 9 of Division B applies whose combined total floor area does not exceed 300 m2, and

c)   buildings containing a mix of the residential and non-residential occupancies described in Clauses (a) and (b).

(See Note A-2.1.1.2.(6).) (See also Article 1.3.3.3.)

Section  2.2.   Objectives

2.2.1. Objectives

2.2.1.1. Objectives

1)   The objectives of this Code are as follows (see Note A-2.2.1.1.(1)):

OS Safety

An objective of this Code is to limit the probability that, as a result of the design, construction or demolition of the building, a person in or adjacent to the building will be exposed to an unacceptable risk of injury.

OS1 Fire Safety

An objective of this Code is to limit the probability that, as a result of the design or construction of the building, a person in or adjacent to the building will be exposed to an unacceptable risk of injury due to fire. The risks of injury due to fire addressed in this Code are those caused by—

OS1.1– fire or explosion occurring

OS1.2– fire or explosion impacting areas beyond its point of origin

OS1.3– collapse of physical elements due to a fire or explosion

OS1.4– fire safety systems failing to function as expected

OS1.5– persons being delayed in or impeded from moving to a safe place during a fire emergency

OS2 Structural Safety

An objective of this Code is to limit the probability that, as a result of the design or construction of the building, a person in or adjacent to the building will be exposed to an unacceptable risk of injury due to structural failure. The risks of injury due to structural failure addressed in this Code are those caused by—

OS2.1– loads bearing on the building elements that exceed their loadbearing capacity

OS2.2– loads bearing on the building that exceed the loadbearing properties of the supporting medium

OS2.3– damage to or deterioration of building elements

OS2.4– vibration or deflection of building elements

OS2.5– instability of the building or part thereof

OS2.6– collapse of the excavation

OS3 Safety in Use

An objective of this Code is to limit the probability that, as a result of the design or construction of the building, a person in or adjacent to the building will be exposed to an unacceptable risk of injury due to hazards. The risks of injury due to hazards addressed in this Code are those caused by—

OS3.1– tripping, slipping, falling, contact, drowning or collision

OS3.2– contact with hot surfaces or substances

OS3.3– contact with energized equipment

OS3.4– exposure to hazardous substances

OS3.5– exposure to high levels of sound from fire alarm systems

OS3.6– persons becoming trapped in confined spaces

OS3.7– persons being delayed in or impeded from moving to a safe place during an emergency (see Note A-2.2.1.1.(1))

OS4 Resistance to Unwanted Entry

An objective of this Code is to limit the probability that, as a result of the design or construction of the building, a person in the building will be exposed to an unacceptable risk of injury due to the building's low level of resistance to unwanted entry (see Sentence 2.1.1.2.(2) for application limitation). The risks of injury due to unwanted entry addressed in this Code are those caused by—

OS4.1– intruders being able to force their way through locked doors or windows

OS4.2– occupants being unable to identify potential intruders as such

OS5 Safety at Construction and Demolition Sites

An objective of this Code is to limit the probability that, as a result of the construction or demolition of the building, the public adjacent to a construction or demolition site will be exposed to an unacceptable risk of injury due to hazards. The risks of injury due to construction and demolition hazards addressed in this Code are those caused by—

OS5.1– objects projected onto public ways

OS5.2– vehicular accidents on public ways

OS5.3– damage to or obstruction of public ways

OS5.4– water accumulated in excavations

OS5.5– entry into the site

OS5.6– exposure to hazardous substances and activities

OS5.7– loads bearing on a covered way that exceed its loadbearing capacity

OS5.8– collapse of the excavation

OS5.9– persons being delayed in or impeded from moving to a safe place during an emergency (see Note A-2.2.1.1.(1))

OH Health

An objective of this Code is to limit the probability that, as a result of the design or construction of the building, a person will be exposed to an unacceptable risk of illness.

OH1 Indoor Conditions

An objective of this Code is to limit the probability that, as a result of the design or construction of the building, a person in the building will be exposed to an unacceptable risk of illness due to indoor conditions. The risks of illness due to indoor conditions addressed in this Code are those caused by—

OH1.1– inadequate indoor air quality

OH1.2– inadequate thermal comfort

OH1.3– contact with moisture

OH2 Sanitation

An objective of this Code is to limit the probability that, as a result of the design or construction of the building, a person in the building will be exposed to an unacceptable risk of illness due to unsanitary conditions. The risks of illness due to unsanitary conditions addressed in this Code are those caused by—

OH2.1– exposure to human or domestic waste

OH2.2– consumption of contaminated water

OH2.3– inadequate facilities for personal hygiene

OH2.4– contact with contaminated surfaces

OH2.5– contact with vermin and insects

OH3 Noise Protection

An objective of this Code is to limit the probability that, as a result of the design or construction of the building, a person in the building will be exposed to an unacceptable risk of illness due to high levels of sound originating in adjacent spaces in the building (see Sentence 2.1.1.2.(3) for application limitation). The risks of illness due to high levels of sound addressed in this Code are those caused by—

OH3.1– exposure to airborne sound transmitted through assemblies separating dwelling units from adjacent spaces in the building

OH4 Vibration and Deflection Limitation

An objective of this Code is to limit the probability that, as a result of the design or construction of the building, a person in the building will be exposed to an unacceptable risk of illness due to high levels of vibration or deflection of building elements.

OH5 Hazardous Substances Containment

An objective of this Code is to limit the probability that, as a result of the design or construction of the building, the public will be exposed to an unacceptable risk of illness due to the release of hazardous substances from the building (see Sentence 2.1.1.2.(4) for application limitation).

OA Accessibility

An objective of this Code is to limit the probability that, as a result of the design or construction of the building, persons with disabilities will be unacceptably impeded from accessing or using the building or its facilities (see Sentence 2.1.1.2.(5) for application limitations).

OA1 Accessible Path of Travel

An objective of this Code is to limit the probability that, as a result of the design or construction of the building, persons with disabilities will be unacceptably impeded from accessing the building or circulating within it (see Sentence 2.1.1.2.(5) for application limitations).

OA2 Accessible Facilities

An objective of this Code is to limit the probability that, as a result of the design or construction of the building, persons with disabilities will be unacceptably impeded from using the building's facilities (see Sentence 2.1.1.2.(5) for application limitations).

OP Fire and Structural Protection of Buildings

An objective of this Code is to limit the probability that, as a result of the design, construction or demolition of the building, the building or adjacent buildings will be exposed to an unacceptable risk of damage due to fire or structural insufficiency, or the building or part thereof will be exposed to an unacceptable risk of loss of use also due to structural insufficiency.

OP1 Fire Protection of the Building

An objective of this Code is to limit the probability that, as a result of its design or construction, the building will be exposed to an unacceptable risk of damage due to fire. The risks of damage due to fire addressed in this Code are those caused by—

OP1.1– fire or explosion occurring

OP1.2– fire or explosion impacting areas beyond its point of origin

OP1.3– collapse of physical elements due to a fire or explosion

OP1.4– fire safety systems failing to function as expected

OP2 Structural Sufficiency of the Building

An objective of this Code is to limit the probability that, as a result of its design or construction, the building or part thereof will be exposed to an unacceptable risk of damage or loss of use due to structural failure or lack of structural serviceability. The risks of damage and of loss of use due to structural failure or lack of structural serviceability addressed in this Code are those caused by—

OP2.1– loads bearing on the building elements that exceed their loadbearing capacity

OP2.2– loads bearing on the building that exceed the loadbearing properties of the supporting medium

OP2.3– damage to or deterioration of building elements

OP2.4– vibration or deflection of building elements

OP2.5– instability of the building or part thereof

OP2.6– instability or movement of the supporting medium

OP3 Protection of Adjacent Buildings from Fire

An objective of this Code is to limit the probability that, as a result of the design or construction of the building, adjacent buildings will be exposed to an unacceptable risk of damage due to fire. The risks of damage to adjacent buildings due to fire addressed in this Code are those caused by—

OP3.1– fire or explosion impacting areas beyond the building of origin

OP4 Protection of Adjacent Buildings from Structural Damage

An objective of this Code is to limit the probability that, as a result of the design, construction or demolition of the building, adjacent buildings will be exposed to an unacceptable risk of structural damage. The risks of structural damage to adjacent buildings addressed in this Code are those caused by—

OP4.1– settlement of the medium supporting adjacent buildings

OP4.2– collapse of the building or portion thereof onto adjacent buildings

OP4.3– impact of the building on adjacent buildings

OP4.4– collapse of the excavation

OE Environment

An objective of this Code is to limit the probability that, as a result of the design, construction or renovation of the building or of the plumbing system, the environment will be affected in an unacceptable manner.

OE1 Energy Efficiency and Water Use

An objective of this Code is to limit the probability that, as a result of the design, construction or renovation of the building, the use of energy will be inefficient or the use of water will be excessive. The risks of inefficient energy use or excessive water use addressed in this Code are those caused by –

OE1.1– inefficient energy performance of buildings or building components

OE2 Greenhouse Gases

An objective of this Code is to limit the probability that, as a result of design and construction of the building, including the building’s systems, and the energy consumed in the operation of those systems, the production of greenhouse gases will be excessive.  The risks of excessive greenhouse gas emissions addressed in this Code are those caused by-

OE2.1 – excessive emissions as a result of the design and construction of the building, including the building’s systems, and the energy consumed in the operation of those systems

Notes to Part 2

Objectives

A-2.1.1.2.(6)   Application of Environment Objective. Objective OE, Environment (including its sub-objectives), is attributed to the requirements in Section 9.36. of Division B, which address energy efficiency for small residential buildings and certain small non-residential and mixed-use buildings (see Article 9.36.1.3. of Division B). The objectives, functional statements and energy efficiency requirements for larger Part 9 residential buildings as well as for non-residential buildings whose combined total floor area exceeds 300 m2 and some mixed-use buildings are addressed in the National Energy Code for Buildings.

A-2.2.1.1.(1)   Objectives.

Listing of objectives

Any gaps in the numbering sequence of the objectives are due to the fact that there is a master list of objectives covering the principal Code Documents—the British Columbia Building Code Book I: General, British Columbia Building Code Book II: Plumbing Systems, and the British Columbia Fire Code—but not all objectives are pertinent to all Codes.

The building

Where the term “the building” is used in the wording of the objectives, it refers to the building for which compliance with the British Columbia Building Code is being assessed.

Emergency

The term “emergency”—in the context of safety in buildings—is often equated to the term “fire emergency;” however, the wording of objectives OS3.7 and OS5.9 makes it clear that the Code addresses any type of emergency that would require the rapid evacuation of the building, such as a bomb threat or the presence of intruders.

Fire Safety

In the definition of Objective OS1, Fire Safety, the term “person” refers to any individual in or adjacent to the building, including the occupants, the public, and emergency responders including firefighters when performing their duties.

Certain technical requirements in the BC Codes are intended to address the safety of emergency responders, including firefighters, when performing their duties.

Part 3

Functional Statements

Section  3.1.   Application

3.1.1. Application

3.1.1.1. Application

1)   This Part applies to all buildings covered in this Code. (See Article 1.1.1.1.)

3.1.1.2. Application of Functional Statements

1)   Except as provided in Sentences (2) to (4), the functional statements described in this Part apply

a)   to all buildings covered in this Code (see Article 1.1.1.1.), and

b)   only to the extent that they relate to compliance with this Code as required in Article 1.2.1.1.

2)   Functional Statement F56 applies only to dwelling units.

3)   Functional Statements F73 and F74 do not apply to

a)   detached houses, semi-detached houses, houses with a secondary suite, duplexes, triplexes, townhouses, row houses and boarding houses (see Note A-1.4.1.2.(1), Secondary Suite),

b)   buildings of Group F, Division 1 major occupancy, and

c)   buildings that are not intended to be occupied on a daily or full-time basis, including automatic telephone exchanges, pumphouses and substations.

4)   Functional Statement F75 applies only to adaptable dwelling units in multiple unit residential occupancy buildings that contain interior corridors and exterior passageways for access to the adaptable dwelling units.

Section  3.2.   Functional Statements

3.2.1. Functional Statements

3.2.1.1. Functional Statements

1)   The objectives of this Code are achieved by measures, such as those described in the acceptable solutions in Division B, that are intended to allow the building or its elements to perform the following functions (see Note A-3.2.1.1.(1)):

F01 To minimize the risk of accidental ignition.

F02 To limit the severity and effects of fire or explosions.

F03 To retard the effects of fire on areas beyond its point of origin.

F04 To retard failure or collapse due to the effects of fire.

F05 To retard the effects of fire on emergency egress facilities.

F06 To retard the effects of fire on facilities for notification, suppression and emergency response.

F10 To facilitate the timely movement of persons to a safe place in an emergency.

F11 To notify persons, in a timely manner, of the need to take action in an emergency.

F12 To facilitate emergency response.

F13 To notify emergency responders, in a timely manner, of the need to take action in an emergency.

F20 To support and withstand expected loads and forces.

F21 To limit or accommodate dimensional change.

F22 To limit movement under expected loads and forces.

F23 To maintain equipment in place during structural movement.

F30 To minimize the risk of injury to persons as a result of tripping, slipping, falling, contact, drowning or collision.

F31 To minimize the risk of injury to persons as a result of contact with hot surfaces or substances.

F32 To minimize the risk of injury to persons as a result of contact with energized equipment.

F33 To limit the level of sound of a fire alarm system.

F34 To resist or discourage unwanted access or entry.

F35 To facilitate the identification of potential intruders.

F36 To minimize the risk that persons will be trapped in confined spaces.

F40 To limit the level of contaminants.

F41 To minimize the risk of generation of contaminants.

F42 To resist the entry of vermin and insects.

F43 To minimize the risk of release of hazardous substances.

F44 To limit the spread of hazardous substances beyond their point of release.

F46 To minimize the risk of contamination of potable water.

F50 To provide air suitable for breathing.

F51 To maintain appropriate air and surface temperatures.

F52 To maintain appropriate relative humidity.

F53 To maintain appropriate indoor/outdoor air pressure differences.

F54 To limit drafts.

F55 To resist the transfer of air through environmental separators.

F56 To limit the transmission of airborne sound into a dwelling unit from spaces elsewhere in the building (see Sentence 3.1.1.2.(2) for application limitation).

F60 To control the accumulation and pressure of water on and in the ground.

F61 To resist the ingress of precipitation, water or moisture from the exterior or from the ground.

F62 To facilitate the dissipation of water and moisture from the building.

F63 To limit moisture condensation.

F70 To provide potable water.

F71 To provide facilities for personal hygiene.

F72 To provide facilities for the sanitary disposal of human and domestic wastes.

F73 To facilitate access to and circulation in the building and its facilities by persons with disabilities (see Sentence 3.1.1.2.(3) for application limitation).

F74 To facilitate the use of the building's facilities by persons with disabilities (see Sentence 3.1.1.2.(3) for application limitation).

F75 To minimize obstacles for future modification to provide access (see Sentence 3.1.1.2.(4) for application limitation).

F80 To resist deterioration resulting from expected service conditions.

F81 To minimize the risk of malfunction, interference, damage, tampering, lack of use or misuse.

F82 To minimize the risk of inadequate performance due to improper maintenance or lack of maintenance.

F90 To limit the amount of uncontrolled air leakage through the building envelope.

F91 To limit the amount of uncontrolled air leakage through system components.

F92 To limit the amount of uncontrolled thermal transfer through the building envelope.

F93 To limit the amount of uncontrolled thermal transfer through system components.

F95 To limit the unnecessary demand and/or consumption of energy for heating and cooling.

F96 To limit the unnecessary demand and/or consumption of energy for service water heating.

F98 To limit the inefficiency of equipment.

F99 To limit the inefficiency of systems.

F100 To limit the unnecessary rejection of reusable waste energy.

F101 To limit excessive emission of greenhouse gases into the environment.

Notes to Part 3

Functional Statements

A-3.2.1.1.(1)   Listing of Functional Statements. The numbered functional statements are grouped according to functions that deal with closely related subjects. For example, the first group deals with fire risks, the second group deals with emergency egress and response, etc. There may be gaps in the numbering sequence for the following reasons:

•   Each group has unused numbers which allows for the possible future creation of additional functional statements within any one group.

•   There is a master list of functional statements covering the principal Code Documents—the British Columbia Building Code Book I: General, British Columbia Building Code Book II: Plumbing Systems, and the British Columbia Fire Code—but not all functional statements are pertinent to all Codes.