Appendix C

Climatic and Seismic Information for Building Design in Canada

Introduction

The great diversity of climate in British Columbia has a considerable effect on the performance of buildings; consequently, building design must reflect this diversity. This Appendix briefly describes how climatic design values are computed and provides recommended design data for a number of cities, towns, and lesser populated locations. Through the use of such data, appropriate allowances can be made for climate variations in different localities of British Columbia Building Code can be applied regionally

The climatic design data presented in Table C-2 are based on weather observations collected by the Meteorological Service of Canada, Environment and Climate Change Canada. The data were researched and analyzed for the Canadian Commission on Building and Fire Codes by Environment and Climate Change Canada.

As it is not practical to list values for all municipalities in British Columbia, recommended climatic design values for locations not listed can be obtained by e-mail from the Engineering Climate Services Unit of Environment and Climate Change Canada at scg-ecs@ec.gc.ca. It should be noted, however, that these recommended values may differ from the legal requirements set by local government building authorities.

The information on seismic hazard given in this Appendix has been provided by Natural Resources Canada.

General

The choice of climatic elements tabulated in this Appendix and the form in which they are expressed have been dictated largely by the requirements for specific values in several sections of this Code. These elements include ground snow loads, wind pressures, design temperatures, heating degree-days, one-day and 15-minute rainfalls, and annual total precipitation values. The following notes briefly explain the significance of these particular elements in building design, and indicate which weather observations were used and how they were analyzed to yield the required design values.

Table C-2 lists design weather recommendations and elevations for over 100 locations, which have been chosen based on a variety of reasons. Many incorporated cities and towns with significant populations are included unless located close to larger cities. For sparsely populated areas, many smaller towns and villages are listed. Other locations have been added to the list when the demand for climatic design recommendations at these sites has been significant. The named locations refer to the specific latitude and longitude defined by the Gazetteer of Canada (Natural Resources Canada), available from Publishing and Depository Services Canada, Public Works and Government Services Canada, Ottawa, Ontario K1A 0S5. The elevations are given in metres and refer to heights above sea level.

Almost all of the weather observations used in preparing Table C-2 were, of necessity, observed at inhabited locations. To estimate design values for arbitrary locations, the observed or computed values for the weather stations were mapped and interpolated appropriately. Where possible, adjustments have been applied for the influence of elevation and known topographical effects. Such influences include the tendency of cold air to collect in depressions, for precipitation to increase with elevation, and for generally stronger winds near large bodies of water. Elevations have been added to Table C-2 because of their potential to significantly influence climatic design values.

Since interpolation from the values in Table C-2 to other locations may not be valid due to local and other effects, Environment and Climate Change Canada will provide climatic design element recommendations for locations not listed in Table C-2. Local effects are particularly significant in mountainous areas, where the values apply only to populated valleys and not to the mountain slopes and high passes, where very different conditions are known to exist.

Changing and Variable Climates

Climate is not static. At any location, weather and climatic conditions vary from season to season, year to year, and over longer time periods (climate cycles). This has always been the case. In fact, evidence is mounting that the climates of Canada are changing and will continue to change significantly into future. When estimating climatic design loads, this variability can be considered using appropriate statistical analysis, data records spanning sufficient periods, and meteorological judgement. The analysis generally assumes that the past climate will be representative of the future climate.

Past and ongoing modifications to atmospheric chemistry (from greenhouse gas emissions and land use changes) are expected to alter most climatic regimes in the future despite the success of the most ambitious greenhouse gas mitigation plans.(1) Some regions could see an increase in the frequency and intensity of many weather extremes, which will accelerate weathering processes. Consequently, many buildings will need to be designed, maintained and operated to adequately withstand ever changing climatic loads.

Similar to global trends, the last decade in Canada was noted as the warmest in instrumented record. Canada has warmed, on average, at almost twice the rate of the global average increase, while the western Arctic is warming at a rate that is unprecedented over the past 400 years.(1) Mounting evidence from Arctic communities indicates that rapid changes to climate in the North have resulted in melting permafrost and impacts from other climate changes have affected nearly every type of built structure. Furthermore, analyses of Canadian precipitation data shows that many regions of the country have, on average, also been tending towards wetter conditions.(1) In the United States, where the density of climate monitoring stations is greater, a number of studies have found an unambiguous upward trend in the frequency of heavy to extreme precipitation events, with these increases coincident with a general upward trend in the total amount of precipitation. Climate change model results, based on an ensemble of global climate models worldwide, project that future climate warming rates will be greatest in higher latitude countries such as Canada.(2)

January Design Temperatures

A building and its heating system should be designed to maintain the inside temperature at some pre-determined level. To achieve this, it is necessary to know the most severe weather conditions under which the system will be expected to function satisfactorily. Failure to maintain the inside temperature at the pre-determined level will not usually be serious if the temperature drop is not great and if the duration is not long. The outside conditions used for design should, therefore, not be the most severe in many years, but should be the somewhat less severe conditions that are occasionally but not greatly exceeded.

The January design temperatures are based on an analysis of January air temperatures only. Wind and solar radiation also affect the inside temperature of most buildings and may need to be considered for energy-efficient design.

The January design temperature is defined as the lowest temperature at or below which only a certain small percentage of the hourly outside air temperatures in January occur. In the past, a total of 158 stations with records from all or part of the period 1951-66 formed the basis for calculation of the 2.5 and 1% January temperatures. Where necessary, the data were adjusted for consistency. Since most of the temperatures were observed at airports, design values for the core areas of large cities could be 1 or 2°C milder, although the values for the outlying areas are probably about the same as for the airports. No adjustments were made for this urban island heat effect. The design values for the next 20 to 30 years will probably differ from these tabulated values due to year-to-year climate variability and global climate change resulting from the impact of human activities on atmospheric chemistry.

The design temperatures were reviewed and updated using hourly temperature observations from 480 stations for a 25-year period up to 2006 with at least 8 years of complete data. These data are consistent with data shown for Canadian locations in the 2009 Handbook of Fundamentals(3) published by the American Society of Heating, Refrigerating, and Air-Conditioning Engineers (ASHRAE). The most recent 25 years of record were used to provide a balance between accounting for trends in the climate and the sampling variation owing to year-to-year variation. The 1% and 2.5% values used for the design conditions represent percentiles of the cumulative frequency distribution of hourly temperatures and correspond to January temperatures that are colder for 8 and 19 hours, respectively, on average over the long term.

The 2.5% January design temperature is the value ordinarily used in the design of heating systems. In special cases, when the control of inside temperature is more critical, the 1% value may be used. Other temperature-dependent climatic design parameters may be considered for future issues of this document.

July Design Temperatures

A building and its cooling and dehumidifying system should be designed to maintain the inside temperature and humidity at certain pre-determined levels. To achieve this, it is necessary to know the most severe weather conditions under which the system is expected to function satisfactorily. Failure to maintain the inside temperature and humidity at the pre-determined levels will usually not be serious if the increases in temperature and humidity are not great and the duration is not long. The outside conditions used for design should, therefore, not be the most severe in many years, but should be the somewhat less severe conditions that are occasionally but not greatly exceeded.

The summer design temperatures in this Appendix are based on an analysis of July air temperatures and humidities. Wind and solar radiation also affect the inside temperature of most buildings and may, in some cases, be more important than the outside air temperature. More complete summer and winter design information can be obtained from Environment and Climate Change Canada.

The July design dry-bulb and wet-bulb temperatures were reviewed and updated using hourly temperature observations from 480 stations for a 25-year period up to 2006. These data are consistent with data shown for Canadian locations in the 2009 Handbook of Fundamentals(3) published by ASHRAE. As with January design temperatures, data from the most recent 25-year period were analyzed to reflect any recent climatic changes or variations. The 2.5% values used for the dry- and wet-bulb design conditions represent percentiles of the cumulative frequency distribution of hourly dry- and wet-bulb temperatures and correspond to July temperatures that are higher for 19 hours on average over the long term.

Heating Degree-Days

The rate of consumption of fuel or energy required to keep the interior of a small building at 21°C when the outside air temperature is below 18°C is roughly proportional to the difference between 18°C and the outside temperature. Wind speed, solar radiation, the extent to which the building is exposed to these elements and the internal heat sources also affect the heat required and may have to be considered for energy-efficient design. For average conditions of wind, radiation, exposure, and internal sources, however, the proportionality with the temperature difference generally still holds.

Since the fuel required is also proportional to the duration of the cold weather, a convenient method of combining these elements of temperature and time is to add the differences between 18°C and the mean temperature for every day in the year when the mean temperature is below 18°C. It is assumed that no heat is required when the mean outside air temperature for the day is 18°C or higher.

Although more sophisticated computer simulations using other forms of weather data have now almost completely replaced degree-day-based calculation methods for estimating annual heating energy consumption, degree-days remain a useful indicator of relative severity of climate and can form the basis for certain climate-related Code requirements.

The degree-days below 18°C were compiled for 1300 stations for the 25-year period ending in 2006. This analysis period is consistent with the one used to derive the design temperatures described above and with the approach used by ASHRAE.(3)

A difference of only one Celsius degree in the mean annual temperature will cause a difference of 250 to 350 in the Celsius degree-days. Since differences of 0.5 of a Celsius degree in the mean annual temperature are quite likely to occur between two stations in the same town, heating degree-days cannot be relied on to an accuracy of less than about 100 degree-days.

Heating degree-day values for the core areas of larger cities can be 200 to 400 degree-days less (warmer) than for the surrounding fringe areas. The observed degree-days, which are based on daily temperature observations, are often most representative of rural settings or the fringe areas of cities.

Climatic Data for Energy Consumption Calculations

The climatic elements tabulated in this Appendix represent commonly used design values but do not include detailed climatic profiles, such as hourly weather data. Where hourly values of weather data are needed for the purpose of simulating the annual energy consumption of a building, they can be obtained from multiple sources, such as Environment and Climate Change Canada, Natural Resources Canada, the Regional Conservation Authority and other such public agencies that record this information. Hourly weather data are also available from public and private agencies that format this information for use with annual energy consumption simulation software; in some cases, these data have been incorporated into the software.

Snow Loads

The roof of a building should be able to support the greatest weight of snow that is likely to accumulate on it in many years. Some observations of snow on roofs have been made in Canada, but not enough to form the basis for estimating roof snow loads throughout the country. Similarly, observations of the weight, or water equivalent, of the snow on the ground have not been available in digital form in the past. The observations of roof loads and water equivalents are very useful, as noted below, but the measured depth of snow on the ground is used to provide the basic information for a consistent set of snow loads.

The estimation of the design snow load on a roof from snow depth observations involves the following steps:

1.   The depth of snow on the ground, which has an annual probability of exceedance of 1-in-50, is computed.

2.   The appropriate specific weight is selected and used to convert snow depth to loads, Ss.

3.   The load, Sr, which is due to rain falling on the snow, is computed.

4.   Because the accumulation of snow on roofs is often different from that on the ground, adjustments are applied to the ground snow load to provide a design snow load on a roof.

The annual maximum depth of snow on the ground has been assembled for 1618 stations for which data has been recorded by the Meteorological Service of Canada (MSC). The period of record used varied from station to station, ranging from 7 to 38 years. These data were analyzed using a Gumbel extreme value distribution fitted using the method of moments(4) as reported by Newark et al.(5) The resulting values are the snow depths, which have a probability of 1-in-50 of being exceeded in any one year.

The specific weight of old snow generally ranges from 2 to 5 kN/m3, and it is usually assumed in Canada that 1 kN/m3 is the average for new snow. Average specific weights of the seasonal snow pack have been derived for different regions across the country(6) and an appropriate value has been assigned to each weather station. Typically, the values average 2.01 kN/m3 east of the continental divide (except for 2.94 kN/m3 north of the treeline), and range from 2.55 to 4.21 kN/m3 west of the divide. The product of the 1-in-50 snow depth and the average specific weight of the seasonal snow pack at a station is converted to the snow load (SL) in units of kilopascals (kPa).

Except for the mountainous areas of western Canada, the values of the ground snow load at MSC stations were normalized assuming a linear variation of the load above sea level in order to account for the effects of topography. They were then smoothed using an uncertainty-weighted moving-area average in order to minimize the uncertainty due to snow depth sampling errors and site-specific variations. Interpolation from analyzed maps of the smooth normalized values yielded a value for each location in Table C-2, which could then be converted to the listed code values (Ss) by means of an equation in the form:

Ss = smooth normalized SL + bZ

where b is the assumed rate of change of SL with elevation at the location and Z is the location's elevation above mean sea level (MSL). Although they are listed in Table C-2 to the nearest tenth of a kilopascal, values of Ss typically have an uncertainty of about 20%. Areas of sparse data in northern Canada were an exception to this procedure. In these regions, an analysis was made of the basic SL values. The effects of topography, variations due to local climates, and smoothing were all subjectively assessed. The values derived in this fashion were used to modify those derived objectively.

For the mountainous areas of British Columbia, Yukon, and the foothills area of Alberta, a more complex procedure was required to account for the variation of loads with terrain and elevation. Since the MSC observational network often does not have sufficient coverage to detail this variability in mountainous areas, additional snow course observations were obtained from the provincial and territorial governments of British Columbia, Yukon, and Alberta. The additional data allowed detailed local analysis of ground snow loads on a valley-by-valley basis. Similar to other studies, the data indicated that snow loads above a critical or reference level increased according to either a linear or quadratic relation with elevation. The determination of whether the increase with elevation was linear or quadratic, the rate of the increase and the critical or reference elevation were found to be specific to the valley and mountain ranges considered. At valley levels below the critical elevation, the loads generally varied less significantly with elevation. Calculated valley- and range-specific regression relations were then used to describe the increase of load with elevation and to normalize the MSC snow observations to a critical or reference level. These normalized values were smoothed using a weighted moving-average.

Tabulated values cannot be expected to indicate all the local differences in Ss. For this reason, especially in complex terrain areas, values should not be interpolated from Table C-2 for unlisted locations. The values of Ss in the Table apply for the elevation and the latitude and longitude of the location, as defined by the Gazetteer of Canada. Values at other locations can be obtained from Environment and Climate Change Canada.

The heaviest loads frequently occur when the snow is wetted by rain, thus the rain load, Sr, was estimated to the nearest 0.1 kPa and is provided in Table C-2. When values of Sr are added to Ss, this provides a 1-in-50-year estimate of the combined ground snow and rain load. The values of Sr are based on an analysis of about 2100 weather station values of the 1-in-50-year one-day maximum rain amount. This return period is appropriate because the rain amounts correspond approximately to the joint frequency of occurrence of the one-day rain on maximum snow packs. For the purpose of estimating rain on snow, the individual observed one-day rain amounts were constrained to be less than or equal to the snow pack water equivalent, which was estimated by a snow pack accumulation model reported by Bruce and Clark.(7)

The results from surveys of snow loads on roofs indicate that average roof loads are generally less than loads on the ground. The conditions under which the design snow load on the roof may be taken as a percentage of the ground snow load are given in Subsection 4.1.6. The Code also permits further decreases in design snow loads for steeply sloping roofs, but requires substantial increases for roofs where snow accumulation may be more rapid due to such factors as drifting. Recommended adjustments are given in the “Structural Commentaries (User's Guide – NBC 2020: Part 4 of Division B).”

The ground snow load values, Ss, were updated for the 2015 edition of the Code using a similar approach to the one used for the ground snow load update in the 1990 edition, which was the basis for the 1992 British Columbia Building Code. The Gumbel extreme value distribution was fitted to the annual maxima of daily snow depth observations made at over 1400 weather stations, which were compiled from 1990 onward—to as recently as 2012 for some stations—to calculate the 50-year return period snow depth. The 50-year ground snow load was then calculated for each weather station by combining the 50-year snow pack depth with the assigned snow pack density. The Ss values for each location in Table C-2 were compared with the updated weather station values and revised accordingly.

Annual Total Precipitation

Total precipitation is the sum in millimetres of the measured depth of rainwater and the estimated or measured water equivalent of the snow (typically estimated as 0.1 of the measured depth of snow, since the average density of fresh snow is about 0.1 that of water).

The average annual total precipitation amounts in Table C-2 have been interpolated from an analysis of precipitation observations from 1379 stations for the 30-year period from 1961 to 1990.

Annual Rainfall

The total amount of rain that normally falls in one year is frequently used as a general indication of the wetness of a climate, and is therefore included in this Appendix. See also Moisture Index below.

Rainfall Intensity

Roof drainage systems are designed to carry off rainwater from the most intense rainfall that is likely to occur. A certain amount of time is required for the rainwater to flow across and down the roof before it enters the gutter or drainage system. This results in the smoothing out of the most rapid changes in rainfall intensity. The drainage system, therefore, need only cope with the flow of rainwater produced by the average rainfall intensity over a period of a few minutes, which can be called the concentration time.

In Canada, it has been customary to use the 15-minute rainfall that will probably be exceeded on an average of once in 10 years. The concentration time for small roofs is much less than 15 minutes and hence the design intensity will be exceeded more frequently than once in 10 years. The safety factors in Book II (Plumbing Systems) of this Code will probably reduce the frequency to a reasonable value and, in addition, the occasional failure of a roof drainage system will not be particularly serious in most cases.

The rainfall intensity values were updated for the 2012 edition of the Code using observations of annual maximum 15-minute rainfall amounts from 485 stations with 10 or more years of record, including data up to 2007 for some stations. Ten-year return period values—the 15-minute rainfall having a probability of 1-in-10 of being exceeded in any year—were calculated by fitting the annual maximum values to the Gumbel extreme value distribution(4) using the method of moments. The updated values are compiled from the most recent short-duration rainfall intensity-duration-frequency (IDF) graphs and tables available from Environment and Climate Change Canada.

It is very difficult to estimate the pattern of rainfall intensity in mountainous areas, where precipitation is extremely variable and rainfall intensity can be much greater than in other types of areas. Many of the observations for these areas were taken at locations in valley bottoms or in extensive, fairly level areas.

One-Day Rainfall

If for any reason a roof drainage system becomes ineffective, the accumulation of rainwater may be great enough in some cases to cause a significant increase in the load on the roof. In previous editions of this information, it had been common practice to use the maximum one-day rainfall ever observed for estimating the additional load. Since the length of record for weather stations in Canada is quite variable, the maximum one-day rainfall amounts in previous editions often reflected the variable length of record at nearby stations as much as the climatology. As a result, the maximum values often differed greatly within relatively small areas where little difference should be expected. The current values have been standardized to represent the one-day rainfall amounts that have 1 chance in 50 of being exceeded in any one year or the 1-in-50-year return value one-day rainfalls.

The one-day rainfall values were updated using daily rainfall observations from more than 3500 stations with 10 years or more of record, including data up to 2008 for some stations. The 50-year return period values were calculated by fitting the annual maximum one-day rainfall observations to the Gumbel extreme value distribution using the method of moments.(4)

Rainfall frequency observations can vary considerably over time and space. This is especially true for mountainous areas, where elevation effects can be significant. In other areas, small-scale intense storms or local influences can produce significant spatial variability in the data. As a result, the analysis incorporates some spatial smoothing.

Moisture Index (MI)

Moisture index (MI) values were developed through the work of a consortium that included representatives from industry and researchers from NRC.(1) The MI is an indicator of the moisture load imposed on a building by the climate and is used in Part 9 to define the minimum levels of protection from precipitation to be provided by cladding assemblies on exterior walls.

It must be noted, in using MI values to determine the appropriate levels of protection from precipitation, that weather conditions can vary markedly within a relatively small geographical area. Although the values provided in the Table give a good indication of the average conditions within a particular region, some caution must be exercised when applying them to a locality that is outside the region where the weather station is located.

MI is calculated from a wetting index (WI) and a drying index (DI).

Wetting Index (WI)

To define, quantitatively, the rainwater load on a wall, wind speed and wind direction have to be taken into consideration in addition to rainfall, along with factors that can affect exposure, such as nearby buildings, vegetation and topography. Quantitative determination of load, including wind speed and wind direction, can be done. However, due to limited weather data, it is not currently possible to provide this information for most of the locations identified in the Table.

This lack of information, however, has been shown to be non-critical for the purpose of classifying locations in terms of severity of rain load. The results of the research indicated that simple annual rainfall is as good an indicator as any for describing rainwater load. That is to say, for Canadian locations, and especially once drying is accounted for, the additional sensitivity provided by hourly directional rainfall values does not have a significant effect on the order in which locations appear when listed from wet to dry.

Consequently, the wetting index (WI) is based on annual rainfall and is normalized based on 1000 mm.

Drying Index (DI)

Temperature and relative humidity together define the drying capacity of ambient air. Based on simple psychrometrics, values were derived for the locations listed in the Table using annual average drying capacity normalized based on the drying capacity at Lytton, B.C. The resultant values are referred to as drying indices (DI).

Determination of Moisture Index (MI)

The relationship between WI and DI to correctly define moisture loading on a wall is not known. The MI values provided in the Table are based on the root mean square values of WI and 1-DI, with those values equally weighted. This is illustrated in Figure C-1. The resultant MI values are sufficiently consistent with industry's understanding of climate severity with respect to moisture loading as to allow limits to be identified for the purpose of specifying where additional protection from precipitation is required.

Figure C-1

Derivation of moisture index (MI) based on normalized values for wetting index (WI) and drying index (DI)

Note to Figure C-1:

(1) MI equals the hypotenuse of the triangle defined by WIN and 1-DIN

Driving Rain Wind Pressure (DRWP)

The presence of rainwater on the face of a building, with or without wind, must be addressed in the design and construction of the building envelope so as to minimize the entry of water into the assembly. Wind pressure on the windward faces of a building will promote the flow of water through any open joints or cracks in the facade.

Driving rain wind pressure (DRWP) is the wind load that is coincident with rain, measured or calculated at a height of 10 m. The values provided in the Table represent the loads for which there is 1 chance in 5 of being reached or exceeded in any one year, or a probability of 20% within any one year. Approximate adjustments for height can be made using the values for Ce given in Sentence 4.1.7.3.(5) as a multiplier.

Because of inaccuracies in developing the DRWP values related to the averaging of extreme wind pressures, the actual heights of recording anemometers, and the use of estimated rather than measured rainfall values, the values are considered to be higher than actual loads.(8)(9) Thus the actual probability of reaching or exceeding the DRWP in a particular location is less than 20% per year and these values can be considered to be conservative.

DRWP can be used to determine the height to which wind will drive rainwater up enclosed vertical conduits. This provides a conservative estimate of the height needed for fins in window extrusions and end dams on flashings to control water ingress. This height can be calculated as:

height of water, mm = DRWP/10, Pa

Note that the pressure difference across the building envelope may be augmented by internal pressures induced in the building interior by the wind. These additional pressures can be estimated using the information provided in the Commentary entitled Wind Load and Effects of the “Structural Commentaries (User's Guide – NBC 2020: Part 4 of Division B).”

Wind Effects

All structures need to be designed to ensure that the main structural system and all secondary components, such as cladding and appurtenances, will withstand the pressures and suctions caused by the strongest wind likely to blow at that location in many years. Some flexible structures, such as tall buildings, slender towers and bridges, also need to be designed to minimize excessive wind-induced oscillations or vibrations.

At any time, the wind acting upon a structure can be treated as a mean or time-averaged component and as a gust or unsteady component. For a small structure, which is completely enveloped by wind gusts, it is only the peak gust velocity that needs to be considered. For a large structure, the wind gusts are not well correlated over its different parts and the effects of individual gusts become less significant. The “Structural Commentaries (User's Guide – NBC 2020: Part 4 of Division B)” evaluates the mean pressure acting on a structure, provides appropriate adjustments for building height and exposure and for the influence of the surrounding terrain and topography (including wind speed-up for hills), and then incorporates the effects of wind gusts by means of the gust factor, which varies according to the type of structure and the size of the area over which the pressure acts.

The wind speeds and corresponding velocity pressures used in the Code are regionally representative or reference values. The reference wind speeds are nominal one-hour averages of wind speeds representative of the 10 m height in flat open terrain corresponding to Exposure A or open terrain in the terminology of the “Structural Commentaries (User's Guide – NBC 2020: Part 4 of Division B).” The reference wind speeds and wind velocity pressures are based on long-term wind records observed at a large number of weather stations across Canada.

Reference wind velocity pressures in the 1961 to 2005 editions of the Code since 1961 were based mostly on records of hourly averaged wind speeds (i.e. the number of miles of wind passing an anemometer in an hour) from over 100 stations with 10 to 22 years of observations ending in the 1950s. The wind pressure values derived from these measurements represented true hourly wind pressures.

The reference wind velocity pressures were reviewed and updated for the 20102 edition of the Code. The primary data set used for the analysis comprised wind records compiled from about 135 stations with hourly averaged wind speeds and from 465 stations with aviation (one- or two-minute average) speeds or surface weather (ten-minute average) speeds observed once per hour at the top of the hour; the periods of record used ranged from 10 to 54 years. In addition, peak wind gust records from 400 stations with periods of record ranging from 10 to 43 years were used. Peak wind gusts (gust durations of approximately 3 to 7 seconds) were used to supplement the primary once-per-hour observations in the analysis.

Several steps were involved in updating the reference wind values. Where needed, speeds were adjusted to represent the standard anemometer height above ground of 10 m. The data from years when the anemometer at a station was installed on the top of a lighthouse or building were eliminated from the analysis since it is impractical to adjust for the effects of wind flow over the structure. (Most anemometers were moved to 10 m towers by the 1960s.) Wind speeds of the various observation types—hourly averaged, aviation, surface weather and peak wind gust—were adjusted to account for different measure durations to represent a one-hour averaging period and to account for differences in the surface roughness of flat open terrain at observing stations.

The annual maximum wind speed data was fitted to the Gumbel distribution using the method of moments(4) to calculate hourly wind speeds having the annual probability of occurrence of 1-in-10 and 1-in-50 (10-year and 50-year return periods). The values were plotted on maps, then analyzed and abstracted for the locations in Table C-2.

The wind velocity pressures, q, were calculated in Pascals using the following equation:

where ρ is an average air density for the windy months of the year and V is wind speed in metres per second. While air density depends on both air temperature and atmospheric pressure, the density of dry air at 0°C and standard atmospheric pressure of 1.2929 kg/m3 was used as an average value for the wind pressure calculations. As explained by Boyd(10), this value is within 10% of the monthly average air densities for most of Canada in the windy part of the year.

As a result of the updating procedure for the 2010 edition of the Code, the 1-in-50 reference wind velocity pressures remained unchanged for most of the locations listed in Table C-2; both increases and decreases were noted for the remaining locations. Many of the decreases resulted from the fact that anemometers at most of the stations used in the previous analysis were installed on lighthouses, airport hangers and other structures. Wind speeds on the tops of buildings are often much higher compared to those registered by a standard 10 m tower. Eliminating anemometer data recorded on the tops of buildings from the analysis resulted in lower values at several locations.

For the 2023 edition of the Code, the reference wind velocity pressures were updated to reflect the new data collected in the approximately 10 years since the previous update for the 20102 edition. Only data collected at stations with a period of record of at least 20 years were used in the analysis. As a result, the data set comprised wind records from 368 hourly and 222 daily peak wind gust stations with periods of record ranging from 20 to 65 years. The annual maximum wind speed data were fitted to the Gumbel distribution.

The 1-in-50 hourly wind speeds, after adjusting for roughness to represent open exposure, were mapped and compared to the BCBC 2018 values for the locations in Table C-2. This updating procedure resulted in small changes to the 1-in-50 reference wind velocity pressures for some locations.

The 1-in-10 reference wind velocity pressures were updated using the same procedure, except that regional values of the coefficient of variation were used in the calculations instead of the national value used previously. This procedure resulted in small changes to the 1-in-10 reference wind velocity pressures for some locations, including many for which there was no change to the 1-in-50 reference wind velocity pressure.

Wind speeds that have a 1-in-”n” chance of being exceeded in any year can be calculated from the wind speeds corresponding to the 1-in-10 and 1-in-50 return period values in Table C-2 using the following equation:

Table C-1 has been arranged to give pressures to the nearest one-hundredth of a kPa and their corresponding wind speeds. The value of “q” in kPa is assumed to be equal to 0.00064645 V2, where V is given in m/s.

Table C-1

Wind Speeds

| q kPa | V m/s | q kPa | V m/s | q kPa | V m/s | q kPa | V m/s |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 0.15 | 15.2 | 0.53 | 28.6 | 0.91 | 37.5 | 1.29 | 44.7 |
| 0.16 | 15.7 | 0.54 | 28.9 | 0.92 | 37.7 | 1.30 | 44.8 |
| 0.17 | 16.2 | 0.55 | 29.2 | 0.93 | 37.9 | 1.31 | 45.0 |
| 0.18 | 16.7 | 0.56 | 29.4 | 0.94 | 38.1 | 1.32 | 45.2 |
| 0.19 | 17.1 | 0.57 | 29.7 | 0.95 | 38.3 | 1.33 | 45.4 |
| 0.20 | 17.6 | 0.58 | 30.0 | 0.96 | 38.5 | 1.34 | 45.5 |
| 0.21 | 18.0 | 0.59 | 30.2 | 0.97 | 38.7 | 1.35 | 45.7 |
| 0.22 | 18.4 | 0.60 | 30.5 | 0.98 | 38.9 | 1.36 | 45.9 |
| 0.23 | 18.9 | 0.61 | 30.7 | 0.99 | 39.1 | 1.37 | 46.0 |
| 0.24 | 19.3 | 0.62 | 31.0 | 1.00 | 39.3 | 1.38 | 46.2 |
| 0.25 | 19.7 | 0.63 | 31.2 | 1.01 | 39.5 | 1.39 | 46.4 |
| 0.26 | 20.1 | 0.64 | 31.5 | 1.02 | 39.7 | 1.40 | 46.5 |
| 0.27 | 20.4 | 0.65 | 31.7 | 1.03 | 39.9 | 1.41 | 46.7 |
| 0.28 | 20.8 | 0.66 | 32.0 | 1.04 | 40.1 | 1.42 | 46.9 |
| 0.29 | 21.2 | 0.67 | 32.2 | 1.05 | 40.3 | 1.43 | 47.0 |
| 0.30 | 21.5 | 0.68 | 32.4 | 1.06 | 40.5 | 1.44 | 47.2 |
| 0.31 | 21.9 | 0.69 | 32.7 | 1.07 | 40.7 | 1.45 | 47.4 |
| 0.32 | 22.2 | 0.70 | 32.9 | 1.08 | 40.9 | 1.46 | 47.5 |
| 0.33 | 22.6 | 0.71 | 33.1 | 1.09 | 41.1 | 1.47 | 47.7 |
| 0.34 | 22.9 | 0.72 | 33.4 | 1.10 | 41.3 | 1.48 | 47.8 |
| 0.35 | 23.3 | 0.73 | 33.6 | 1.11 | 41.4 | 1.49 | 48.0 |
| 0.36 | 23.6 | 0.74 | 33.8 | 1.12 | 41.6 | 1.50 | 48.2 |
| 0.37 | 23.9 | 0.75 | 34.1 | 1.13 | 41.8 | 1.51 | 48.3 |
| 0.38 | 24.2 | 0.76 | 34.3 | 1.14 | 42.0 | 1.52 | 48.5 |
| 0.39 | 24.6 | 0.77 | 34.5 | 1.15 | 42.2 | 1.53 | 48.6 |
| 0.40 | 24.9 | 0.78 | 34.7 | 1.16 | 42.4 | 1.54 | 48.8 |
| 0.41 | 25.2 | 0.79 | 35.0 | 1.17 | 42.5 | 1.55 | 49.0 |
| 0.42 | 25.5 | 0.80 | 35.2 | 1.18 | 42.7 | 1.56 | 49.1 |
| 0.43 | 25.8 | 0.81 | 35.4 | 1.19 | 42.9 | 1.57 | 49.3 |
| 0.44 | 26.1 | 0.82 | 35.6 | 1.20 | 43.1 | 1.58 | 49.4 |
| 0.45 | 26.4 | 0.83 | 35.8 | 1.21 | 43.3 | 1.59 | 49.6 |
| 0.46 | 26.7 | 0.84 | 36.0 | 1.22 | 43.4 | 1.60 | 49.7 |
| 0.47 | 27.0 | 0.85 | 36.3 | 1.23 | 43.6 | 1.61 | 49.9 |
| 0.48 | 27.2 | 0.86 | 36.5 | 1.24 | 43.8 | 1.62 | 50.1 |
| 0.49 | 27.5 | 0.87 | 36.7 | 1.25 | 44.0 | 1.63 | 50.2 |
| 0.50 | 27.8 | 0.88 | 36.9 | 1.26 | 44.1 | 1.64 | 50.4 |
| 0.51 | 28.1 | 0.89 | 37.1 | 1.27 | 44.3 | 1.65 | 50.5 |
| 0.52 | 28.4 | 0.90 | 37.3 | 1.28 | 44.5 | 1.66 | 50.7 |

Table C-2

Climatic Design Data for Selected Locations in British Columbia

| Location | Elev., m | Design Temperature |  |  |  | Degree-Days Below 18°C | 15 Min. Rain, mm | One Day Rain, 1/50, mm | Ann. Rain, mm | Moist. Index | Ann. Tot. Ppn., mm | Driving Rain Wind Pressures, Pa, 1/5 | Snow Load, kPa, 1/50 |  | Hourly Wind Pressures, kPa |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | January |  | July 2.5% |  |  |  |  |  |  |  |  | Ss | Sr | 1/10 | 1/50 |
|  |  | 2.5% °C | 1% °C | Dry °C | Wet °C |  |  |  |  |  |  |  |  |  |  |  |
| British Columbia |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 100 Mile House | 1040 | -30 | -32 | 29 | 17 | 5030 | 10 | 48 | 300 | 0.4 | 425 | 60 | 2.6 | 0.3 | 0.27 | 0.35 |
| Abbotsford | 70 | -8 | -10 | 29 | 20 | 2860 | 12 | 112 | 1525 | 1.6 | 1600 | 160 | 2.0 | 0.3 | 0.33 | 0.44 |
| Agassiz | 15 | -9 | -11 | 31 | 21 | 2750 | 8 | 128 | 1650 | 1.7 | 1700 | 160 | 2.4 | 0.7 | 0.35 | 0.47 |
| Alberni | 12 | -5 | -8 | 31 | 19 | 3100 | 10 | 144 | 1900 | 2.0 | 2000 | 220 | 2.6 | 0.4 | 0.24 | 0.32 |
| Ashcroft | 305 | -24 | -27 | 34 | 20 | 3700 | 10 | 37 | 250 | 0.3 | 300 | 80 | 1.7 | 0.1 | 0.29 | 0.38 |
| Bamfield | 20 | -2 | -4 | 23 | 17 | 3080 | 13 | 170 | 2870 | 3.0 | 2890 | 280 | 1.0 | 0.4 | 0.38 | 0.50 |
| Beatton River | 840 | -37 | -39 | 26 | 18 | 6300 | 15 | 64 | 330 | 0.5 | 450 | 80 | 3.3 | 0.1 | 0.23 | 0.30 |
| Bella Bella | 25 | -5 | -7 | 23 | 18 | 3180 | 13 | 145 | 2715 | 2.8 | 2800 | 350 | 2.6 | 0.8 | 0.40 | 0.50 |
| Bella Coola | 40 | -14 | -18 | 27 | 19 | 3560 | 10 | 140 | 1500 | 1.9 | 1700 | 350 | 4.5 | 0.8 | 0.29 | 0.39 |
| Burns Lake | 755 | -31 | -34 | 26 | 17 | 5450 | 12 | 54 | 300 | 0.6 | 450 | 100 | 3.4 | 0.2 | 0.29 | 0.39 |
| Cache Creek | 455 | -24 | -27 | 34 | 20 | 3700 | 10 | 37 | 250 | 0.3 | 300 | 80 | 1.7 | 0.2 | 0.29 | 0.39 |
| Campbell River | 20 | -5 | -7 | 26 | 18 | 3000 | 10 | 116 | 1500 | 1.6 | 1600 | 260 | 2.8 | 0.4 | 0.41 | 0.48 |
| Carmi | 845 | -24 | -26 | 31 | 19 | 4750 | 10 | 64 | 325 | 0.4 | 550 | 60 | 3.6 | 0.2 | 0.29 | 0.38 |
| Castlegar | 430 | -18 | -20 | 32 | 20 | 3580 | 10 | 54 | 560 | 0.6 | 700 | 60 | 4.2 | 0.1 | 0.26 | 0.34 |
| Chetwynd | 605 | -35 | -38 | 27 | 18 | 5500 | 15 | 70 | 400 | 0.6 | 625 | 60 | 2.4 | 0.2 | 0.30 | 0.40 |
| Chilliwack | 10 | -9 | -11 | 30 | 20 | 2780 | 8 | 139 | 1625 | 1.7 | 1700 | 160 | 2.2 | 0.3 | 0.35 | 0.47 |
| Colwood Region |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Colwood (Colwood Corners) | 64 | -6 | -8 | 26 | 18 | 2900 | 10 | 100 | 1000 | 1.13 | 1030 | 220 | 1.7 | 0.3 | 0.48 | 0.63 |
| Colwood (Royal Bay Village) | 20 | -5 | -7 | 24 | 17 | 2600 | 8 | 80 | 910 | 1.05 | 930 | 220 | 1.2 | 0.3 | 0.48 | 0.63 |
| Colwood (Triangle Mountain) | 220 | -7 | -9 | 25 | 17 | 3300 | 10 | 105 | 11885 | 1.29 | 1225 | 220 | 2.5 | 0.3 | 0.48 | 0.63 |
| Comox | 15 | -7 | -9 | 27 | 18 | 2930 | 10 | 106 | 1175 | 1.3 | 1200 | 260 | 2.4 | 0.4 | 0.41 | 0.48 |
| Courtenay | 10 | -7 | -9 | 28 | 18 | 2930 | 10 | 106 | 1400 | 1.5 | 1450 | 260 | 2.4 | 0.4 | 0.41 | 0.48 |
| Cranbrook | 910 | -26 | -28 | 32 | 18 | 4400 | 12 | 59 | 275 | 0.3 | 400 | 100 | 3.0 | 0.2 | 0.25 | 0.33 |
| Crescent Valley | 585 | -18 | -20 | 31 | 20 | 3650 | 10 | 54 | 675 | 0.8 | 850 | 80 | 4.2 | 0.1 | 0.25 | 0.33 |
| Crofton | 5 | -4 | -6 | 28 | 19 | 2880 | 8 | 86 | 925 | 1.1 | 950 | 160 | 1.8 | 0.2 | 0.32 | 0.40 |
| Dawson Creek | 665 | -38 | -40 | 27 | 18 | 5900 | 18 | 75 | 325 | 0.5 | 475 | 100 | 2.5 | 0.2 | 0.30 | 0.40 |
| Dease Lake | 800 | -37 | -40 | 24 | 15 | 6730 | 10 | 45 | 265 | 0.6 | 425 | 50 | 2.8 | 0.1 | 0.23 | 0.30 |
| Dog Creek | 450 | -28 | -30 | 29 | 17 | 4800 | 10 | 48 | 275 | 0.4 | 375 | 100 | 1.8 | 0.2 | 0.27 | 0.35 |
| Duncan | 10 | -6 | -8 | 28 | 19 | 2980 | 8 | 103 | 1000 | 1.1 | 1050 | 180 | 1.8 | 0.4 | 0.31 | 0.39 |
| Elko | 1065 | -28 | -31 | 30 | 19 | 4600 | 13 | 64 | 440 | 0.5 | 650 | 100 | 3.6 | 0.2 | 0.30 | 0.40 |
| Fernie | 1010 | -27 | -30 | 30 | 19 | 4750 | 13 | 118 | 860 | 0.9 | 1175 | 100 | 4.5 | 0.2 | 0.30 | 0.40 |
| Fort Nelson | 465 | -39 | -42 | 28 | 18 | 6710 | 15 | 70 | 325 | 0.6 | 450 | 80 | 2.4 | 0.1 | 0.23 | 0.30 |
| Fort St. John | 685 | -35 | -37 | 26 | 18 | 5750 | 15 | 72 | 320 | 0.5 | 475 | 100 | 2.8 | 0.1 | 0.29 | 0.39 |
| Glacier | 1145 | -27 | -30 | 27 | 17 | 5800 | 10 | 70 | 625 | 0.8 | 1500 | 80 | 9.4 | 0.2 | 0.24 | 0.32 |
| Golden | 790 | -27 | -30 | 30 | 17 | 4750 | 10 | 55 | 325 | 0.6 | 500 | 100 | 3.7 | 0.2 | 0.26 | 0.35 |
| Gold River | 120 | -8 | -11 | 31 | 18 | 3230 | 13 | 200 | 2730 | 2.8 | 2850 | 250 | 2.8 | 0.6 | 0.24 | 0.32 |
| Grand Forks | 565 | -19 | -22 | 34 | 20 | 3820 | 10 | 48 | 390 | 0.5 | 475 | 80 | 2.8 | 0.1 | 0.30 | 0.40 |
| Greenwood | 745 | -20 | -23 | 34 | 20 | 4100 | 10 | 64 | 430 | 0.5 | 550 | 80 | 3.6 | 0.1 | 0.30 | 0.40 |
| Hope | 40 | -13 | -15 | 31 | 20 | 2820 | 8 | 139 | 1825 | 1.9 | 1900 | 140 | 2.8 | 0.7 | 0.47 | 0.63 |
| Jordan River | 20 | -1 | -3 | 22 | 17 | 2900 | 12 | 170 | 2300 | 2.4 | 2370 | 250 | 1.2 | 0.4 | 0.44 | 0.55 |
| Kamloops | 355 | -23 | -25 | 34 | 20 | 3450 | 13 | 42 | 225 | 0.2 | 275 | 80 | 1.8 | 0.2 | 0.30 | 0.40 |
| Kaslo | 545 | -17 | -20 | 30 | 19 | 3830 | 10 | 55 | 660 | 0.8 | 850 | 80 | 2.8 | 0.1 | 0.23 | 0.31 |
| Kelowna | 350 | -17 | -20 | 33 | 20 | 3400 | 12 | 43 | 260 | 0.3 | 325 | 80 | 1.7 | 0.1 | 0.30 | 0.40 |
| Kimberley | 1090 | -25 | -27 | 31 | 18 | 4650 | 12 | 59 | 350 | 0.4 | 500 | 100 | 3.0 | 0.2 | 0.25 | 0.33 |
| Kitimat Plant | 15 | -16 | -18 | 25 | 16 | 3750 | 13 | 193 | 2100 | 2.2 | 2500 | 220 | 5.5 | 0.8 | 0.36 | 0.48 |
| Kitimat Townsite | 130 | -16 | -18 | 24 | 16 | 3900 | 13 | 171 | 1900 | 2.0 | 2300 | 220 | 6.5 | 0.8 | 0.36 | 0.48 |
| Ladysmith | 80 | -7 | -9 | 27 | 19 | 2920 | 8 | 97 | 1075 | 1.2 | 1160 | 180 | 2.4 | 0.4 | 0.32 | 0.40 |
| Langford | 80 | -4 | -6 | 27 | 19 | 2750 | 9 | 135 | 1095 | 1.2 | 1125 | 220 | 1.8 | 0.3 | 0.32 | 0.40 |
| Lillooet | 245 | -21 | -23 | 34 | 20 | 3400 | 10 | 70 | 300 | 0.3 | 350 | 100 | 2.1 | 0.1 | 0.33 | 0.44 |
| Lytton | 325 | -17 | -20 | 35 | 20 | 3300 | 10 | 70 | 330 | 0.3 | 425 | 80 | 2.8 | 0.3 | 0.32 | 0.43 |
| Mackenzie | 765 | -34 | -38 | 27 | 17 | 5550 | 10 | 50 | 350 | 0.5 | 650 | 60 | 5.1 | 0.2 | 0.25 | 0.32 |
| Masset | 10 | -5 | -7 | 17 | 15 | 3700 | 13 | 80 | 1350 | 1.5 | 1400 | 400 | 1.8 | 0.4 | 0.50 | 0.61 |
| McBride | 730 | -29 | -32 | 29 | 18 | 4980 | 13 | 54 | 475 | 0.6 | 650 | 60 | 4.3 | 0.2 | 0.27 | 0.35 |
| McLeod Lake | 695 | -35 | -37 | 27 | 17 | 5450 | 10 | 50 | 350 | 0.5 | 650 | 60 | 4.1 | 0.2 | 0.25 | 0.32 |
| Merritt | 570 | -24 | -27 | 34 | 20 | 3900 | 8 | 54 | 240 | 0.2 | 310 | 80 | 1.8 | 0.3 | 0.33 | 0.44 |
| Mission City | 45 | -9 | -11 | 30 | 20 | 2850 | 13 | 123 | 1650 | 1.7 | 1700 | 160 | 2.4 | 0.3 | 0.32 | 0.43 |
| Montrose | 615 | -16 | -18 | 32 | 20 | 3600 | 10 | 54 | 480 | 0.6 | 700 | 60 | 4.1 | 0.1 | 0.26 | 0.35 |
| Nakusp | 445 | -20 | -22 | 31 | 20 | 3560 | 10 | 60 | 650 | 0.8 | 850 | 60 | 4.4 | 0.1 | 0.25 | 0.33 |
| Nanaimo | 15 | -6 | -8 | 27 | 19 | 2920 | 10 | 91 | 1000 | 1.1 | 1050 | 200 | 2.1 | 0.4 | 0.38 | 0.48 |
| Nelson | 600 | -18 | -20 | 31 | 20 | 3500 | 10 | 59 | 460 | 0.6 | 700 | 60 | 4.2 | 0.1 | 0.25 | 0.33 |
| Ocean Falls | 10 | -10 | -12 | 23 | 17 | 3400 | 13 | 260 | 4150 | 4.2 | 4300 | 350 | 3.9 | 0.8 | 0.44 | 0.59 |
| Oliver | 307 | -16 | -18 | 33 | 20 | 3400 | 10 | 40 | 275 | 0.28 | 300 | 60 | 1.0 | 0.1 | 0.40 | 0.52 |
| Osoyoos | 285 | -14 | -17 | 35 | 21 | 3100 | 10 | 48 | 275 | 0.3 | 310 | 60 | 1.1 | 0.1 | 0.30 | 0.40 |
| Parksville | 40 | -6 | -8 | 26 | 19 | 2990 | 10 | 91 | 1200 | 1.3 | 1250 | 200 | 2.0 | 0.4 | 0.40 | 0.48 |
| Penticton | 350 | -15 | -17 | 33 | 20 | 3350 | 10 | 48 | 275 | 0.3 | 300 | 60 | 1.3 | 0.1 | 0.30 | 0.40 |
| Port Alberni | 15 | -5 | -8 | 31 | 19 | 3100 | 10 | 161 | 1900 | 2.0 | 2000 | 240 | 2.6 | 0.4 | 0.24 | 0.32 |
| Port Alice | 25 | -3 | -6 | 26 | 17 | 3010 | 13 | 200 | 3300 | 3.4 | 3340 | 220 | 1.1 | 0.4 | 0.24 | 0.32 |
| Port Hardy | 5 | -5 | -7 | 20 | 16 | 3440 | 13 | 150 | 1775 | 1.9 | 1850 | 220 | 0.9 | 0.4 | 0.36 | 0.48 |
| Port McNeill | 5 | -5 | -7 | 22 | 17 | 3410 | 13 | 128 | 1750 | 1.9 | 1850 | 260 | 1.1 | 0.4 | 0.36 | 0.48 |
| Port Renfrew | 20 | -3 | -5 | 24 | 17 | 2900 | 13 | 200 | 3600 | 3.6 | 3675 | 270 | 1.1 | 0.4 | 0.42 | 0.52 |
| Powell River | 10 | -7 | -9 | 26 | 18 | 3100 | 10 | 80 | 1150 | 1.3 | 1200 | 220 | 1.7 | 0.4 | 0.39 | 0.48 |
| Prince George | 580 | -32 | -36 | 28 | 18 | 4720 | 15 | 54 | 425 | 0.6 | 600 | 80 | 3.4 | 0.2 | 0.28 | 0.37 |
| Prince Rupert | 20 | -13 | -15 | 19 | 15 | 3900 | 13 | 160 | 2750 | 2.8 | 2900 | 240 | 1.9 | 0.4 | 0.43 | 0.54 |
| Princeton | 655 | -24 | -29 | 33 | 19 | 4250 | 10 | 43 | 235 | 0.4 | 350 | 80 | 2.9 | 0.6 | 0.27 | 0.36 |
| Qualicum Beach | 10 | -7 | -9 | 27 | 19 | 2990 | 10 | 96 | 1200 | 1.3 | 1250 | 200 | 2.0 | 0.4 | 0.41 | 0.48 |
| Queen Charlotte City | 35 | -6 | -8 | 21 | 16 | 3520 | 13 | 110 | 1300 | 1.5 | 1350 | 360 | 1.8 | 0.4 | 0.50 | 0.61 |
| Quesnel | 475 | -31 | -33 | 30 | 17 | 4650 | 10 | 50 | 380 | 0.5 | 525 | 80 | 3.0 | 0.1 | 0.24 | 0.31 |
| Revelstoke | 440 | -20 | -23 | 31 | 19 | 4000 | 13 | 55 | 625 | 0.8 | 950 | 80 | 7.2 | 0.1 | 0.24 | 0.32 |
| Salmon Arm | 425 | -19 | -24 | 33 | 21 | 3650 | 13 | 48 | 400 | 0.5 | 525 | 80 | 3.5 | 0.1 | 0.29 | 0.39 |
| Sandspit | 5 | -4 | -6 | 18 | 15 | 3450 | 13 | 86 | 1300 | 1.5 | 1350 | 500 | 1.8 | 0.4 | 0.59 | 0.72 |
| Sechelt | 25 | -6 | -8 | 27 | 20 | 2680 | 10 | 75 | 1140 | 1.3 | 1200 | 160 | 1.8 | 0.4 | 0.38 | 0.48 |
| Sidney | 10 | -4 | -6 | 26 | 18 | 2850 | 8 | 96 | 825 | 1.0 | 850 | 160 | 1.1 | 0.2 | 0.34 | 0.42 |
| Smithers | 500 | -29 | -31 | 26 | 17 | 5040 | 13 | 60 | 325 | 0.6 | 500 | 120 | 3.5 | 0.2 | 0.30 | 0.40 |
| Smith River | 660 | -45 | -47 | 26 | 17 | 7100 | 10 | 64 | 300 | 0.6 | 500 | 40 | 2.8 | 0.1 | 0.24 | 0.30 |
| Sooke | 20 | -1 | -3 | 21 | 16 | 2900 | 9 | 130 | 1250 | 1.4 | 1280 | 220 | 1.3 | 0.3 | 0.38 | 0.48 |
| Squamish | 5 | -9 | -11 | 29 | 20 | 2950 | 10 | 140 | 2050 | 2.1 | 2200 | 160 | 2.8 | 0.7 | 0.38 | 0.50 |
| Stewart | 10 | -17 | -20 | 25 | 16 | 4350 | 13 | 135 | 1300 | 1.5 | 1900 | 180 | 7.9 | 0.8 | 0.27 | 0.36 |
| Tahsis | 25 | -4 | -6 | 26 | 18 | 3150 | 13 | 200 | 3845 | 3.9 | 3900 | 300 | 1.1 | 0.4 | 0.26 | 0.34 |
| Taylor | 515 | -35 | -37 | 26 | 18 | 5720 | 15 | 72 | 320 | 0.5 | 450 | 100 | 2.3 | 0.1 | 0.30 | 0.40 |
| Terrace | 60 | -19 | -21 | 27 | 17 | 4150 | 13 | 120 | 950 | 1.1 | 1150 | 200 | 5.4 | 0.6 | 0.27 | 0.36 |
| Tofino | 10 | -2 | -4 | 20 | 16 | 3150 | 13 | 193 | 3275 | 3.4 | 3300 | 300 | 1.1 | 0.4 | 0.51 | 0.68 |
| Trail | 440 | -14 | -17 | 33 | 20 | 3600 | 10 | 54 | 580 | 0.7 | 700 | 60 | 4.1 | 0.1 | 0.26 | 0.35 |
| Ucluelet | 5 | -2 | -4 | 18 | 16 | 3120 | 13 | 180 | 3175 | 3.3 | 3200 | 280 | 1.0 | 0.4 | 0.51 | 0.68 |
| Vancouver Region |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Burnaby (General) | 137 | -7 | -9 | 25 | 17 | 2735 | 10 | 140 | 1840 | 1.92 | 1900 | 160 | 2.7 | 0.4 | 0.36 | 0,47 |
| Burnaby (Simon Fraser Univ.) | 330 | -7 | -9 | 25 | 17 | 3100 | 10 | 150 | 1850 | 1.9 | 1950 | 160 | 2.9 | 0.7 | 0.35 | 0.47 |
| Cloverdale | 10 | -8 | -10 | 29 | 20 | 2700 | 10 | 112 | 1350 | 1.4 | 1400 | 160 | 2.5 | 0.2 | 0.33 | 0.44 |
| Haney | 10 | -9 | -11 | 30 | 20 | 2840 | 10 | 134 | 1800 | 1.9 | 1950 | 160 | 2.4 | 0.2 | 0.33 | 0.44 |
| Ladner | 3 | -6 | -8 | 27 | 19 | 2600 | 10 | 80 | 1000 | 1.1 | 1050 | 160 | 1.3 | 0.2 | 0.37 | 0.46 |
| Langley | 15 | -8 | -10 | 29 | 20 | 2700 | 10 | 112 | 1450 | 1.5 | 1500 | 160 | 2.4 | 0.2 | 0.33 | 0.44 |
| New Westminster | 10 | -8 | -10 | 29 | 19 | 2800 | 10 | 134 | 1500 | 1.6 | 1575 | 160 | 2.3 | 0.2 | 0.33 | 0.44 |
| North Vancouver | 135 | -7 | -9 | 26 | 19 | 2910 | 12 | 150 | 2000 | 2.1 | 2100 | 160 | 3.0 | 0.3 | 0.34 | 0.45 |
| Richmond | 5 | -7 | -9 | 27 | 19 | 2800 | 10 | 86 | 1070 | 1.2 | 1100 | 160 | 1.5 | 0.2 | 0.36 | 0.45 |
| Surrey (88 Ave & 156 St.) | 90 | -8 | -10 | 29 | 20 | 2750 | 10 | 128 | 1500 | 1.6 | 1575 | 160 | 2.4 | 0.3 | 0.33 | 0.44 |
| Vancouver (City Hall) | 40 | -7 | -9 | 28 | 20 | 2825 | 10 | 112 | 1325 | 1.4 | 1400 | 160 | 1.8 | 0.2 | 0.34 | 0.45 |
| Vancouver (Granville St. & 41st Ave) | 120 | -6 | -8 | 28 | 20 | 2925 | 10 | 107 | 1325 | 1.4 | 1400 | 160 | 1.9 | 0.3 | 0.36 | 0.45 |
| West Vancouver | 45 | -7 | -9 | 28 | 19 | 2950 | 12 | 150 | 1600 | 1.7 | 1700 | 160 | 2.4 | 0.2 | 0.36 | 0.48 |
| Vernon | 405 | -20 | -23 | 33 | 20 | 3600 | 13 | 43 | 350 | 0.4 | 400 | 80 | 2.2 | 0.1 | 0.30 | 0.40 |
| Victoria Region |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Victoria | 10 | -4 | -6 | 24 | 17 | 2650 | 8 | 91 | 800 | 1.0 | 825 | 220 | 1.1 | 0.2 | 0.46 | 0.57 |
| Victoria (Gonzales Hts) | 65 | -4 | -6 | 24 | 17 | 2700 | 9 | 91 | 600 | 0.8 | 625 | 220 | 1.5 | 0.3 | 0.46 | 0.57 |
| Victoria (Mt Tolmie) | 125 | -6 | -8 | 24 | 16 | 2700 | 9 | 91 | 775 | 1.0 | 800 | 220 | 2.1 | 0.3 | 0.46 | 0.57 |
| Whistler | 665 | -17 | -20 | 30 | 20 | 4180 | 10 | 85 | 845 | 1.0 | 1215 | 160 | 9.5 | 0.9 | 0.24 | 0.32 |
| White Rock | 30 | -5 | -7 | 25 | 20 | 2620 | 10 | 80 | 1065 | 1.2 | 1100 | 160 | 2.0 | 0.2 | 0.33 | 0.44 |
| Williams Lake | 615 | -30 | -33 | 29 | 17 | 4400 | 10 | 48 | 350 | 0.5 | 425 | 80 | 2.4 | 0.2 | 0.27 | 0.35 |
| Youbou | 200 | -5 | -8 | 31 | 19 | 3050 | 10 | 161 | 2000 | 2.1 | 2100 | 200 | 3.5 | 0.7 | 0.26 | 0.32 |

Seismic Hazard for Part 4

The seismic hazard values to be used for the design of buildings under Part 4 can be obtained from the 2020 National Building Code of Canada Seismic Hazard Tool 
( https://doi.org/10.23687/b1bd3cf0-0672-47f4-8bfa-290ae75fde9b), which provides seismic hazard values for any site in Canada defined by latitude, longitude and site designation. The seismic hazard values used for the design of buildings under Part 4 must correspond to the applicable probability of exceedance stated in Subsection 4.1.8. The tool also provides seismic hazard values at additional probabilities and periods.

Seismic hazard values can be appreciably different for localities across a large locale. Therefore, applying the same seismic hazard value to a large geographic area could result in buildings being over-designed or under-designed. Given the large number of data points in Canada, listing every locality in a table is not practical. For archival purposes, the seismic hazard values for 679 specific latitudes and longitudes are reproduced from the 2020 National Building Code of Canada Seismic Hazard Tool on NPARC at https://doi.org/10.4224/nqzr-dz38. The digital properties of the NPARC website are more suited for a static, archival data set. As such, Figure A-1.1.3.1.(4) identifies the NPARC website as the primary data set for the specified latitude and longitudes.

The parameters used to represent seismic hazard for specific geographical locations are the 5%-damped horizontal spectral acceleration for periods of 0.2 s, 0.5 s, 1.0 s, 2.0 s, 5.0 s and 10.0 s, the horizontal peak ground acceleration (PGA) and the horizontal peak ground velocity (PGV) corresponding to a 2% probability of being exceeded in 50 years. The six spectral acceleration parameters are deemed sufficient to define spectra closely matching the shape of the uniform hazard spectra (UHS) for design purposes. Spectral acceleration values for additional periods are provided for use in the selection of ground motion time histories. Spectral acceleration values for additional probabilities of exceedance are also provided.

The seismic hazard values are mean values based on a statistical analysis of the earthquakes that have been experienced in Canada and adjacent regions.(11) They were updated for the 2020 edition of the Code by slightly revising the seismic source zones, adding the Leech River and Devil's Mountain fault sources near Victoria, B.C.,(12) increasing the rate of occurrence of great earthquakes on the Cascadia subduction zone to match new information, revising the ground motion models (GMMs),(13) and using a probabilistic model to combine all inputs.

In addition, the method of determining seismic hazard values for different site designations has changed. For the NBC 2015, the seismic hazard values were calculated for reference Site Class C, and the values for other site designations were determined by applying a site coefficient to the calculated values. For the NBC 2020, the seismic hazard values for each site designation were calculated directly.

For almost all locations, the revised GMMs are the most significant reason for changes in the seismic hazard values from the NBC 2015. In general, the estimated seismic hazard has increased across Canada.

Further details regarding the representation of seismic hazard can be found in the Commentary entitled Design for Seismic Effects in the “Structural Commentaries (User's Guide – NBC 2020: Part 4 of Division B).”

Seismic Hazard for Part 9

Table C-3 lists the seismic hazard values to be used in the application of the prescriptive requirements in Part 9 relating to lateral loads due to earthquake. For locations not listed in Table C-3, the seismic hazard values to be used can be determined using the 2020 National Building Code of Canada Seismic Hazard Tool (https://doi.org/10.23687/b1bd3cf0-0672-47f4-8bfa-290ae75fde9b).

The Tool provides seismic hazard values for any site in Canada based on the following information:

- Latitude and longitude of the site’s location: Seismic hazard values can be appreciably different for localities across a large locale. Therefore, applying the same seismic hazard value to a large geographic area could result in buildings being over-designed or under-designed.

- Site designation in terms of Site Class, XS, where S is the Site Class (see Sentence 4.1.8.4.(3)).

The procedure to determine the seismic design parameter, Smax, for a site is as follows:

- Go to the 2020 National Building Code of Canada Seismic Hazard Tool (https://doi.org/10.23687/b1bd3cf0-0672-47f4-8bfa-290ae75fde9b).

- Select “Site Class (Xs)” as the site designation.

- Select the appropriate Site Class (A, B, C, D or E).

- Enter the latitude and longitude of the site’s location manually, or determine the latitude and longitude from an address or current location.

- Click “Obtain Seismic Hazard Values.” The following values are needed to determine Smax: Sa(0.2,XS) and Sa(0.5,XS).

- Determine S(0.2,XS) in accordance with Sentence 4.1.8.4.(6):
	S(0.2,XS) = Sa(0.2,XS) or Sa(0.5,XS), whichever is greater

- Determine S(0.5,XS) in accordance with Sentence 4.1.8.4.(6):
	S(0.5,XS) = Sa(0.5,XS)

- Determine Smax:
	Smax = (2/3)S(0.2,XS) or S(0.5,XS), whichever is greater

- Round Smax to three significant digits.

In cases where the Site Class is determined in accordance with Sentence 4.1.8.4.(3),

Smax is calculated for the determined Site Class. In cases where the Site Class is

unknown, Smax must be calculated for each of Site Classes A, B, C, D and E, by

repeating Steps 1 to 9, and the highest value of Smax among all the Site Classes used

for design.

Example

Consider a site in Strathmore, Alberta, a location not listed in Table C-3. The latitude

and longitude of Strathmore are 51.04040 and −113.40205, respectively. In this

example, the Site Class is determined by a geotechnical investigation to be Site Class

C.

Using the 2020 National Building Code of Canada Seismic Hazard Tool (Step 1), select

“Site Class (XS)” as the site designation (Step 2). Select “C” as the Site Class (Step 3).

Under “Location,” enter the latitude, 51.04040, and longitude, −113.40205, and then

click “Set coordinates” (Step 4). Click “Obtain Seismic Hazard Values” to obtain the

values for Sa(0.2,XC) and Sa(0.5,XC), which are 0.191 and 0.125, respectively (Step 5).

Next, determine S(0.2,XC) as follows (Step 6):

S(0.2,XC) = Sa(0.2,XC) or Sa(0.5,XC), whichever is greater

S(0.2,XC) = 0.191 or 0.125, whichever is greater

S(0.2,XC) = 0.191

Now, determine S(0.5,XC) as follows (Step 7):

S(0.5,XC) = Sa(0.5,XC)

S(0.5,XC) = 0.125

Finally, determine Smax for Site Class C as follows (Step 8):

Smax = (2/3)S(0.2,XC) or S(0.5,XC), whichever is greater

Smax = 0.127333 or 0.125, whichever is greater

Smax = 0.127 (rounded to three significant digits according to Step 9)

If the Site Class is unknown, this procedure is repeated to determine Smax for each of

Site Classes A, B, C, D and E. For Strathmore, the resulting values of Smax are as

follows: 0.071 for Site Class A, 0.097 for Site Class B, 0.127 for Site Class C, 0.213 for

Site Class D, and 0.254 for Site Class E. The highest value is selected as Smax for

unknown Site Class: 0.254.

Table C-3

Seismic Design Parameter, Smax,  for Selected Locations in Canada

| Province and Location | Smax for Unknown Site Class | Smax According to Site Class |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  |  | A | B | C | D | E |
| British Columbia |  |  |  |  |  |  |
| 100 Mile House | 0.283 | 0.0661 | 0.084 | 0.144 | 0.239 | 0.283 |
| Abbotsford | 1.07 | 0.381 | 0.473 | 0.742 | 1.01 | 1.07 |
| Agassiz | 0.802 | 0.25 | 0.313 | 0.507 | 0.729 | 0.802 |
| Alberni | 1.62 | 0.573 | 0.74 | 1.25 | 1.57 | 1.62 |
| Ashcroft | 0.389 | 0.098 | 0.123 | 0.209 | 0.335 | 0.389 |
| Bamfield | 2.27 | 0.919 | 1.18 | 1.92 | 2.23 | 2.27 |
| Beatton River | 0.248 | 0.074 | 0.102 | 0.13 | 0.211 | 0.248 |
| Bella Bella | 0.585 | 0.126 | 0.169 | 0.312 | 0.501 | 0.585 |
| Bella Coola | 0.417 | 0.0887 | 0.117 | 0.22 | 0.355 | 0.417 |
| Burns Lake | 0.214 | 0.0475 | 0.0596 | 0.107 | 0.179 | 0.214 |
| Cache Creek | 0.381 | 0.0953 | 0.12 | 0.204 | 0.327 | 0.381 |
| Campbell River | 1.14 | 0.346 | 0.452 | 0.789 | 1.07 | 1.14 |
| Carmi | 0.298 | 0.0693 | 0.0867 | 0.153 | 0.251 | 0.298 |
| Castlegar | 0.252 | 0.0592 | 0.076 | 0.124 | 0.211 | 0.252 |
| Chetwynd | 0.334 | 0.0867 | 0.115 | 0.174 | 0.286 | 0.334 |
| Chilliwack | 0.887 | 0.294 | 0.367 | 0.583 | 0.82 | 0.887 |
| Comox | 1.27 | 0.408 | 0.53 | 0.912 | 1.21 | 1.27 |
| Courtenay | 1.29 | 0.415 | 0.538 | 0.926 | 1.22 | 1.29 |
| Cranbrook | 0.321 | 0.0713 | 0.0933 | 0.158 | 0.269 | 0.321 |
| Crescent Valley | 0.252 | 0.0589 | 0.076 | 0.124 | 0.211 | 0.252 |
| Crofton | 1.75 | 0.667 | 0.813 | 1.32 | 1.7 | 1.75 |
| Dawson Creek | 0.275 | 0.0767 | 0.105 | 0.14 | 0.233 | 0.275 |
| Dease Lake | 0.342 | 0.0648 | 0.0895 | 0.173 | 0.289 | 0.342 |
| Dog Creek | 0.338 | 0.08 | 0.101 | 0.177 | 0.287 | 0.338 |
| Duncan | 1.86 | 0.713 | 0.867 | 1.42 | 1.81 | 1.86 |
| Elko | 0.39 | 0.09 | 0.117 | 0.197 | 0.33 | 0.39 |
| Fernie | 0.404 | 0.104 | 0.137 | 0.21 | 0.345 | 0.404 |
| Fort Nelson | 0.284 | 0.0753 | 0.103 | 0.144 | 0.239 | 0.284 |
| Fort St. John | 0.27 | 0.076 | 0.104 | 0.138 | 0.229 | 0.27 |
| Glacier | 0.356 | 0.094 | 0.123 | 0.184 | 0.303 | 0.356 |
| Golden | 0.425 | 0.126 | 0.164 | 0.239 | 0.369 | 0.425 |
| Gold River | 1.73 | 0.6 | 0.776 | 1.31 | 1.66 | 1.73 |
| Grand Forks | 0.272 | 0.0641 | 0.0807 | 0.138 | 0.229 | 0.272 |
| Greenwood | 0.283 | 0.0662 | 0.0833 | 0.144 | 0.238 | 0.283 |
| Hope | 0.672 | 0.197 | 0.246 | 0.405 | 0.601 | 0.672 |
| Jordan River | 2.31 | 0.902 | 1.15 | 1.90 | 2.227 | 2.31 |
| Kamloops | 0.304 | 0.0707 | 0.0887 | 0.157 | 0.257 | 0.304 |
| Kaslo | 0.271 | 0.0615 | 0.08 | 0.132 | 0.226 | 0.271 |
| Kelowna | 0.302 | 0.07 | 0.088 | 0.155 | 0.255 | 0.302 |
| Kimberley | 0.311 | 0.0707 | 0.0927 | 0.153 | 0.261 | 0.311 |
| Kitimat Plant | 0.456 | 0.091 | 0.123 | 0.233 | 0.385 | 0.456 |
| Kitimat Townsite | 0.456 | 0.091 | 0.123 | 0.233 | 0.385 | 0.456 |
| Ladysmith | 1.7 | 0.636 | 0.773 | 1.28 | 1.65 | 1.7 |
| Langford | 2.07 | 0.887 | 1.09 | 1.74 | 2.06 | 2.07 |
| Lillooet | 0.503 | 0.147 | 0.187 | 0.289 | 0.442 | 0.503 |
| Lytton | 0.532 | 0.155 | 0.196 | 0.309 | 0.469 | 0.532 |
| Mackenzie | 0.314 | 0.0773 | 0.101 | 0.162 | 0.268 | 0.314 |
| Masset | 1.56 | 0.491 | 0.605 | 1.05 | 1.44 | 1.56 |
| McBride | 0.396 | 0.116 | 0.151 | 0.222 | 0.343 | 0.396 |
| McLeod Lake | 0.295 | 0.0707 | 0.092 | 0.15 | 0.251 | 0.295 |
| Merritt | 0.423 | 0.108 | 0.136 | 0.23 | 0.364 | 0.423 |
| Mission City | 1.01 | 0.354 | 0.439 | 0.692 | 0.949 | 1.01 |
| Montrose | 0.251 | 0.059 | 0.0753 | 0.124 | 0.21 | 0.251 |
| Nakusp | 0.259 | 0.0599 | 0.0773 | 0.127 | 0.216 | 0.259 |
| Nanaimo | 1.55 | 0.571 | 0.7 | 1.15 | 1.5 | 1.55 |
| Nelson | 0.255 | 0.0587 | 0.076 | 0.124 | 0.213 | 0.255 |
| Ocean Falls | 0.503 | 0.106 | 0.141 | 0.264 | 0.428 | 0.503 |
| Osoyoos | 0.365 | 0.0867 | 0.109 | 0.192 | 0.311 | 0.365 |
| Parksville | 1.46 | 0.509 | 0.638 | 1.08 | 1.41 | 1.46 |
| Penticton | 0.337 | 0.078 | 0.098 | 0.175 | 0.285 | 0.337 |
| Port Alberni | 1.66 | 0.594 | 0.768 | 1.29 | 1.61 | 1.66 |
| Port Alice | 1.86 | 0.84 | 1.06 | 1.64 | 1.85 | 1.86 |
| Port Hardy | 1.29 | 0.372 | 0.486 | 0.853 | 1.18 | 1.29 |
| Port McNeill | 1.31 | 0.385 | 0.504 | 0.878 | 1.21 | 1.31 |
| Port Renfrew | 2.32 | 0.923 | 1.18 | 1.94 | 2.28 | 2.32 |
| Powell River | 1.08 | 0.343 | 0.43 | 0.75 | 1.02 | 1.08 |
| Prince George | 0.234 | 0.0497 | 0.0644 | 0.114 | 0.195 | 0.234 |
| Prince Rupert | 0.684 | 0.149 | 0.199 | 0.367 | 0.587 | 0.684 |
| Princeton | 0.492 | 0.135 | 0.171 | 0.278 | 0.43 | 0.492 |
| Qualicum Beach | 1.45 | 0.496 | 0.633 | 1.08 | 1.39 | 1.45 |
| Queen Charlotte City | 2.52 | 1.05 | 1.28 | 2.03 | 2.45 | 2.52 |
| Quesnel | 0.225 | 0.0475 | 0.0605 | 0.111 | 0.188 | 0.225 |
| Revelstoke | 0.275 | 0.0634 | 0.082 | 0.135 | 0.23 | 0.275 |
| Salmon Arm | 0.264 | 0.0618 | 0.0787 | 0.132 | 0.222 | 0.264 |
| Sandspit | 2.2 | 0.833 | 1.02 | 1.68 | 2.11 | 2.2 |
| Sechelt | 1.25 | 0.455 | 0.559 | 0.9 | 1.2 | 1.25 |
| Sidney | 1.85 | 0.74 | 0.907 | 1.44 | 1.81 | 1.85 |
| Smithers | 0.236 | 0.0516 | 0.0645 | 0.118 | 0.197 | 0.236 |
| Smith River | 0.859 | 0.339 | 0.439 | 0.598 | 0.807 | 0.859 |
| Sooke | 2.21 | 0.873 | 1.07 | 1.78 | 2.17 | 2.21 |
| Squamish | 0.963 | 0.334 | 0.415 | 0.659 | 0.903 | 0.963 |
| Stewart | 0.427 | 0.0828 | 0.113 | 0.217 | 0.361 | 0.427 |
| Tahsis | 1.97 | 0.807 | 1 | 1.62 | 1.93 | 1.97 |
| Taylor | 0.267 | 0.0753 | 0.103 | 0.137 | 0.226 | 0.267 |
| Terrace | 0.406 | 0.08 | 0.107 | 0.205 | 0.342 | 0.406 |
| Tofino | 2.25 | 0.903 | 1.16 | 1.89 | 2.2 | 2.25 |
| Trail | 0.252 | 0.0594 | 0.076 | 0.125 | 0.21 | 0.252 |
| Ucluelet | 2.3 | 0.936 | 1.21 | 1.96 | 2.26 | 2.3 |
| Vancouver Region |  |  |  |  |  |  |
| Burnaby (Simon Fraser Univ.) | 1.14 | 0.416 | 0.513 | 0.806 | 1.08 | 1.14 |
| Cloverdale | 1.18 | 0.434 | 0.535 | 0.839 | 1.13 | 1.18 |
| Haney | 1.06 | 0.378 | 0.467 | 0.736 | 1 | 1.06 |
| Ladner | 1.34 | 0.504 | 0.618 | 0.971 | 1.29 | 1.34 |
| Langley | 1.15 | 0.419 | 0.517 | 0.812 | 1.09 | 1.15 |
| New Westminster | 1.18 | 0.433 | 0.533 | 0.837 | 1.12 | 1.18 |
| North Vancouver | 1.17 | 0.429 | 0.529 | 0.831 | 1.11 | 1.17 |
| Richmond | 1.29 | 0.479 | 0.589 | 0.924 | 1.23 | 1.29 |
| Surrey (88 Ave & 156 St.) | 1.17 | 0.427 | 0.525 | 0.824 | 1.11 | 1.17 |
| Vancouver (City Hall) | 1.24 | 0.458 | 0.563 | 0.884 | 1.18 | 1.24 |
| Vancouver (Granville St. & 41st Ave) | 1.26 | 0.466 | 0.573 | 0.899 | 1.2 | 1.26 |
| West Vancouver | 1.2 | 0.441 | 0.544 | 0.855 | 1.14 | 1.2 |
| Vernon | 0.273 | 0.0639 | 0.0807 | 0.138 | 0.23 | 0.273 |
| Victoria Region |  |  |  |  |  |  |
| Victoria | 2.01 | 0.86 | 1.06 | 1.68 | 2 | 2.01 |
| Victoria (Gonzales Hts) | 1.99 | 0.853 | 1.05 | 1.66 | 1.98 | 1.99 |
| Victoria (Mt Tolmie) | 1.96 | 0.82 | 1.01 | 1.6 | 1.94 | 1.96 |
| Whistler | 0.748 | 0.239 | 0.301 | 0.478 | 0.684 | 0.748 |
| White Rock | 1.27 | 0.471 | 0.579 | 0.907 | 1.21 | 1.27 |
| Williams Lake | 0.274 | 0.064 | 0.0813 | 0.14 | 0.231 | 0.274 |
| Youbou | 1.92 | 0.707 | 0.9 | 1.5 | 1.87 | 1.92 |

References

(1) Environment Canada, Climate Trends and Variation Bulletin: Annual 2007, 2008.

(2) Intergovernmental Panel on Climate Change (IPCC), Climate Change 2007: The Physical Science Basis. Contribution of Working Group I to the Fourth Assessment Report of the Intergovernmental Panel on Climate Change. S. Solomon, D. Qin, M. Manning, Z. Chen, M. Marquis, K.B. Averyt, M. Tignor and H.L. Miller (Eds.). Cambridge University Press, Cambridge, United Kingdom and New York, NY, USA, 
996 pp., 2007.

(3) American Society of Heating, Refrigerating, and Air-conditioning Engineers, Handbook of Fundamentals, Chapter 14 – Climatic Design Information, Atlanta, GA, 2009.

(4) Lowery, M.D. and Nash, J.E., A comparison of methods of fitting the double exponential distribution. J. of Hydrology, 10 (3), pp. 259–275, 1970.

(5) Newark, M.J., Welsh, L.E., Morris, R.J. and Dnes, W.V. Revised Ground Snow Loads for the 1990 NBC of Canada. Can. J. Civ. Eng., Vol. 16, No. 3, June 1989.

(6) Newark, M.J. A New Look at Ground Snow Loads in Canada. Proceedings, 41st Eastern Snow Conference, Washington, D.C., Vol. 29, pp. 59-63, 1984.

(7) Bruce, J.P. and Clark, R.H. Introduction to Hydrometeorology. Pergammon Press, London, 1966.

(8) Skerlj, P.F. and Surry, D. A Critical Assessment of the DRWPs Used in CAN/CSA-A440-M90. Tenth International Conference on Wind Engineering, Wind Engineering into the 21st Century, Larsen, Larose & Livesay (eds), 1999 Balkema, Rotterdam, ISBN 90 5809 059 0.

(9) Cornick, S., Chown, G.A., et al. Committee Paper on Defining Climate Regions as a Basis for Specifying Requirements for Precipitation Protection for Walls. Institute for Research in Construction, National Research Council, Ottawa, April 2001.

(10) Boyd, D.W. Variations in Air Density over Canada. National Research Council of Canada, Division of Building Research, Technical Note No. 486, June 1967.

(11)  Adams, J., Allen, T., Halchuk, S., and Kolaj, M. Canada's 6th Generation Seismic Hazard Model, as Prepared for the 2020 National Building Code. 12th Canadian Conference on Earthquake Engineering, Québec, QC, paper 192-Mkvp-139, 2019.

(12) Halchuk, S., Allen, T., Adams, J., and Onur, T. Contribution of the Leech River Valley - Devil's Mountain Fault System to Seismic Hazard for Victoria, B.C. 12th Canadian Conference on Earthquake Engineering, Québec, QC, paper 192-WGm8-169, 2019.

(13) Kolaj, M., Allen, T., Mayfield, R., Adams, J., and Halchuk, S. Ground-Motion Models for the 6th Generation Seismic Hazard Model of Canada. 12th Canadian Conference on Earthquake Engineering, Québec, QC, paper 192-hHtH-159, 2019.

Appendix D

Fire-Performance Ratings

Section  D-1  General

The content of this Appendix was prepared on the recommendations of the Standing Committee on Fire Protection, which was established by the Canadian Commission on Building and Fire Codes (CCBFC) for this purpose.

D-1.1. Introduction

D-1.1.1. Scope

1)    This fire-performance information is presented in a form closely linked to the performance requirements and the minimum materials specifications of this Code.

2)    The ratings have been assigned only after careful consideration of all available literature on assemblies of common building materials, where they are adequately identified by description. The assigned values based on this information will, in most instances, be conservative when compared to the ratings determined on the basis of actual tests on individual assemblies.

3)    The fire-performance information set out in this Appendix applies to materials and assemblies of materials that comply in all essential details with the minimum structural design standards described in Part 4. Additional requirements, where appropriate, are described in other Sections of this Appendix.

4)    Section D-2 assigns fire-resistance ratings for walls, floors, roofs, columns and beams related to CAN/ULC-S101, “Standard Method of Fire Endurance Tests of Building Construction and Materials,” and describes methods for determining these ratings.

5)    Section D-3 assigns flame-spread ratings and smoke developed classifications for surface materials related to CAN/ULC-S102, “Standard Method of Test for Surface Burning Characteristics of Building Materials and Assemblies,” and CAN/ULC-S102.2, “Standard Method of Test for Surface Burning Characteristics of Flooring, Floor Coverings, and Miscellaneous Materials and Assemblies.”

6)    Section D-4 describes noncombustibility in building materials when tested in accordance with CAN/ULC-S114, “Standard Method of Test for Determination of Non-Combustibility in Building Materials.”

7)    Section D-5 contains requirements for the installation of fire doors and fire dampers in fire-rated stud wall assemblies.

8)    Section D-6 contains construction specifications for exterior wall assemblies that are deemed to satisfy the criteria of Clause 3.1.5.5.(1)(b) when tested in accordance with CAN/ULC-S134, “Standard Method of Fire Test of Exterior Wall Assemblies.”

9)    Section D-7 contains background information regarding fire test reports, obsolete materials and assemblies, assessment of archaic assemblies and the development of the component additive method.

D-1.1.2. Referenced Documents

1)    Where documents are referenced in this Appendix, they shall be the editions designated in Table D-1.1.2.

Table D-1.1.2.

Documents Referenced in Appendix D(1)

| Issuing Agency | Document Number(2) | Title of Document | Code Reference |
| --- | --- | --- | --- |
| ANSI | A208.1-2009 | Particleboard | D-3.1.1. |
| ASTM | C330/C330M-17 | Standard Specification for Lightweight Aggregates for Structural Concrete | D-1.4.3. |
| ASTM | C840-18b | Standard Specification for Application and Finishing of Gypsum Board | D-2.3.9. |
| ASTM | C1396/C1396M-17 | Standard Specification for Gypsum Board | D-1.5.1. D-3.1.1. |
| ASTM | D2898-10 | Standard Practice for Accelerated Weathering of Fire-Retardant-Treated Wood for Fire Testing | D-6.1.1. |
| CCBFC | NRCC 30629 | Supplement to the National Building Code of Canada 1990 | D-7.2. D-7.3. |
| CGSB | 4-GP-36M-1978 | Carpet Underlay, Fiber Type | D-3.1.1. |
| CGSB | CAN/CGSB-4.129-93 | Carpet for Commercial Use | D-3.1.1. |
| CGSB | CAN/CGSB-92.2-M90 | Trowel or Spray Applied Acoustical Material | D-2.3.4. |
| CSA | A23.1:19/A23.2:19 | Concrete materials and methods of concrete construction/Test methods and standard practices for concrete | D-1.4.3. |
| CSA | A23.3:19 | Design of concrete structures | D-2.1.5. D-2.6.6. D-2.8.2. |
| CSA | CAN/CSA-A82:14 | Fired masonry brick made from clay or shale | D-2.6.1. |
| CSA | A82.22-M1977 | Gypsum Plasters | D-3.1.1. |
| CSA | CAN/CSA A82.27-M91 | Gypsum Board | D-1.5.1. D-3.1.1. |
| CSA | A82.30-M1980 | Interior Furring, Lathing and Gypsum Plastering | D-1.7.2. D-2.3.9. D-2.5.1. |
| CSA | A165.1-14 | Concrete block masonry units | D-2.1.1. |
| CSA | O86:19 | Engineering design in wood | D-2.11.3. D-2.11.4. |
| CSA | O112.10-08 | Evaluation of Adhesives for Structural Wood Products (Limited Moisture Exposure) | D-2.3.6. |
| CSA | O121-17 | Douglas fir plywood | D-3.1.1. |
| CSA | O141:05 | Softwood Lumber | D-2.3.6. D-2.4.1. |
| CSA | O151-17 | Canadian softwood plywood | D-3.1.1. |
| CSA | O153-13 | Poplar plywood | D-3.1.1. |
| CSA | O325-16 | Construction sheathing | D-3.1.1. |
| CSA | O437.0-93 | OSB and Waferboard | D-3.1.1. |
| CSA | S16:19 | Design of steel structures | D-2.6.6. |
| NFPA | 80-2013 | Standard for Fire Doors and Other Opening Protectives | D-5.2.1. |
| ULC | CAN/ULC-S101-14 | Standard Method of Fire Endurance Tests of Building Construction and Materials | D-1.1.1. D-1.12.1. D-2.3.2. D-2.11.1. |
| ULC | CAN/ULC-S102-10 | Standard Method of Test for Surface Burning Characteristics of Building Materials and Assemblies | D-1.1.1. D-6.1.1. |
| ULC | CAN/ULC-S102.2:2018 | Standard Method of Test for Surface Burning Characteristics of Flooring, Floor Coverings, and Miscellaneous Materials and Assemblies | D-1.1.1. D-3.1.1. |
| ULC | CAN/ULC-S112.2-07 | Standard Method of Fire Test of Ceiling Firestop Flap Assemblies | D-2.3.10. D-2.3.11. |
| ULC | CAN/ULC-S114:2018 | Standard Method of Test for Determination of Non-Combustibility in Building Materials | D-1.1.1. D-4.1.1. D-4.2.1. |
| ULC | CAN/ULC-S134-13 | Standard Method of Fire Test of Exterior Wall Assemblies | D-1.1.1. D-6.1.1. |
| ULC | CAN/ULC-S702.1-14 | Standard for Mineral Fibre Thermal Insulation for Buildings, Part 1: Material Specification | D-2.3.4. D-2.3.5. D-2.6.1. D-6.1.1. D-7.4. |
| ULC | CAN/ULC-S703-09 | Standard for Cellulose Fibre Insulation (CFI) for Buildings | D-2.3.4. |
| ULC | CAN/ULC-S706.1:2016 | Standard for Wood Fibre Insulating Boards for Buildings | D-3.1.1. |

Notes to Table D-1.1.2.:

(1) While every effort was made to ensure the accuracy of the information in this Table, the NRC is not responsible for the accuracy, timeliness or reliability of the content presented therein. For all purposes of interpreting and applying the referenced standards, Code users should refer to the most recent official versions of the referenced editions.

(2) Some documents may have been reaffirmed or reapproved. Check with the applicable issuing agency for up-to-date information.

D-1.1.3. Applicability of Ratings

The ratings shown in this document apply if more specific test values are not available. The construction of an assembly that is the subject of an individual test report must be followed in all essential details if the fire-resistance rating reported is to be applied for use with this Code.

D-1.1.4. Higher Ratings

The authority having jurisdiction may allow higher fire-resistance ratings than those derived from this Appendix, where supporting evidence justifies a higher rating. Additional information is provided in summaries of published test information and the reports of fire tests carried out by NRC, which are included in Section D-7, Background Information.

D-1.1.5. Additional Information on Fire Rated Assemblies

Assemblies containing materials for which there is no nationally recognized standard are not included in this Appendix. Many such assemblies have been rated by Underwriters' Laboratories Inc. (UL), ULC Standards (ULC), or Intertek Testing Services NA Ltd. (ITS).

D-1.2. Interpretation of Test Results

D-1.2.1. Limitations

1)    The fire-performance ratings set out in this Appendix are based on those that would be obtained from the standard methods of test described in the Code. The test methods are essentially a means of comparing the performance of one building component or assembly with another in relation to its performance in fire.

2)    Since it is not practicable to measure the fire resistance of constructions in situ, they must be evaluated under some agreed test conditions. A specified fire-resistance rating is not necessarily the actual time that the assembly would endure in situ in a building fire, but is that which the particular construction must meet under the specified methods of test.

3)    Considerations arising from departures in use from the conditions established in the standard test methods may, in some circumstances, have to be taken into account by the designer and the authority having jurisdiction. Some of these conditions are covered at present by the provisions of the Code.

4)    For walls and partitions, the stud spacings previously specified as 16 or 24 inch have been converted to 400 and 600 mm, respectively, for consistency with other metric values; however, the use of equivalent imperial dimensions for stud spacing is permitted.

D-1.3. Concrete

D-1.3.1. Aggregates in Concrete

Low density aggregate concretes generally exhibit better fire performance than natural stone aggregate concretes. A series of tests on concrete masonry walls, combined with mathematical analysis of the test results, has allowed further distinctions between certain low density aggregates to be made.

D-1.4. Types of Concrete

D-1.4.1. Description

1)    For purposes of this Appendix, concretes are described as Types S, N, L, L 1, L2, L40S, L120S or L220S as described in Sentences (2) to (8).

2)    Type S concrete is the type in which the coarse aggregate is granite, quartzite, siliceous gravel or other dense materials containing at least 30% quartz, chert or flint.

3)    Type N concrete is the type in which the coarse aggregate is cinders, broken brick, blast furnace slag, limestone, calcareous gravel, trap rock, sandstone or similar dense material containing not more than 30% of quartz, chert or flint.

4)    Type L concrete is the type in which all the aggregate is expanded slag, expanded clay, expanded shale or pumice.

5)    Type L1 concrete is the type in which all the aggregate is expanded shale.

6)    Type L2 concrete is the type in which all the aggregate is expanded slag, expanded clay or pumice.

7)    Type L40S concrete is the type in which the fine portion of the aggregate is sand and low density aggregate in which the sand does not exceed 40% of the total volume of all aggregates in the concrete.

8)    Type L120S and Type L220S concretes are the types in which the fine portion of the aggregate is sand and low density aggregate in which the sand does not exceed 20% of the total volume of all aggregates in the concrete.

D-1.4.2. Determination of Ratings

Where concretes are described as being of Type S, N, L, L1 or L2, the rating applies to the concrete containing the aggregate in the group that provides the least fire resistance. If the nature of an aggregate cannot be determined accurately enough to place it in one of the groups, the aggregate shall be considered as being in the group that requires a greater thickness of concrete for the required fire resistance.

D-1.4.3. Description of Aggregates

1)    The descriptions of the aggregates in Type S and Type N concretes apply to the coarse aggregates only. Coarse aggregate for this purpose means that retained on a 5 mm sieve using the method of grading aggregates described in CSA A23.1/A23.2, “Concrete materials and methods of concrete construction/Test methods and standard practices for concrete.”

2)    Increasing the proportion of sand as fine aggregate in low density concretes requires increased thicknesses of material to produce equivalent fire-resistance ratings. Low density aggregates for Type L and Types L-S concretes used in loadbearing components shall conform to ASTM C330/C330M, “Standard Specification for Lightweight Aggregates for Structural Concrete.”

3)    Non-loadbearing low density components of vermiculite and perlite concrete, in the absence of other test evidence, shall be rated on the basis of the values shown for Type L concrete.

D-1.5. Gypsum Board

D-1.5.1. Types of Gypsum Board

1)    Where the term “gypsum board” is used in this Appendix, it is intended to include—in addition to gypsum board—gypsum backing board and gypsum base for veneer plaster as described in

a)    CAN/CSA A82.27-M, “Gypsum Board,” or

b)    ASTM C1396/C1396M, “Standard Specification for Gypsum Board.”

2)    Where the term “Type X gypsum board” is used in this Appendix, it applies to special fire-resistant board as described in

a)    CAN/CSA A82.27-M, “Gypsum Board,” or

b)    ASTM C1396/C1396M, “Standard Specification for Gypsum Board.”

D-1.6. Equivalent Thickness

D-1.6.1. Method of Calculating

1)    The thickness of solid-unit masonry and concrete described in this Appendix shall be the thickness of solid material in the unit or component thickness. For units that contain cores or voids, the Tables refer to the equivalent thickness determined in conformance with Sentences (2) to (10).

2)    Where a plaster finish is used, the equivalent thickness of a wall, floor, column or beam protection shall be equal to the sum of the equivalent thicknesses of the concrete or masonry units and the plaster finish measured at the point that will give the least value of equivalent thickness.

3)    Except as provided in Sentence (5), the equivalent thickness of a hollow masonry unit shall be calculated as equal to the actual overall thickness of a unit in millimetres multiplied by a factor equal to the net volume of the unit and divided by its gross volume.

4)    Net volume shall be determined using a volume displacement method that is not influenced by the porous nature of the units.

5)    Gross volume of a masonry unit shall be equal to the actual length of the unit multiplied by the actual height of the unit multiplied by the actual thickness of the unit.

6)    Where all the core spaces in a wall of hollow concrete masonry or hollow-core precast concrete units are filled with grout, mortar, or loose fill materials such as expanded slag, burned clay or shale (rotary kiln process), vermiculite or perlite, the equivalent thickness rating of the wall shall be considered to be the same as that of a wall of solid units, or a solid wall of the same concrete type and the same overall thickness.

7)    The equivalent thickness of hollow-core concrete slabs and panels having a uniform thickness and cores of constant cross section throughout their length shall be obtained by dividing the net cross-sectional area of the slab or panel by its width.

8)    The equivalent thickness of concrete panels with tapered cross sections shall be the cross section determined at a distance of 2 t or 150 mm, whichever is less, from the point of minimum thickness, where t is the minimum thickness.

9)    Except as permitted in Sentence (10), the equivalent thickness of concrete panels with ribbed or undulating surfaces shall be

a)    ta for s less than or equal to 2 t,

b)    t + (4 t/s - 1)(ta - t) for s less than 4 t and greater than 2 t, and

c)    t for s greater than or equal to 4 t

where

t   = minimum thickness of panel,

ta   = average thickness of panel (unit cross-sectional area divided by unit width), and

s   = centre to centre spacing of ribs or undulations.

10)    Where the total thickness of a panel described in Sentence (9), exceeds 2 t, only that portion of the panel which is less than 2 t from the non-ribbed surface shall be considered for the purpose of the calculations in Sentence (9).

D-1.7. Contribution of Plaster or Gypsum Board Finish to Fire Resistance of Masonry or Concrete

D-1.7.1. Determination of Contribution

1)    Except as provided in Sentences (2) to (5), the contribution of a plaster or gypsum board finish to the fire resistance of a masonry or concrete wall, floor or roof assembly shall be determined by multiplying the actual thickness of the finish by the factor shown in Table D-1.7.1., depending on the type of masonry or concrete to which it is applied. This corrected thickness shall then be included in the equivalent thickness as described in Subsection D-1.6.

Table D-1.7.1.

Multiplying Factors for Masonry or Concrete Construction

| Type of Surface Protection | Type of Masonry or Concrete |  |  |  |
| --- | --- | --- | --- | --- |
|  | Solid Clay Brick, Unit Masonry and Monolithic Concrete, Type N or S | Cored Clay Brick, Clay Tile, Monolithic Concrete, Type L40S and Unit Masonry, Type L120S | Concrete Unit Masonry, Type L1 or L220S and Monolithic Concrete, Type L | Concrete Unit Masonry, Type L2 |
| Portland cement-sand plaster or lime sand plaster | 1 | 0.75 | 0.75 | 0.50 |
| Gypsum-sand plaster, wood fibred gypsum plaster or gypsum board | 1.25 | 1 | 1 | 1 |
| Vermiculite or perlite aggregate plaster | 1.75 | 1.5 | 1.25 | 1.25 |

2)    Where a plaster or gypsum board finish is applied to a concrete or masonry wall, the calculated fire-resistance rating of the assembly shall not exceed twice the fire-resistance rating provided by the masonry or concrete because structural collapse may occur before the limiting temperature is reached on the surface of the non-fire-exposed side of the assembly.

3)    Where a plaster or gypsum board finish is applied only on the non-fire-exposed side of a hollow clay tile wall, no increase in fire resistance is permitted because structural collapse may occur before the limiting temperature is reached on the surface of the non-fire-exposed side of the assembly.

4)    The contribution to fire resistance of a plaster or gypsum board finish applied to the non-fire-exposed side of a monolithic concrete or unit masonry wall shall be determined in conformance with Sentence (1), but shall not exceed 0.5 times the contribution of the concrete or masonry wall.

5)    When applied to the fire-exposed side, the contribution of a gypsum lath and plaster or gypsum board finish to the fire resistance of masonry or concrete wall, floor or roof assemblies shall be determined from Table D-2.3.4.-A or D-2.3.4.-D.

D-1.7.2. Plaster

1)    Gypsum plastering shall conform to CSA A82.30-M, “Interior Furring, Lathing and Gypsum Plastering.”

2)    Portland cement-sand plaster shall be applied in 2 coats: the first coat containing 1 part Portland cement to 2 parts sand by volume, and the second coat containing 1 part Portland cement to 3 parts sand by volume.

3)    Plaster finish shall be securely bonded to the wall or ceiling.

4)    The thickness of plaster finish applied directly to monolithic concrete without metal lath shall not exceed 10 mm on ceilings and 16 mm on walls.

5)    Where the thickness of plaster finish on masonry or concrete exceeds 38 mm, wire mesh with 1.57 mm diam wire and openings not exceeding 50 mm by 50 mm shall be embedded midway in the plaster.

D-1.7.3. Attachment of Gypsum Board and Lath

Gypsum board and gypsum lath finishes applied to masonry or concrete walls shall be secured to wood or steel furring members in conformance with Article D-2.3.9.

D-1.7.4. Sample Calculations

The following examples are included as a guide to the method of calculating the fire resistance of concrete or hollow masonry walls with plaster or gypsum board protection:

Example (1)

A 3 h fire-resistance rating is required for a monolithic concrete wall of Type S aggregate with a 20 mm gypsum-sand plaster finish on metal lath on each face.

(a)   The minimum equivalent thickness of Type S monolithic concrete needed to give a 3 h fire-resistance rating = 158 mm (Table D-2.1.1.).

(b)   Since the gypsum-sand plaster finish is applied on metal lath, Sentence D-1.7.1.(5) does not apply. Therefore, the contribution to the equivalent thickness of the wall of 20 mm gypsum-sand plaster on each face of the concrete is 20 × 1.25 = 25 mm (see Sentences D-1.7.1.(1) to (4)).

(c)   The total contribution of the plaster finishes is 2 × 25 = 50 mm.

(d)   The minimum equivalent thickness of concrete required is 158 mm - 50 mm = 108 mm.

(e)   From Table D-2.1.1., the 108 mm equivalent thickness of monolithic concrete gives a contribution of less than 1.5 h. This is less than half the rating of the assembly so that the conditions in Sentence D-1.7.1.(2) are not met. Thus the equivalent thickness of monolithic concrete must be increased to 112 mm to give 1.5 h contribution.

(f)   The total equivalent thickness of the plaster finishes can then be reduced to 158 mm - 112 mm = 46 mm.

(g)   The total actual thickness of the plaster finishes required is therefore 46 mm ÷ 1.25 = 37 mm ( Sentences D-1.7.1.(1) to (4)) or 18.5 mm on each face.

(h)   Since the thickness of the plaster finish on each face exceeds 16 mm, metal lath is still required (Sentence D-1.7.2.(4)).

(i)   Since this wall is symmetrical with plaster on both faces, the contribution to fire resistance of the plaster finish on either face is limited to one-quarter of the wall rating by virtue of Sentence D-1.7.1.(2). Under these circumstances, the conditions in Sentence D-1.7.1.(4) are automatically met.

Example (2)

A 2 h fire-resistance rating is required for a hollow masonry wall of Type N concrete with a 12.7 mm Type X gypsum board finish on each face.

(a)   Since gypsum board is used, Sentence D-1.7.1.(5) applies. The 12.7 mm gypsum board finish on the fire-exposed side is, therefore, assigned 25 min by using Table D-2.3.4.-A.

(b)   The fire resistance required of the balance of the assembly is 120 min - 25 min = 95 min.

(c)   Interpolating between 1.5 h and 2 h in Table D-2.1.1. for 95 min fire resistance, the equivalent thickness for hollow masonry units required is 95 mm + ( 18 mm × 5/30) = 95 mm + 3 mm = 98 mm.

(d)   The contribution to the equivalent thickness of the wall of the 12.7 mm gypsum board finish on the non-fire-exposed side using Table D-1.7.1. = 12.7 × 1.25 = 16 mm.

(e)   Equivalent thickness required of concrete masonry unit = 98 - 16 = 82 mm.

(f)   The fire-resistance rating of a concrete masonry wall having an equivalent thickness of 82 mm = 1 h for 73 mm + (9 mm × 30/22) = 1 h 12 min.

As this is more than 1 h, the conditions of Sentence D-1.7.1.(2) are met and the rating of 2 h is justified.

Example (3)

A 2 h fire-resistance rating is required for a hollow masonry exterior wall of Type L220S concrete with a 15.9 mm Type X gypsum board finish on the non-fire-exposed side only.

(a)   According to Table D-2.1.1., the minimum equivalent thickness for Type L220S concrete masonry units needed to achieve a 2 h rating is 94 mm.

(b)   Since gypsum board is not used on the fire-exposed side, Sentence D-1.7.1.(5) does not apply. The contribution to the equivalent thickness of the wall by the 15.9 mm Type X gypsum board finish applied on the non-fire-exposed side is 15.9 × 1 ≈ 16 mm (see Sentence D-1.7.1.(1) and Table D-1.7.1.).

(c)   Therefore, the equivalent thickness required of the concrete masonry unit is 94 - 16 = 78 mm.

(d)   The contribution to fire resistance of a 78 mm L 220S concrete hollow masonry unit is 85 min. The contribution of the Type X gypsum board finish is 120 - 85 = 35 min, which does not exceed half the 85 min contribution of the masonry unit or 42.5 min, so that the conditions in Sentence D-1.7.1.(4) are met.

(e)   The rating of the wall (120 min) is less than twice the contribution of the masonry unit (170 min) so that the conditions in Sentence D-1.7.1.(2) are also met.

D-1.8. Tests on Floors and Roofs

D-1.8.1. Exposure to Fire

All tests relate to the performance of a floor assembly or floor-ceiling or roof-ceiling assembly above a fire. It has been assumed on the basis of experience that fire on top will take a longer time to penetrate the floor than one below, and that the fire resistance in such a situation will be at least equal to that obtained from below in the standard test.

D-1.9. Moisture Content

D-1.9.1. Effect of Moisture

1)    The moisture content of building materials at the time of fire test may have a significant influence on the measured fire resistance. In general, an increase in the moisture content should result in an increase in the fire resistance, though in some materials the presence of moisture may produce disruptive effects and early collapse of the assembly.

2)    Moisture content is now controlled in standard fire test methods and is generally recorded in the test reports. In earlier tests, moisture content was not always properly determined.

D-1.10. Permanence and Durability

D-1.10.1. Test Conditions

The ratings in this Appendix relate to tested assemblies and do not take into account possible changes or deterioration in use of the materials. The standard fire test measures the fire resistance of a sample building assembly erected for the test. No judgment as to the permanence or durability of the assembly is made in the test.

D-1.11. Steel Structural Members

D-1.11.1. Thermal Protection

Since the ability of a steel structural member to sustain the loading for which it was designed may be impaired because of elevated temperatures, measures shall be taken to provide thermal protection. The fire-resistance ratings, as established by the provisions of this Appendix, indicate the time periods during which the effects of heat on protected steel structural members are considered to be within acceptable limits.

D-1.12. Restraint Effects

D-1.12.1. Effect on Fire-Resistance Ratings

In fire tests of floors, roofs and beams, it is necessary to state whether the rating applies to a thermally restrained or thermally unrestrained assembly. Edge restraint of a floor or roof, structural continuity, or end restraint of a beam can significantly extend the time before collapse in a standard test. A restrained condition is one in which expansion or rotation at the supports of a load-carrying element resulting from the effects of fire is resisted by forces or moments external to the element. An unrestrained condition is one in which the load-carrying element is free to thermally expand and rotate at its supports.

Whether an assembly or structural member can be considered thermally restrained or thermally unrestrained depends on the type of construction and location in a building. Guidance on this subject can be found in Appendix A of CAN/ULC-S101, “Standard Method of Fire Endurance Tests of Building Construction and Materials.” Different acceptance criteria also apply to thermally unrestrained and thermally restrained assemblies. These are described in CAN/ULC-S101.

The ratings for floors, roofs, and beams in this Appendix meet the conditions of CAN/ULC-S101, “Standard Method of Fire Endurance Tests of Building Construction and Materials,” for thermally unrestrained specimens. In a thermally restrained condition, the structural element or assembly would probably have greater fire resistance, but the extent of this increase can be determined only by reference to behavior in a standard test.

Section  D-2  Fire-Resistance Ratings

D-2.1. Masonry and Concrete Walls

D-2.1.1. Minimum Equivalent Thickness for Fire-Resistance Rating

The minimum thicknesses of unit masonry and monolithic concrete walls are shown in Table D-2.1.1. Hollow masonry units and hollow-core concrete panels shall be rated on the basis of equivalent thickness as described in Subsection D-1.6.

Table D-2.1.1.

Minimum Equivalent Thicknesses(1) of Unit Masonry and Monolithic Concrete Walls Loadbearing and Non-Loadbearing, mm

| Type of Wall | Fire-Resistance Rating |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | 30 min | 45 min | 1 h | 1.5 h | 2 h | 3 h | 4 h |
| Solid brick units (80% solid and over), actual overall thickness | 63 | 76 | 90 | 108 | 128 | 152 | 178 |
| Cored brick units and hollow tile units (less than 80% solid), equivalent thickness | 50 | 60 | 72 | 86 | 102 | 122 | 142 |
| Solid and hollow concrete masonry units, equivalent thickness |  |  |  |  |  |  |  |
| Type S or N concrete(2) | 44 | 59 | 73 | 95 | 113 | 142 | 167 |
| Type L120S concrete | 42 | 54 | 66 | 87 | 102 | 129 | 152 |
| Type L1 concrete | 42 | 54 | 64 | 82 | 97 | 122 | 143 |
| Type L220S concrete | 42 | 54 | 64 | 81 | 94 | 116 | 134 |
| Type L2 concrete | 42 | 54 | 63 | 79 | 91 | 111 | 127 |
| Monolithic concrete and concrete panels, equivalent thickness |  |  |  |  |  |  |  |
| Type S concrete | 60 | 77 | 90 | 112 | 130 | 158 | 180 |
| Type N concrete | 59 | 74 | 87 | 108 | 124 | 150 | 171 |
| Type L40S or Type L concrete | 49 | 62 | 72 | 89 | 103 | 124 | 140 |

Notes to Table D-2.1.1.:

(1) See definition of equivalent thickness in Subsection D-1.6.

(2) Hollow concrete masonry units made with Type S or N concrete shall have a minimum compressive strength of 15 MPa based on net area, as defined in CSA A165.1, “Concrete block masonry units.”

D-2.1.2. Applicability of Ratings

1)    Ratings obtained as described in Article D-2.1.1. apply to either loadbearing or non-loadbearing walls, except for walls described in Sentences (2) to (6).

2)    Ratings for walls with a thickness less than the minimum thickness prescribed for loadbearing walls in this Code apply to non-loadbearing walls only.

3)    Masonry cavity walls (consisting of 2 wythes of masonry with an air space between) that are loaded to a maximum allowable compressive stress of 380 kPa have a fire resistance at least as great as that of a solid wall of a thickness equal to the sum of the equivalent thicknesses of the 2 wythes.

4)    Masonry cavity walls that are loaded to a compressive stress exceeding 380 kPa are not considered to be within the scope of this Appendix.

5)    A masonry wall consisting of 2 types of masonry units, either bonded together or in the form of a cavity wall, shall be considered to have a fire-resistance rating equal to that which would apply if the whole of the wall were of the material that gives the lesser rating.

6)    A non-loadbearing cavity wall made up of 2 precast concrete panels with an air space or insulation in the cavity between them shall be considered to have a fire-resistance rating as great as that of a solid wall of a thickness equal to the sum of the thicknesses of the 2 panels.

D-2.1.3. Framed Beams and Joists

Beams and joists that are framed into a masonry or concrete fire separation shall not reduce the thickness of the fire separation to less than the equivalent thickness required for the fire separation.

D-2.1.4. Credit for Plaster Thickness

On monolithic walls and walls of unit masonry, the full plaster finish on one or both faces multiplied by the factor shown in Table D-1.7.1. shall be included in the wall thickness shown in Table D-2.1.1., under the conditions and using the methods described in Subsection D-1.7.

D-2.1.5. Walls Exposed to Fire on Both Sides

1)    Except as permitted in Sentence (2), portions of loadbearing reinforced concrete walls, which do not form a complete fire separation and thus may be exposed to fire on both sides simultaneously, shall have minimum dimensions and minimum cover to steel reinforcement in conformance with Articles D-2.8.2. to D-2.8.5.

2)    A concrete wall exposed to fire from both sides as described in Sentence (1) has a fire-resistance rating of 2 h if the following conditions are met:

a)    its equivalent thickness is not less than 200 mm,

b)    its aspect ratio (width/thickness) is not less than 4.0,

c)    the minimum thickness of concrete cover over the steel reinforcement specified in Clause (d) is not less than 50 mm,

d)    each face of the wall is reinforced with both vertical and horizontal steel reinforcement in conformance with either Clause 10 or Clause 14 of CSA A23.3, “Design of concrete structures,”

e)    the structural design of the wall is governed by the minimum eccentricity (15 + 0.03h) specified in Clause 10.15.3.1 of CSA A23.3, “Design of concrete structures,” and

f)    the effective length of the wall, klu, is not more than 3.7 m

where

k   = effective length factor obtained from CSA A23.3, “Design of concrete structures,”

lu   = unsupported length of the wall in metres.

D-2.2. Reinforced and Prestressed Concrete Floor and Roof Slabs

D-2.2.1. Assignment of Rating

1)    Floors and roofs in a fire test are assigned a fire-resistance rating which relates to the time that an average temperature rise of 140°C or a maximum temperature rise of 180 °C at any location is recorded on the unexposed side, or the time required for collapse to occur, whichever is the lesser. The thickness of concrete shown in Table D-2.2.1.-A shall be required to resist the transfer of heat during the fire resistance period shown.

Table D-2.2.1.-A

Minimum Thickness of Reinforced and Prestressed Concrete Floor or Roof Slabs, mm

| Type of Concrete | Fire-Resistance Rating |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | 30 min | 45 min | 1 h | 1.5 h | 2 h | 3 h | 4 h |
| Type S concrete | 60 | 77 | 90 | 112 | 130 | 158 | 180 |
| Type N concrete | 59 | 74 | 87 | 108 | 124 | 150 | 171 |
| Type L40S or Type L concrete | 49 | 62 | 72 | 89 | 103 | 124 | 140 |

2)    The concrete cover over the reinforcement and steel tendons shown in Table D-2.2.1.-B shall be required to maintain the integrity of the structure and prevent collapse during the same period.

Table D-2.2.1.-B

Minimum Concrete Cover over Reinforcement in Concrete Slabs, mm

| Type of Concrete | Fire-Resistance Rating |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | 30 min | 45 min | 1 h | 1.5 h | 2 h | 3 h | 4 h |
| Type S, N, L40S or L concrete | 20 | 20 | 20 | 20 | 25 | 32 | 39 |
| Prestressed concrete slabs Type S, N, L40S or L concrete | 20 | 25 | 25 | 32 | 39 | 50 | 64 |

D-2.2.2. Floors with Hollow Units

The fire resistance of floors containing hollow units may be determined on the basis of equivalent thickness as described in Subsection D-1.6.

D-2.2.3. Composite Slabs

1)    For composite concrete floor and roof slabs consisting of one layer of Type S or N concrete and another layer of Type L40S or L concrete in which the minimum thickness of both the top and bottom layers is not less than 25 mm, the combined fire-resistance rating may be determined using the following expressions:

a)    when the base layer consists of Type S or N concrete,

b)    when the base layer consists of Type L40S or L concrete,

where

R   = fire resistance of slab, h,

t   = total thickness of slab, mm, and

d   = thickness of base layer, mm.

2)    If the base course described in Sentence (1) is covered by a top layer of material other than Type S, N, L40S or L concrete, the top course thickness may be converted to an equivalent concrete thickness by multiplying the actual thickness by the appropriate factor listed in Table D-2.2.3.-A This equivalent concrete thickness may be added to the thickness of the base course and the fire-resistance rating calculated using Table D-2.2.1.-A.

3)    The minimum concrete cover under the main reinforcement for composite concrete floor and roof slabs with base slabs less than 100 mm thick shall conform to Table D-2.2.3.-B For base slabs 100 mm or more thick, the minimum cover thickness requirements of Table D-2.2.1.-B shall apply.

4)    Where the top layer of a 2-layer slab is less than 25 mm thick, the fire-resistance rating for the slab shall be calculated as though the entire slab were made up of the type of concrete with the lesser fire resistance.

Table D-2.2.3.-A

Multiplying Factors for Equivalent Thickness

| Top Course Material | Base Slab Normal Density Concrete (Type S or N) | Base Slab Low Density Concrete (Type L40S or L) |
| --- | --- | --- |
| Gypsum board | 3 | 2.25 |
| Cellular concrete (mass density 400 – 560 kg/m3 ) | 2 | 1.50 |
| Vermiculite and perlite concrete (mass density 560 kg/m3 or less) | 1.75 | 1.50 |
| Portland cement with sand aggregate | 1 | 0.75 |
| Terrazzo | 1 | 0.75 |

Table D-2.2.3.-B

Minimum Concrete Cover under Bottom Reinforcement in Composite Concrete Slabs, mm

| Base Slab Concrete Type | Fire-Resistance Rating |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | 30 min | 45 min | 1 h | 1.5 h | 2 h | 3 h | 4 h |
| Reinforced concrete |  |  |  |  |  |  |  |
| Type S, N, L40S or L | 15 | 15 | 20 | 25 | 30 | 40 | 55 |
| Prestressed concrete |  |  |  |  |  |  |  |
| Type S | 20 | 25 | 30 | 40 | 50 | 65 | 75 |
| Type N | 20 | 20 | 25 | 35 | 45 | 60 | 70 |
| Type L40S or L | 20 | 20 | 25 | 30 | 40 | 50 | 60 |

D-2.2.4. Contribution of Plaster Finish

1)    The contribution of plaster finish securely fastened to the underside of concrete may be taken into account in floor or roof slabs under the conditions and using the methods described in Subsection D-1.7.

2)    Plaster finish on the underside of concrete floors or roofs may be used in lieu of concrete cover referred to in Sentence D-2.2.1.(2) under the conditions and using the methods described in Subsection D-1.7.

D-2.2.5. Concrete Cover

1)    In prestressed concrete slab construction, the concrete cover over an individual tendon shall be the minimum thickness of concrete between the surface of the tendon and the fire-exposed surface of the slab, except that for ungrouted ducts the assumed cover thickness shall be the minimum thickness of concrete between the surface of the duct and the bottom of the slab. For slabs in which several tendons are used, the cover is assumed to be the average of those of individual tendons, except that the cover for any individual tendon shall be not less than half of the value given in Table D-2.2.1.-B nor less than 20 mm.

2)    Except as provided in Sentence (3), in post-tensioned prestressed concrete slabs, the concrete cover to the tendon at the anchor shall be not less than 15 mm greater than the minimum cover required by Sentence (1). The minimum concrete cover to the anchorage bearing plate and to the end of the tendon, if it projects beyond the bearing plate, shall be 20 mm.

3)    The requirements of Sentence (2) do not apply to those portions of slabs not likely to be exposed to fire, such as the ends and tops.

D-2.2.6. Minimum Dimensions for Cover

Minimum dimensions and cover to steel tendons of prestressed concrete beams shall conform to Subsection D-2.10.

D-2.3. Wood and Steel Framed Walls, Floors and Roofs

D-2.3.1. Maximum Fire-Resistance Rating

The fire-resistance rating of walls constructed of wood studs or cold-formed-steel studs, of floors constructed of wood joists, wood I-joists, pre-manufactured wood trusses, cold-formed steel joists or open web steel joists, and of roofs constructed of wood joists, pre-manufactured metal-plate-connected wood trusses or open web steel joists can be determined for ratings of not more than 90 min from the information in this Subsection.

D-2.3.2. Loadbearing Conditions

1)    The fire-resistance ratings derived from the information in this Subsection apply to loadbearing and non-loadbearing wood-framed and cold-formed-steel-framed walls, and to loadbearing floors and roofs, as specifically described in this Subsection.

2)    Loadbearing conditions shall be as defined in CAN/ULC-S101, “Standard Method of Fire Endurance Tests of Building Construction and Materials.”

D-2.3.3. Limitations of Component Additive Method

(See Section D-7, Background Information.)

1)    The fire-resistance rating of a framed assembly depends primarily on the time during which the membrane on the fire-exposed side remains in place.

2)    The assigned times in Sentences D-2.3.4.(2) to (4) are not intended to be construed as the fire-resistance ratings of the individual components of an assembly, nor are they intended to be construed as times that are applicable or acceptable for use beyond the method and systems described in this Subsection. These assigned times are the individual contributions of each component to the overall fire-resistance rating of an assembly, which is permitted to be derived using the component additive method described in this Subsection.

3)    The fire-resistance rating calculated by the component additive method cannot be increased by installing membranes in multiple layers, other than as specified in Tables D-2.3.4.-A, D-2.3.4.-B and D-2.3.4.-C.

D-2.3.4. Method of Calculation

1)    In the component additive method, the fire-resistance rating of a framed assembly is calculated by adding the time assigned in Sentence (2) for the membrane on the fire-exposed side to the time assigned in Sentence (3) for the framing members and then adding any time assigned in Sentence (4) for additional protective measures, such as the inclusion of insulation or of reinforcement for a membrane. For loadbearing walls where resilient metal channels are installed with a single layer of gypsum board membrane in accordance with Table D-2.3.4.-A, the fire-resistance rating determined using this method of calculation must be reduced by 10 min.

2)    The times to be used in the component additive method that have been assigned to membranes on the fire-exposed side of the assembly, which are partly based on their ability to remain in place during fire tests, are listed in Tables D-2.3.4.-A to D-2.3.4.-D. (This is not to be confused with the fire-resistance rating of the membrane, which also takes into account the rise in temperature on the unexposed side of the membrane. [See Sentence D-2.3.3.(2).])

Table D-2.3.4.-A

Time Assigned to Protective Membranes on Fire-Exposed Side of Wood-Framed and Cold-Formed-Steel-Framed Walls

| Description of Finish | Time, min |  |
| --- | --- | --- |
|  | Loadbearing Walls | Non-Loadbearing Walls |
| 11.0 mm Douglas Fir plywood phenolic bonded | – | 10(1) |
| 14.0 mm Douglas Fir plywood phenolic bonded | – | 15(1) |
| 12.7 mm Type X gypsum board | 25(2) | 25 |
| 15.9 mm Type X gypsum board | 40(2) | 40(3) |
| Double 12.7 mm Type X gypsum board(4) | 50 | 80 |

Notes to Table D-2.3.4.-A:

(1) Applies to stud cavities filled with mineral wool conforming to CAN/ULC-S702.1, “Standard for Mineral Fibre Thermal Insulation for Buildings, Part 1: Material Specification,” and having a mass per unit area of not less than 2 kg/m2, with no additional credit for insulation according to Table D-2.3.4.-G.

(2) Applies only to wood-framed walls.

(3) Applies only to steel-framed walls.

(4) Resilient metal channels are permitted to be installed at a spacing of 400 mm o.c. with no effect on the rating of the wall assembly.

Table D-2.3.4.-B

Time Assigned to Gypsum Board Membranes on Fire-Exposed Side of Floors

| Description of Finish | Resilient Metal Channels(1) | Time, min |  |
| --- | --- | --- | --- |
|  |  | Floors with Wood or Steel Joists | Floors with Open-Web Steel Joists |
| 12.7 mm Type X gypsum board | Spaced ≤ 400 mm o.c.(2) | 25(3) | — |
| 15.9 mm Type X gypsum board |  | 40 | — |
| 12.7 mm Type X gypsum board | — | 25(4) | 25 |
| 15.9 mm Type X gypsum board |  | 40(4) | 40 |
| Double 12.7 mm Type X gypsum board | Spaced ≤ 400 mm o.c.(5) | 50(3) | — |
| Double 12.7 mm Type X gypsum board | Spaced at 600 mm o.c.(6) | 45(3) | — |
| Double 15.9 mm Type X gypsum board | Spaced ≤ 600 mm o.c.(6) | 60(3) | — |

Notes to Table D-2.3.4.-B:

(1) See Figures A-9.10.3.1.-A, A-9.10.3.1.-B and A-9.10.3.1.-D in Note A-9.10.3.1. for the attachment of single and double layers of gypsum board to resilient metal channels.

(2) Resilient metal channels must be installed to achieve the stated rating.

(3) Applies to wood joists, wood trusses, wood I-joists and cold-formed steel joists (C-shaped joists).

(4) Applies to wood joists and pre-fabricated metal-plate-connected wood trusses.

(5) Resilient metal channels must be installed or gypsum board must be applied directly to the structural members, which must be spaced not more than 400 mm o.c.

(6) Resilient metal channels are permitted to be installed with no effect on the rating of the floor assembly. Gypsum board is also permitted to be directly applied to the structural members.

Table D-2.3.4.-C

Time Assigned to Gypsum Board Membranes on Fire-Exposed Side of Roofs

| Description of Finish | Time, min(1) |
| --- | --- |
| 12.7 mm Type X gypsum board | 25 |
| 15.9 mm Type X gypsum board | 40 |

Notes to Table D-2.3.4.-C:

(1) Applies to wood joists, pre-fabricated metal-plate-connected wood trusses, and open-web steel joists with ceiling supports spaced ≤ 400 mm o.c.

Table D-2.3.4.-D

Time Assigned for Contribution of Lath and Plaster Protection on Fire-Exposed Side

| Type of Lath | Plaster Thickness, mm | Type of Plaster Finish |  |  |
| --- | --- | --- | --- | --- |
|  |  | Portland Cement and Sand(1) or Lime and Sand | Gypsum and Sand or Gypsum Wood Fibre | Gypsum and Perlite or Gypsum and Vermiculite |
|  |  | Time, min(2) |  |  |
| 9.5 mm gypsum | 13 | — | 35 | 55 |
|  | 16 | — | 40 | 65 |
|  | 19 | — | 50 | 80(3) |
| Metal | 19 | 20 | 50 | 80(3) |
|  | 23 | 25 | 65 | 80(3) |
|  | 26 | 30 | 80 | 80(3) |

Notes to Table D-2.3.4.-D:

(1) For mixture of Portland cement-sand plaster, see Sentence D-1.7.2.(2).

(2) Applies to loadbearing and non-loadbearing wood studs or non-loadbearing cold-formed-steel studs, to floors constructed of wood joists or open-web steel joists, and to roofs constructed of wood joists, pre-manufactured metal-plate-connected wood trusses, or open-web steel joists.

(3) Values shown for these membranes have been limited to 80 min because the fire-resistance ratings of framed assemblies derived from these Tables must not exceed 1.5 h.

3)    The times to be used in the component additive method that have been assigned to wall framing members and to floor and roof framing members are listed in Tables D-2.3.4.-E and D-2.3.4.-F respectively.

Table D-2.3.4.-E

Time Assigned for Contribution of Wood-Framed or Cold-Formed-Steel-Framed Walls

| Description of Frame | Time, min |  |
| --- | --- | --- |
|  | Loadbearing Walls | Non-Loadbearing Walls |
| Wood studs spaced ≤ 400 mm o.c. | 20 |  |
| Wood studs spaced ≤ 600 mm o.c. | 15 |  |
| Cold-formed-steel studs spaced ≤ 400 mm o.c. | 10 |  |
| Cold-formed-steel studs spaced ≤ 600 mm o.c. | 10 | – |

Table D-2.3.4.-F

Time Assigned for Contribution of Wood or Steel Frame of Floors and Roofs

| Description of Frame |  | Time, min |
| --- | --- | --- |
| Type of Assembly | Structural Members |  |
| Floor(1) | Wood joists, wood I-joists, wood trusses and cold-formed-steel joists spaced ≤ 600 mm o.c. | 10(2) |
|  | Open-web steel joists with ceiling supports spaced ≤ 400 mm o.c. |  |
| Roof | Wood joists spaced ≤ 400 mm o.c. | 10 |
|  | Open-web steel joists with ceiling supports spaced ≤ 400 mm o.c. | 10 |
|  | Wood truss assemblies [metal-plate-connected] spaced ≤ 600 mm o.c. | 5 |

Notes to Table D-2.3.4.-F:

(1) Resilient metal channels are permitted to be installed with no effect on the rating of the floor assembly.

(2) Applies only to floor structural members that are protected by a membrane.

4)    Preformed insulation of glass, rock or slag fibre and cellulose fibre insulation provide additional protection to wood studs by shielding the studs from exposure to the fire and thus delaying the time of collapse. The use of preformed glass fibre, preformed rock or slag fibre and dry-blown cellulose insulation material does not decrease the rating of wall assemblies with the membranes identified in Table D-2.3.4.-A. Similarly, the use of preformed glass fibre, preformed rock or slag fibre and cellulose insulation material does not decrease the rating of floor assemblies constructed with wood joists, wood trusses, wood I-joists and cold-formed-steel floor joists (C-shaped joists), provided the insulation is not in direct contact with the membranes identified in Table D-2.3.4.-B. The use of reinforcement in the membrane exposed to fire also adds to the fire resistance by extending the time to failure. Table D-2.3.4.-G shows the time increments that may be added to the fire resistance if these features are incorporated in the assembly.

Table D-2.3.4.-G

Time Assigned for Additional Protection

| Description of Additional Protection | Time, min |
| --- | --- |
| Add to the fire-resistance rating of wood stud walls, sheathed with gypsum board or lath and plaster, if the spaces between the studs are filled with preformed insulation of rock or slag fibres conforming to CAN/ULC-S702.1, “Standard for Mineral Fibre Thermal Insulation for Buildings, Part 1: Material Specification,” and with a mass per unit area of not less than 1.22 kg/m2 of wall surface | 15(1) |
| Add to the fire-resistance rating of non-loadbearing wood stud walls, sheathed with gypsum board or lath and plaster, if the spaces between the studs are filled with preformed insulation of glass fibres conforming to CAN/ULC-S702.1, “Standard for Mineral Fibre Thermal Insulation for Buildings, Part 1: Material Specification,” and having a mass per unit area of not less than 0.6 kg/m 2 of wall surface | 5(2) |
| Add to the fire-resistance rating of loadbearing wood stud walls sheathed with gypsum board if the spaces between the studs are filled with insulation of cellulose fibres conforming to CAN/ULC-S703, “Standard for Cellulose Fibre Insulation (CFI) for Buildings,” and having a density of not less than 50 kg/m3 | 10 |
| Add to the fire-resistance rating of plaster on gypsum lath ceilings if 0.76 mm diam wire mesh with 25 mm by 25 mm openings or 1.57 mm diam diagonal wire reinforcing at 250 mm o.c. is placed between lath and plaster | 30 |
| Add to the fire-resistance rating of plaster on gypsum lath ceilings if 76 mm wide metal lath strips are placed over joints between lath and plaster | 10 |
| Add to the fire-resistance rating of plaster on 9.5 mm thick gypsum lath ceilings (Table D-2.3.4.-D) if supports for lath are 300 mm o.c. | 10 |
| Add to the fire-resistance rating of floor assemblies if the spaces between the structural members are filled with preformed insulation of rock or slag fibres conforming to CAN/ULC-S702.1, “Standard for Mineral Fibre Thermal Insulation for Buildings, Part 1: Material Specification,” and having a mass per unit area of not less than 1.22 kg/m2 of floor surface | 5(2) |
| Add to the fire-resistance rating of floor assemblies if the spaces between the structural members are filled with wet-blown cellulose fibres conforming to CAN/ULC-S703, “Standard for Cellulose Fibre Insulation (CFI) for Buildings,” and having a density of not less than 50 kg/m3 | 5(2)(3) |
| Add to the fire-resistance rating of floor assemblies where the floor topping on the unexposed side of the floor assemblies consists of concrete not less than 38 mm thick | 5(2) |

Notes to Table D-2.3.4.-G:

(1) Applies to wood-framed walls only.

(2) Applies to wood joists, wood trusses, wood I-joists and cold-formed-steel joists (C-shaped joists).

(3) Applies to cellulose fibre:

(i)   for wood joists, wood I-joist and wood trusses–that is spray-applied with a minimum density of 50 kg/m3, a minimum depth of 90 mm on the underside of the subfloor, and of 90 mm on the sides of the structural members;

(ii)   for cold-formed-steel joists–that is spray-applied with a minimum density of 50 kg/m3 and a minimum thickness of 90 mm on the underside of the subfloor, of 90 mm on the sides of the structural members, and of 13 mm on the underside of the bottom flange other than at resilient metal channel locations.

5)    Cellulose fibre insulation conforming to CAN/ULC-S703, “Standard for Cellulose Fibre Insulation (CFI) for Buildings,” applied in conformance with CAN/CGSB-92.2-M, “Trowel or Spray Applied Acoustical Material,” does not affect the fire-resistance rating of a non-loadbearing cold-formed-steel stud wall assembly, provided that it is sprayed to either face of the wall cavity.

D-2.3.5. Considerations for Various Types of Assemblies

1)    Interior vertical fire separations are to be rated for exposure to fire on each side (see Sentence 3.1.7.3.(2)). The method described in this Subsection applies when a membrane is provided on both sides of the assembly. However, in the calculation of the fire-resistance rating of such an assembly using this method, no additional contribution to fire resistance is to be assigned for a membrane on the non-fire-exposed side, since its contribution is already accounted for in the values assigned to the other components of the assembly.

2)    Exterior wall assemblies required to have a fire-resistance rating are required to be rated for exposure to fire from the interior side only (see Sentence 3.1.7.3.(3)). When deriving a fire-resistance rating for such wall assemblies using the method described in this Subsection, only wood studs with a single layer of gypsum board or non-loadbearing cold-formed-steel studs conforming to Table D-2.3.4.-E may be used. Such walls must have a membrane on the exterior side of the stud consisting of plywood, oriented strandboard or gypsum sheathing, and exterior cladding. Additional materials are also permitted between the required sheathing and cladding. The spaces between the studs are to be filled with insulation conforming to CAN/ULC-S702.1, “Standard for Mineral Fibre Thermal Insulation for Buildings, Part 1: Material Specification,” and having a mass per unit area of not less than 1.22 kg/m2 of wall surface. However, in the calculation of the fire-resistance rating of such an assembly, no additional contribution to fire resistance is to be assigned for a membrane on the non-fire-exposed side, since its contribution is already accounted for in the values assigned to the other components of the assembly.

3)    In the case of a floor or roof assembly, the Code only requires testing for fire exposure from below. Floors or roofs must have an upper flooring or roofing membrane in accordance with Table D-2.3.5.

Table D-2.3.5.

Flooring or Roofing Membranes

| Type of Assembly | Structural Members | Subfloor or Roof Deck | Finished Flooring or Roofing |
| --- | --- | --- | --- |
| Floor | Wood or open-web steel joists(1) and metal-plate-connected wood trusses(1) | 12.5 mm plywood or 15.5 mm oriented strandboard or 17 mm T & G softwood or 14 mm phenolic-bonded Douglas Fir plywood (no finished flooring required) | Hardwood or softwood flooring on building paper Resilient flooring, parquet floor, felted synthetic fibre floor coverings, carpeting, or ceramic tile on 8 mm thick panel-type underlay Ceramic tile on 30 mm mortar bed |
|  | Open-web steel joists(1) | 50 mm reinforced concrete or 50 mm concrete on metal lath or formed steel sheet or 40 mm reinforced gypsum-fibre concrete on 12.7 mm gypsum board | Finish flooring |
|  | Wood joists, wood I-joists, wood trusses and cold-formed-steel joists | minimum 15.5 mm T & G plywood or minimum 15.5 mm oriented strandboard | No requirement |
| Roof | Wood or open-web steel joists(1) and wood trusses(1) | 12.5 mm plywood or 15.5 mm oriented strandboard or 17 mm T & G softwood or 14 mm phenolic-bonded Douglas Fir plywood (no finished flooring required) | Finish roofing material with or without insulation |
|  | Open-web steel joists(1) | 50 mm reinforced concrete or 50 mm concrete on metal lath or formed steel sheet or 40 mm reinforced gypsum-fibre concrete on 12.7 mm gypsum board | Finish roofing material with or without insulation |

Notes to Table D-2.3.5.:

(1) Applies to single layer of gypsum board membrane, and lath and plaster.

4)    Insulation used in the cavities of a wood joist or metal-plate-connected wood truss floor assembly with a single layer of gypsum board will not reduce the assigned fire-resistance rating of the assembly, provided:

a)     the insulation is preformed of rock, slag or glass fibre conforming to CAN/ULC-S702.1, “Standard for Mineral Fibre Thermal Insulation for Buildings, Part 1: Material Specification,” and having a mass per unit area of not more than 1.1 kg/m2 and is installed adjacent to the bottom edge of the framing member, directly above steel furring channels,

b)    the gypsum board ceiling membrane is attached to

i)   wood trusses in conformance with Sentence D-2.3.9.(2) by way of steel furring channels spaced not more than 400 mm o.c., and the channels are secured to each bottom truss member with a double strand of 1.2 mm galvanized steel wire, or

ii)   wood joists by way of resilient metal or steel furring channels spaced not more than 400 mm o.c. in conformance with Sentences D-2.3.9.(2) and (3), and

c)    a steel furring channel is installed midway between each furring channel mentioned in Clause (b) to provide additional support for the insulation.

5)    Except as required in Sentence D-2.3.5.(4), resilient metal or steel furring channels may be used to attach a gypsum board ceiling membrane to a floor assembly using wood joists, metal-plate-connected wood trusses and open-web steel joists, or to a roof assembly. The channels must be made of galvanized steel not less than 0.5 mm thick spaced not more than 600 mm o.c. perpendicular to the framing members, with an overlap of not less than 100 mm at splices and a minimum end clearance between the channels and walls of 15 mm.

D-2.3.6. Framing Members

1)    The values shown in Tables D-2.3.4.-A, D-2.3.4.-B, D-2.3.4.-D and D-2.3.12. apply to membranes supported on framing members installed in their conventional orientation and spaced in conformance with Tables D-2.3.4.-E and D-2.3.4.-F.

2)    Wood studs and wood roof framing members are to be not less than 38 mm by 89 mm. Wood floor joists are to be not less than 38 mm by 184 mm, except where they are used in an assembly from Table D-2.3.4.-D or from Table D-2.3.5. that uses a single layer of gypsum board as the lower (ceiling) membrane, in which case, wood floor joists are to be not less than 38 mm by 89 mm.

3)    Wood roof trusses are to consist of wood chord and web framing members not less than 38 mm by 89 mm and metal connector plates fabricated from galvanized steel not less than 1 mm in nominal thickness with projecting teeth not less than 8 mm long.

4)    Wood floor trusses are to consist of:

a)    metal-plate-connected wood trusses that are not less than 305 mm deep with wood chord and web framing members not less than 38 mm by 64 mm and metal connector plates fabricated from galvanized steel not less than 1 mm in nominal thickness with projecting teeth not less than 8 mm long;

b)     metal-web wood trusses that are not less than 286 mm deep with wood chords not less than 38 mm by 64 mm and V-shaped webs made from galvanized steel not less than 1 mm in nominal thickness with plate areas having teeth not less than 8 mm long; or

c)     fingerjoined wood trusses that are not less than 330 mm deep with fingerjoined connections, chord members not less than 38 mm by 64 mm, and web members not less than 38 mm by 38 mm glued together with a R-14 phenol-resorcinol resin conforming to CSA O112.10, “Evaluation of Adhesives for Structural Wood Products (Limited Moisture Exposure).”

5)    Wood I-joists are to be not less than 241 mm deep with flanges that are not less than 38 mm by 38 mm and an oriented strandboard or plywood web that is not less than 9.5 mm thick.

6)    The dimensions for dressed lumber given in CSA O141, “Softwood Lumber,” are to be used for wood studs, joists, I-joists and trusses.

7)    Cold-formed-steel studs for non-loadbearing walls are to consist of galvanized steel that is not less than 0.5 mm thick and not less than 63 mm wide, and have a flange that is not less than 31 mm wide.

8)    Cold-formed-steel studs in non-loadbearing wall assemblies are to be installed with not less than a 12 mm clearance between the top of the stud and the top of the runner to allow for expansion in the event of a fire. Where the studs are required to be attached for alignment purposes during erection, they must be attached to the bottom runners only.

9)    Cold-formed-steel studs for loadbearing walls are to consist of galvanized steel that is not less than 0.912 mm thick but not greater than 1.52 mm thick, with a C-shaped cross-section not less than 92 mm deep by 41 mm wide and 12.7 mm stiffening lips.

10)    Cold-formed-steel studs in loadbearing wall assemblies are to be installed with diagonal cross-bracing.

11)    Cold-formed-steel floor joists (C-shaped joists) are to be not less than 41 mm wide by 203 mm deep by 1.22 mm material thickness.

12)    The allowable spans for wood joists listed in the Span Tables in Part 9 are provided for floors supporting specific occupancies.

D-2.3.7. Plaster Finish

The thickness of plaster finish shall be measured from the face of gypsum or metal lath.

D-2.3.8. Edge Support for Gypsum Board in Wall Assembly

Gypsum board installed over framing or furring in a wall assembly shall be installed so that all edges are supported, except that 15.9 mm Type X gypsum board may be installed horizontally with the horizontal joints unsupported when framing members are at 400 mm o.c. maximum.

D-2.3.9. Membrane Fastening

1)    Except as provided in Sentences (2) to (5), Table D-2.3.4.-B and Sentence D-2.3.5.(5), the application of lath and plaster finish shall conform to CSA A82.30-M, “Interior Furring, Lathing and Gypsum Plastering,” and of gypsum board finish shall conform to ASTM C840, “Standard Specification for Application and Finishing of Gypsum Board.”

2)    Where a membrane referred to in Table D-2.3.4.-A, D-2.3.4.-B, D-2.3.4.-C, D-2.3.4.-D or D-2.3.12. is applied to steel framing or furring, fasteners shall penetrate not less than 10 mm through the metal.

3)    Except as provided in Sentence (4), where a membrane referred to in Table D-2.3.4.-A, D-2.3.4.-B, D-2.3.4.-C, D-2.3.4.-D or D-2.3.12. is applied to wood framing or furring, minimum fastener penetrations into wood members shall conform to Table D-2.3.9. for the time assigned to the membrane.

Table D-2.3.9.

Membrane Fastening

| Type of Membrane | Minimum Penetration of Fasteners for Membrane Protection on Wood Framing, mm |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | 5 – 25 | 30 – 35 | 40 | 50 | 55 – 70 | 80 |
|  | Time,(1) min |  |  |  |  |  |
| Single layer | 20 | 29 | 32 | — | — | — |
| Double layer | 20 | 20 | 20 | 29 | 35 | 44 |
| Gypsum lath | 20 | 20 | 23 | 23 | 29 | 29 |

Notes to Table D-2.3.9.:

(1) Assigned contributions of membranes to fire resistance are listed in Tables D-2.3.4.-A, D-2.3.4.-B, D-2.3.4.-C, D-2.3.4.-D and D-2.3.12.

4)    Where a membrane is applied in 2 layers, the fastener penetrations described in Table D-2.3.9. shall apply to the base layer. Fasteners for the face layer shall penetrate not less than 20 mm into wood supports.

5)    In a double layer application of gypsum board on wood supports, fastener spacing shall conform to ASTM C840, “Standard Specification for Application and Finishing of Gypsum Board.”

D-2.3.10. Ceiling Membrane Openings – Combustible Construction

1)    Except as permitted in Article D-2.3.12., where a floor or roof assembly of combustible construction is assigned a fire-resistance rating on the basis of this Subsection and incorporates a ceiling membrane described in Table D-2.3.4.-B, D-2.3.4.-C or D-2.3.4.-D, the ceiling membrane may be penetrated by openings leading to ducts within concealed spaces above the membrane provided:

a)    the assembly is not required to have a fire-resistance rating in excess of 1 h,

b)    the area of any openings does not exceed 930 cm2 (see Sentence (2)),

c)    the aggregate area of openings does not exceed 1% of the ceiling area of the fire compartment,

d)    the depth of the concealed space above the ceiling is not less than 230 mm,

e)    no dimension of any opening exceeds 310 mm,

f)    supports are provided for openings with any dimension exceeding 150 mm where framing members are spaced greater than 400 mm o.c.,

g)    individual openings are spaced not less than 2 m apart,

h)    the ducts above the membrane are sheet steel and are supported by steel strapping firmly attached to the framing members, and

i)    the clearance between the top surface of the membrane and the bottom surface of the ducts is not less than 100 mm.

2)    Where an individual opening permitted in Sentence (1) exceeds 130 cm2 in area, it shall be protected by

a)    a fire stop flap conforming to CAN/ULC-S112.2, “Standard Method of Fire Test of Ceiling Firestop Flap Assemblies,” that activates at a temperature approximately 30°C above the normal maximum temperature that occurs in the ducts, whether the air duct system is operating or shut down, or

b)    thermal protection above the duct consisting of the same materials as used for the ceiling membrane, mechanically fastened to the ductwork and extending 200 mm beyond the opening on all sides (see Article D-2.3.10.).

Figure D-2.3.10.

Thermal protection above a duct

D-2.3.11. Ceiling Membrane Openings – Noncombustible Construction

1)    Except as permitted in Article D-2.3.12., where a floor or roof assembly of noncombustible construction is assigned a fire-resistance rating on the basis of this Subsection and incorporates a ceiling membrane described in Table D-2.3.4.-B, D-2.3.4.-C or D-2.3.4.-D, the ceiling membrane may be penetrated by openings leading to ducts located within concealed spaces provided:

a)    the area of any opening does not exceed 930 cm2 (see Sentence (2)),

b)    the aggregate area of openings does not exceed 2% of the ceiling area of the fire compartment,

c)    no dimension of any opening exceeds 400 mm,

d)    individual openings are spaced not less than 2 m apart,

e)    openings are located not less than 200 mm from major structural members such as beams, columns or joists,

f)    the ducts above the membrane are sheet steel and are supported by steel strapping firmly attached to the framing members, and

g)    the clearance between the top surface of the membrane and the bottom surface of the duct is not less than 100 mm.

2)    Where an individual opening permitted in Sentence (1) exceeds 130 cm2 in area, it shall be protected by

a)    a fire stop flap conforming to CAN/ULC-S112.2, “Standard Method of Fire Test of Ceiling Firestop Flap Assemblies,” that activates at a temperature approximately 30°C above the normal maximum temperature that occurs in the ducts, whether the air duct system is operating or shut down, or

b)    thermal protection above the duct consisting of the same materials as used for the ceiling membrane, mechanically fastened to the ductwork and extending 200 mm beyond the opening on all sides (see Article D-2.3.10.).

D-2.3.12. Ceiling Membrane Rating

Where the fire-resistance rating of a ceiling assembly is to be determined on the basis of the membrane only and not of the complete assembly, the ratings may be determined from Table D-2.3.12., provided no openings described in Articles D-2.3.10. and D-2.3.11. are located within the ceiling membrane.

Table D-2.3.12.

Fire-Resistance Rating for Ceiling Membranes

| Description of Membrane | Fire-Resistance Rating, min |
| --- | --- |
| 15.9 mm Type X gypsum board with ≥ 75 mm mineral wool batt insulation above board | 30 |
| 19 mm gypsum-sand plaster on metal lath | 30 |
| Double 14.0 mm Douglas Fir plywood phenolic bonded | 30 |
| Double 12.7 mm Type X gypsum board | 45 |
| 25 mm gypsum-sand plaster on metal lath | 45 |
| Double 15.9 mm Type X gypsum board | 60 |
| 32 mm gypsum-sand plaster on metal lath | 60 |

D-2.3.13. Membrane Penetrations in Combustible and Noncombustible Construction

1)    Where a wall, floor or roof assembly is assigned a fire-resistance rating on the basis of this Subsection and includes a membrane or membranes described in Table D-2.3.4.-A, D-2.3.4.-B, D-2.3.4.-C, D-2.3.4.-D or D-2.3.12., penetrations of the membrane or membranes must be firestopped in conformance with the applicable requirements in Article 3.1.9.1. or Sentence 9.10.9.6.(1).

D-2.3.14. Beams

1)    Where a steel beam is included with an open-web steel joist and is protected by the same continuous ceiling, the beam is assumed to have a fire-resistance rating equal to that assigned to the rest of the assembly.

2)    The ratings in this Subsection assume that the construction to which the beam is related is a normal one and does not carry unusual loads from the floor or slab above.

D-2.3.15. Wired Glass Assembly Support

1)    Openings in a vertical fire separation having a fire-resistance rating of not more than 1 h are allowed to be protected by wired glass assemblies, provided the wired glass is

a)    not less than 6 mm thick;

b)    reinforced by a steel wire mesh in the form of diamonds, squares or hexagons having dimensions of

i)   approximately 25 mm across the flats, using wire of not less than 0.45 mm diameter, or

ii)   approximately 13 mm across the flats, using wire of not less than 0.40 mm diameter, the wire to be centrally embedded during manufacture and welded or intertwined at each intersection;

c)    set in fixed steel frames with metal not less than 1.35 mm thick and providing a glazing stop of not less than 20 mm on each side of the glass; and

d)    limited in area so that

i)   individual panes are not more than 0.84 m2, with neither height nor width more than 1.4 m, and

ii)   the area not structurally supported by mullions is not more than 7.5 m2.

2)    It is intended that the structural mullions referred to in Subclause (1)(d)(ii) will not distort or be displaced to the extent that there would be a failure of the wired glass closure during the period for which a closure in the fire separation would be expected to function. Hollow structural steel tubing not less than 100 mm square filled with a Portland cement-based grout will satisfy the intent of the Subclause.

D-2.4. Solid Wood Walls, Floors and Roofs

D-2.4.1. Minimum Thickness

The minimum thickness of solid wood walls, floors and roofs for fire-resistance ratings from 30 min to 1.5 h is shown in Table D-2.4.1.

Table D-2.4.1.

Minimum Thickness of Solid Wood Walls, Roofs and Floors, mm(1)(2)

| Type of Construction | Fire-Resistance Rating |  |  |  |
| --- | --- | --- | --- | --- |
|  | 30 min | 45 min | 1 h | 1.5 h |
| Solid wood floor with building paper and finish flooring on top(3) | 89 | 114 | 165 | 235 |
| Solid wood, splined or tongued and grooved floor with building paper and finish flooring on top(4) | 64 | 76 | — | — |
| Solid wood walls of loadbearing vertical plank(3) | 89 | 114 | 140 | 184 |
| Solid wood walls of non-loadbearing horizontal plank(3) | 89 | 89 | 89 | 140 |

Notes to Table D-2.4.1.:

(1) See CSA O141, “Softwood Lumber,” for sizes.

(2) The fire-resistance ratings and minimum dimensions for floors also apply to solid wood roof decks of comparable thickness with finish roofing material.

(3) The assembly shall consist of 38 mm thick members on edge fastened together with 101 mm common wire nails spaced not more than 400 mm o.c. and staggered in the direction of the grain.

(4) The floor shall consist of 64 mm by 184 mm wide planks either tongued and grooved or with 19 mm by 38 mm splines set in grooves and fastened together with 88 mm common nails spaced not more than 400 mm o.c.

D-2.4.2. Increased Fire-Resistance Rating

1)    The fire-resistance rating of the assemblies described in Table D-2.4.1. may be increased by 15 min if one of the following finishes is applied on the fire-exposed side:

a)    12.7 mm thick gypsum board,

b)    20 mm thick gypsum-sand plaster on metal lath, or

c)    13 mm thick gypsum-sand plaster on 9.5 mm gypsum lath.

2)    Fastening of the plaster to the wood structure shall conform to Subsection D-2.3.

D-2.4.3. Supplementary Ratings

Supplementary ratings based on tests are included in Table D-2.4.3. The ratings given shall apply to constructions that conform in all details with the descriptions given.

Table D-2.4.3.

Fire-Resistance Rating of Non-Loadbearing Built-up Solid Wood Partitions(1)

| Construction Details | Actual Overall Thickness, mm | Fire-Resistance Rating |
| --- | --- | --- |
| Solid panels of wood boards 64 mm to 140 mm wide grooved and joined with wood splines, nailed together, boards placed vertically with staggered joints, 3 boards thick | 58 | 30 min |
| Solid panels with 4 mm plywood facings(2) glued to 46 mm solid wood core of glued, tongued and grooved construction for both sides and ends of core pieces with tongued and grooved rails in the core about 760 mm apart | 54 | 1 h |

Notes to Table D-2.4.3.:

(1) The ratings and notes are taken from “Fire Resistance Classifications of Building Constructions,” Building Materials and Structures Report BMS 92, National Bureau of Standards, Washington, 1942.

(2) Ratings for plywood faced panel are based on phenolic resin glue being used for gluing facings to wood frames. If other types of glue are used for this purpose, the ratings apply if the facings are nailed to the frames in addition to being glued.

D-2.5. Solid Plaster Partitions

D-2.5.1. Minimum Thickness

The minimum thickness of solid plaster partitions for fire-resistance ratings from 30 min to 4 h is shown in Table D-2.5.1.

Table D-2.5.1.

Minimum Thickness of Non-Loadbearing Solid Plaster Partitions, mm

| Type of Plaster on Metal Lath(1) | Fire-Resistance Rating |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | 30 min | 45 min | 1 h | 1.5 h | 2 h | 3 h | 4 h |
| Portland cement-sand(2) or Portland cement-lime-sand | 50(3) | — | — | — | — | — | — |
| Gypsum-sand | 50(3) | 50(3) | 64 | — | — | — | — |
| Gypsum-vermiculite, gypsum-perlite, Portland cement-vermiculite or Portland cement-perlite | 50(3) | 50(3) | 50(3) | 58 | 64 | 83 | 102 |

Notes to Table D-2.5.1.:

(1) Metal lath shall be expanded metal lath or welded woven wire fabric supported on 19 mm vertical light steel studs spaced not more than 600 mm o.c. Plaster shall be applied to both sides of the lath.

(2) For mixture of Portland cement-sand plaster, see Sentence D-1.7.2.(2).

(3) CSA A82.30-M, “Interior Furring, Lathing and Gypsum Plastering,” does not permit solid plaster partitions less than 50 mm thick.

D-2.6. Protected Steel Columns

D-2.6.1. Minimum Thickness of Protective Covering

The minimum thickness of protective covering to steel columns is shown in Tables D-2.6.1.-A to D-2.6.1.-F for fire-resistance ratings from 30 min to 4 h.

Table D-2.6.1.-A

Minimum Thickness of Concrete or Masonry Protection to Steel Columns, mm

| Description of Cover | Fire-Resistance Rating |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | 30 min | 45 min | 1 h | 1.5 h | 2 h | 3 h | 4 h |
| Monolithic concrete |  |  |  |  |  |  |  |
| Type S concrete(1) (column spaces filled)(2) | 25 | 25 | 25 | 25 | 39 | 64 | 89 |
| Type N or L concrete(1) (column spaces filled)(2) | 25 | 25 | 25 | 25 | 32 | 50 | 77 |
| Concrete masonry units(3) or precast reinforced concrete units |  |  |  |  |  |  |  |
| Type S concrete (column spaces not filled) | 50 | 50 | 50 | 50 | 64 | 89 | 115 |
| Type N or L concrete (column spaces not filled) | 50 | 50 | 50 | 50 | 50 | 77 | 102 |
| Clay or shale brick(4) (column spaces filled)(2) | 50 | 50 | 50 | 50 | 50 | 64 | 77 |
| Clay or shale brick(4) (column spaces not filled) | 50 | 50 | 50 | 50 | 50 | 77 | 102 |
| Hollow clay tile(5) (column spaces filled)(2) | 50(6) | 50(6) | 50(6) | 50(6) | (7) | (7) | (7) |
| Hollow clay tile(5) (column spaces not filled) | 50(6) | 50(6) | 50(6) | — | — | — | — |

Notes to Table D-2.6.1.-A:

(1) Applies to cast-in-place concrete reinforced with 5.21 mm diam wire wrapped around column spirally 200 mm o.c., or 1.57 mm diam wire mesh with 100 mm by 100 mm openings.

(2) The space between the protective covering and the web or flange of the column shall be filled with concrete, cement mortar or a mixture of cement mortar and broken bricks.

(3) Concrete masonry shall be reinforced with 5.21 mm diam wire or wire mesh with 1.19 mm diam wire and 10 mm by 10 mm openings, laid in every second course.

(4) Brick cover 77 mm thick or less shall be reinforced with 2.34 mm diam wire or 1.19 mm diam wire mesh with 10 mm by 10 mm openings, laid in every second course.

(5) Hollow clay tiles and masonry mortar shall be reinforced with 1.19 mm diam wire mesh with 10 mm by 10 mm openings, laid in every horizontal joint and lapped at corners.

(6) Hollow clay tiles shall conform to CAN/CSA-A82, “Fired masonry brick made from clay or shale.”

(7) 50 mm nominal hollow clay tile, reinforced with 1.19 mm diam wire mesh with 10 mm by 10 mm openings laid in every horizontal joint and covered with 19 mm gypsum-sand plaster and with limestone concrete fill in column spaces, has a 4 h fire-resistance rating.

Table D-2.6.1.-B

Minimum Thickness of Plaster Protection to Steel Columns, mm

| Description | Fire-Resistance Rating(1)(2) |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | 30 min | 45 min | 1 h | 1.5 h | 2 h | 3 h | 4 h |
| Gypsum-sand plaster on 9.5 mm gypsum lath(3) | 13 | 13 | 13 | 20 | — | — | — |
| Gypsum-perlite or vermiculite plaster on 9.5 mm gypsum lath(3) | 13 | 13 | 13 | 20 | 25 | — | — |
| Gypsum perlite or vermiculite plaster on 12.7 mm gypsum lath(3) | 13 | 13 | 13 | 20 | 25 | 32 | 50 |
| Gypsum perlite or vermiculite plaster on double 12.7 mm gypsum lath(3) | 13 | 13 | 13 | 20 | 25 | 25 | 32 |
| Portland cement-sand plaster on metal lath(4)(5) | 25 | 25 | 25 | — | — | — | — |

Notes to Table D-2.6.1.-B:

(1) Fire-resistance ratings of 30 min and 45 min apply to columns whose M/D ratio is 30 or greater. Fire-resistance ratings greater than 45 min apply to columns whose M/D ratio is greater than 60. Where the M/D ratio is between 30 and 60 and the required fire-resistance rating is greater than 45 min, the total thickness of protection specified in the Table shall be increased by 50%. (To determine M/D, refer to Article D-2.6.4.)

(2) Where the thickness of plaster over gypsum lath is 25 mm or more, wire mesh with 1.57 mm diam wire and openings not exceeding 50 mm by 50 mm shall be placed midway in the plaster.

(3) Lath held in place by 1.19 mm diam wire wrapped around lath 450 mm o.c.

(4) Expanded metal lath 1.36 kg/m 2 fastened to 9.5 mm by 19 mm steel channels held in vertical position around column by 1.19 mm diam wire ties.

(5) For mixture of Portland cement-sand plaster, see Sentence D-1.7.2.(2).

Table D-2.6.1.-C

Minimum Thickness of Gypsum-Sand Plaster on Metal Lath Protection to Steel Columns, mm

| M/D(1) | Fire-Resistance Rating |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | 30 min | 45 min | 1 h | 1.5 h | 2 h | 3 h |
| 30 to 60 | 16 | 16 | 32 | — | — | — |
| over 60 to 90 | 16 | 16 | 16 | 32 | — | — |
| over 90 to 120 | 16 | 16 | 16 | 25 | 39 | — |
| over 120 to 180 | 16 | 16 | 16 | 16 | 25 | — |
| over 180 | 16 | 16 | 16 | 16 | 25 | 39 |

Notes to Table D-2.6.1.-C:

(1) To determine the M/D ratio, refer to Article D-2.6.4.

Table D-2.6.1.-D

Minimum Thickness of Gypsum-Perlite or Gypsum-Vermiculite Plaster on Metal Lath Protection to Steel Columns, mm

| M/D(1) | Fire-Resistance Rating |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | 30 min | 45 min | 1 h | 1.5 h | 2 h | 3 h | 4 h |
| 30 to 60 | 16 | 16 | 20 | 32 | 35 | — | — |
| over 60 to 90 | 16 | 16 | 16 | 20 | 26 | 35 | 45 |
| over 90 to 120 | 16 | 16 | 16 | 16 | 26 | 35 | 45 |
| over 120 to 180 | 16 | 16 | 16 | 16 | 20 | 32 | 35 |
| over 180 | 16 | 16 | 16 | 16 | 16 | 26 | 35 |

Notes to Table D-2.6.1.-D:

(1) To determine the M/D ratio, refer to Article D-2.6.4.

Table D-2.6.1.-E

Steel Columns with Sheet-Steel Membrane and Insulation as Shown in Figures D-2.6.1.-A and D-2.6.1.-B

| Type of Protection | Steel Thickness,(1) mm | Fastening(2) | Insulation | Fire-Resistance Rating |
| --- | --- | --- | --- | --- |
| See Figure D-2.6.1.-A | 0.51 | No. 8 sheet-metal screws 9.5 mm long, 200 mm o.c. | 50 mm mineral wool batts(3) | 45 min |
| See Figure D-2.6.1.-B | 0.64 | Self-threading screws or No. 8 sheet-metal screws, 600 mm o.c. | 2 layers 12.7 mm gypsum board | 1.5 h |
| See Figure D-2.6.1.-A | 0.64 | No. 8 sheet-metal screws, 9.5 mm long 200 mm o.c. | 75 mm mineral wool batts,(3) 12.7 mm gypsum board | 2 h |
| See Figure D-2.6.1.-B | 0.76 | Crimped joint or No. 8 sheet-metal screws, 300 mm o.c. | 2 layers 15.9 mm gypsum board | 2 h |

Notes to Table D-2.6.1.-E:

(1) Minimum thickness, galvanized or wiped-zinc-coated sheet-steel.

(2) Sheet-steel shall be securely fastened to the floor and superstructure, or where sheet-steel cover does not extend floor to floor, firestopping shall be provided at the level where sheet-steel protection ends. In the latter case, an alternate type of fire protection shall be applied between the firestopping and the superstructure.

(3) Conforming to CAN/ULC-S702.1, “Standard for Mineral Fibre Thermal Insulation for Buildings, Part 1: Material Specification,” Type 1A, minimum density 30 kg/m3: column section and batts wrapped with 25 mm mesh chicken wire.

Table D-2.6.1.-F

Minimum M/D Ratio for Steel Columns Covered with Type X Gypsum Board Protection(1)

| Minimum Thickness of Type X Gypsum Board Protection,(2) mm | Fire-Resistance Rating |  |  |  |
| --- | --- | --- | --- | --- |
|  | 1 h | 1.5 h | 2 h | 3 h |
| 12.7 | 75 | — | — | — |
| 15.9 | 55 | — | — | — |
| 25.4 | 35 | 60 | — | — |
| 28.6 | 35 | 50 | — | — |
| 31.8 | 35 | 40 | 75 | — |
| 38.1 | 35 | 35 | 55 | — |
| 41.3 | 35 | 35 | 45 | — |
| 44.5 | 35 | 35 | 35 | — |
| 47.6 | 35 | 35 | 35 | — |
| 50.8 | 35 | 35 | 35 | 75 |
| 63.5 | 35 | 35 | 35 | 45 |

Notes to Table D-2.6.1.-F:

(1) To determine the M/D ratio, refer to Article D-2.6.4.

(2) See Article D-2.6.5.

Figure D-2.6.1.-A

Column protected by sheet-steel membrane and mineral-wool insulation

Figure D-2.6.1.-B

Column protected by sheet-steel membrane and gypsum board

D-2.6.2. Hollow Unit Masonry Columns

For hollow-unit masonry column protection, the thickness shown in Tables D-2.6.1.-A to D-2.6.1.-D is the equivalent thickness as described in Subsection D-1.6.

D-2.6.3. Effect of Plaster

The effect on fire-resistance ratings of the addition of plaster to masonry and monolithic concrete column protection is described in Subsection D-1.7.

D-2.6.4. Determination of M/D Ratio

1)    The ratio M/D to which reference is made in Tables D-2.6.1.-B, D-2.6.1.-C, D-2.6.1.-D and D-2.6.1.-F shall be found by dividing “M,” the mass of the column in kilograms per metre by “D,” the heated perimeter of the steel column section in metres.

2)    The heated perimeter “D” of steel columns, shown as the dashed line in Figure D-2.6.4.-A, shall be equal to 2 (B+H) in Examples (1) and (2), and 3.14B in Example (3). In Figure D-2.6.4.-B, the heated perimeter “D” shall be equal to 2 (B+H).

Figure D-2.6.4.-A

Example (1), standard or wide-flange beam; Example (2), hollow structural section (rectangular or square); Example (3), hollow structural section (round)

Figure D-2.6.4.-B

Columns protected by Type X gypsum board without sheet-steel membrane

D-2.6.5. Attachment of Gypsum Board

1)    Where Type X gypsum board is used to protect a steel column without an outside sheet-steel membrane, the method of gypsum board attachment to the column shall be as shown in Figure D-2.6.4.-B and shall meet the construction details described in Sentences (2) to (7).

2)    The Type X gypsum board shall be applied vertically without horizontal joints.

3)    The first layer of gypsum board shall be attached to steel studs with screws spaced not more than 600 mm o.c. and other layers of gypsum board shall be attached to steel studs and steel corner beads with screws spaced at a maximum of 300 mm o.c. Where a single layer of gypsum board is used, attachment screws shall be spaced not more than 300 mm o.c.

4)    Steel tie wires spaced at a maximum of 600 mm o.c. shall be used to secure the second last layer of gypsum board in 3- and 4-layer systems.

5)    Studs shall be fabricated of galvanized steel not less than 0.53 mm thick and not less than 41.3 mm wide, with legs not less than 33.3 mm long and shall be 12.7 mm less than the assembly height.

6)    Corner beads shall

a)    be fabricated of galvanized steel that is not less than 0.41 mm thick,

b)    have legs not less than 31 mm long,

c)    be attached to the gypsum board or stud with 25.4 mm screws spaced not more than 300 mm o.c., and

d)    have the attaching fasteners penetrate either another corner bead in multiple layer assemblies or the steel stud member.

7)    In a 4-layer system, metal angles shall be fabricated of galvanized steel and shall be not less than 0.46 mm thick with legs not less than 51 mm long.

D-2.6.6. Concrete Filled Hollow Steel Columns

1)    A fire-resistance rating, R, is permitted to be assigned to concentrically loaded hollow steel columns that are filled with plain concrete, steel-fibre reinforced concrete or bar-reinforced concrete, that are fabricated and erected within the tolerances stipulated in CSA S16, “Design of steel structures,” and that comply with Sentences (2) and (3), provided:

where

C   = axial compressive force due to dead and live loads without load factors, kN,

Cmax   =

but shall not exceed

a)    1.0 for plain concrete filling (PC),

b)    1.1 for steel-fibre reinforced concrete filling (FC), and

c)    1.7 for bar-reinforced concrete filling (RC),

where

=

where

a   = constant obtained from Table D-2.6.6.-A,

= specified compressive strength of concrete in accordance with CSA A23.3, “Design of concrete structures,” MPa,

rc   = radius of gyration of the concrete area,

Ac   = area of concrete, mm2,

D   = outside diameter of a round column or outside width of a square column, mm,

Ec   = initial elastic modulus for concrete, considering the effects of long-term loading for normal-weight concrete = , where is expressed in MPa, S is the short-term load, and T is the total load on the column,

R   = specified fire-resistance rating, min,

KL   = effective length of column as defined in CSA S16, “Design of steel structures,” mm,

λc   , and

φc   = 0.60

subject to the validity limits stated in Table D-2.6.6.-B.

Table D-2.6.6.-A

Values of Constant “a”

| Filling Type | Concrete Type(1) | Steel Reinforcement | Circular Columns | Square Columns |
| --- | --- | --- | --- | --- |
| PC | S | n/a | 0.070 | 0.060 |
| FC | S | ≈ 2% | 0.075 | 0.065 |
| RC | S | 1.5%-3% | 0.080 | 0.070 |
| RC | S | 3%-5% | 0.085 | 0.075 |
| PC | N | n/a | 0.080 | 0.070 |
| FC | N | ≈ 2% | 0.085 | 0.075 |
| RC | N | 1.5%-3% | 0.090 | 0.080 |
| RC | N | 3%-5% | 0.095 | 0.085 |

Notes to Table D-2.6.6.-A:

(1) See Subsection D-1.4.

2)    A pair of steam vent holes shall be provided at each end of the hollow steel column and at each intermediate floor level, and the holes shall be

a)    not less than 13 mm in diameter,

b)    located on opposite faces, 150 mm above or below a base plate, cap plate or concrete slab,

c)    orientated so that adjacent pairs are perpendicular, and

d)    not obstructed by other building elements.

3)    Load application and reaction shall be through end bearing in accordance with CSA S16, “Design of steel structures.”

Table D-2.6.6.-B

Validity Limits

| Parameter | Type of Concrete Filling |  |  |
| --- | --- | --- | --- |
|  | PC | FC | RC |
| (MPa) | 20 to 40 | 20 to 55 | 20 to 55 |
| D (round) (mm) | 140 to 410 | 140 to 410 | 165 to 410 |
| D (square) (mm) | 140 to 305 | 102 to 305 | 175 to 305 |
| Reinforcement (%) | n/a | ≈ 2% of the concrete mix by mass | 1.5% to 5% of cross-sectional area(1) |
| Concrete Cover (mm) | n/a | n/a | ≥ 25 |
| R (min) | ≤ 120 | ≤ 180 | ≤ 180 |
| KL (mm) | 2 000 to 4 000 | 2 000 to 4 500 | 2 000 to 4 500 |
| Class(2) | 1, 2 or 3 | 1, 2 or 3 | 1, 2 or 3 |

Notes to Table D-2.6.6.-B:

(1) Limits on size, number and spacing of bars and ties in accordance with CSA A23.3, “Design of concrete structures.”

(2) Classification of sections in accordance with CSA S16, “Design of steel structures.”

D-2.7. Individually Protected Steel Beams

D-2.7.1. Minimum Thickness of Protective Covering

The minimum thickness of protective covering on steel beams exposed to fire on 3 sides for fire-resistance ratings from 30 min to 4 h is shown in Table D-2.7.1.

Table D-2.7.1.

Minimum Thickness of Cover to Individual Protected Steel Beams, mm(1)

| Description of Cover | Fire-Resistance Rating |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | 30 min | 45 min | 1 h | 1.5 h | 2 h | 3 h | 4 h |
| Type S concrete(2) (beam spaces filled solid) | 25 | 25 | 25 | 25 | 32 | 50 | 64 |
| Type N or L concrete(2) (beam spaces filled solid) | 25 | 25 | 25 | 25 | 25 | 39 | 50 |
| Gypsum-sand plaster on 9.5 mm gypsum lath(3) | 13 | 13 | 13 | 20 | — | — | — |
| Gypsum-perlite or vermiculite plaster on 9.5 mm gypsum lath(3) | 13 | 13 | 13 | 13 | 25 | — | — |
| Gypsum-perlite or gypsum-vermiculite on 12.7 mm gypsum lath(3) | 13 | 13 | 13 | 20 | 25 | 39 | 50 |
| Gypsum-perlite or vermiculite plaster on double 12.7 mm gypsum lath(3) | 13 | 13 | 13 | 20 | 25 | 25 | 39 |
| Portland cement-sand on metal lath(4) | 23 | 23 | 23 | — | — | — | — |
| Gypsum-sand on metal lath(4) (plaster in contact with lower flange) | 16 | 20 | 25 | 39 | — | — | — |
| Gypsum-sand on metal lath with air gap between plaster and lower flange(4) | 16 | 16 | 16 | 25 | 25 | — | — |
| Gypsum-perlite or gypsum-vermiculite on metal lath(4) | 16 | 16 | 16 | 23 | 23 | 35 | 48(5) |

Notes to Table D-2.7.1.:

(1) Where the thickness of plaster finish applied over gypsum lath is 26 mm or more, the plaster shall be reinforced with wire mesh with 1.57 mm diam wire and 50 mm by 50 mm openings placed midway in the plaster.

(2) Applies to cast-in-place concrete reinforced by 5.21 mm diam wire spaced 200 mm o.c. or 1.57 mm diam wire mesh with 100 mm by 100 mm openings.

(3) Lath held in place by 1.18 mm diam wire wrapped around the gypsum lath 450 mm o.c.

(4) Expanded metal lath 1.63 kg/m2 fastened to 9.5 mm by 19 mm steel channels held in position by 1.19 mm diam wire.

(5) Plaster finish shall be reinforced with wire mesh with 1.57 mm diam wire and 50 mm by 50 mm openings placed midway in the plaster.

D-2.7.2. Types of Concrete

Concrete is referred to as Type S, N or L, depending on the nature of the aggregate used. This is described in Article D-1.4.1.

D-2.7.3. Effect of Plaster

The effect on fire-resistance ratings of the addition of plaster finish to concrete or masonry beam protection is described in Article D-1.7.1.

D-2.7.4. Exceptions

The fire resistance of protected steel beams depends on the means used to hold the protection in place. Because of the importance of this factor, no rating has been assigned in Table D-2.7.1. to masonry units used as protective cover to steel beams. These ratings, however, may be determined on the basis of comparison with column protection at the discretion of the authority having jurisdiction, if satisfactory means of fastening are provided.

D-2.7.5. Beam Protected by a Membrane

A steel beam or steel joist assembly that is entirely above a horizontal ceiling membrane will be protected from fire below the membrane and will resist structural collapse for a period equal to the fire-resistance rating determined in conformance with Subsection D-2.3. The support for this membrane shall be equivalent to that described in Subsection D-2.3. The rating on this basis shall not exceed 1.5 h.

D-2.8. Reinforced Concrete Columns

D-2.8.1. Minimum Dimensions

Minimum dimensions for reinforced concrete columns and minimum concrete cover for vertical steel reinforcement are obtained from Articles D-2.8.2. to D-2.8.5., taking into account the type of concrete, the effective length of the column and the area of the vertical reinforcement.

D-2.8.2. Method

1)    The minimum dimension, t, in millimetres, of a rectangular reinforced concrete column shall be equal to

a)    75 f (R + 1) for all Types L and L40S concrete,

b)    80 f (R + 1) for Type S concrete when the design condition of the concrete column is defined in the second and fourth columns of Table D-2.8.2.,

c)    80 f (R + 0.75) for Type N concrete when the design condition of the concrete column is defined in the second and fourth columns of Table D-2.8.2., and

d)    100 f (R + 1) for Types S and N concrete when the design condition of the concrete column is defined in the third column of Table D-2.8.2.

where

f   = the value shown in Table D-2.8.2.,

R   = the required fire-resistance rating in hours,

k   = the effective length factor obtained from CSA A23.3, “Design of concrete structures,”

h   = the unsupported length of the column in metres, and

p   = the area of vertical reinforcement in the column as a percentage of the column area.

2)    The diameter of a round column shall be not less than 1.2 times the value t determined in Sentence (1) for a rectangular column.

Table D-2.8.2.

Values of Factor f(1)

| Overdesign Factor(2) | Values of Factor f to be Used in Applying Article D-2.8.2. |  |  |
| --- | --- | --- | --- |
|  | Where kh is not more than 3.7 m | Where kh is more than 3.7 m but not more than 7.3 m |  |
|  |  | t is not more than 300 mm, p is not more than 3%(3) | All other cases(4) |
| 1.00 | 1.0 | 1.2 | 1.0 |
| 1.25 | 0.9 | 1.1 | 0.9 |
| 1.50 | 0.83 | 1.0 | 0.83 |

Notes to Table D-2.8.2.:

(1) For conditions that do not fall within the limits described in Table D-2.8.2., further information may be obtained from Reference (7) in Subsection D-7.1.

(2) Overdesign factor is the ratio of the calculated load carrying capacity of the column to the column strength required to carry the specified loads determined in conformance with CSA A23.3, “Design of concrete structures.”

(3) Where the factor f results in a t greater than 300 mm, the appropriate factor f for “All other cases” shall be applicable.

(4) Where p is equal to or less than 3% and the factor f results in a t less than 300 mm, the minimum thickness shall be 300 mm.

D-2.8.3. Minimum Thickness of Concrete Cover

1)    Where the required fire-resistance rating of a concrete column is 3 h or less, the minimum thickness in millimetres of concrete cover over vertical steel reinforcement shall be equal to 25 times the number of hours of fire resistance required or 50 mm, whichever is less.

2)    Where the required fire-resistance rating of a concrete column is greater than 3 h, the minimum thickness in millimetres of concrete cover over vertical steel reinforcement shall be equal to 50 plus 12.5 times the required number of hours of fire resistance in excess of 3 h.

3)    Where the concrete cover over vertical steel required in Sentence (2) exceeds 62.5 mm, wire mesh reinforcement with 1.57 mm diameter wire and 100 mm openings shall be incorporated midway in the concrete cover to retain the concrete in position.

D-2.8.4. Minimum Requirements

The structural design standards may require minimum column dimensions or concrete cover over vertical steel reinforcement differing from those obtained in Sentences D-2.8.2.(1) and D-2.8.2.(2). Where a difference occurs, the greater dimension shall govern.

D-2.8.5. Addition of Plaster

The addition of plaster finish to the concrete column may be taken into account in determining the cover over vertical steel reinforcement by applying the multiplying factors described in Subsection D-1.7. The addition of plaster shall not, however, justify any decrease in the minimum column sizes shown.

D-2.8.6. Built-in Columns

The fire-resistance rating of a reinforced concrete column that is built into a masonry or concrete wall so that not more than one face may be exposed to the possibility of fire at one time may be determined on the basis of cover to vertical reinforcing steel alone. In order to meet this condition, the wall shall conform to Subsection D-2.1. for the fire-resistance rating required.

D-2.9. Reinforced Concrete Beams

D-2.9.1. Minimum Cover Thickness

The minimum thickness of cover over principal steel reinforcement in reinforced concrete beams is shown in Table D-2.9.1. for fire-resistance ratings from 30 min to 4 h where the width of the beam or joist is at least 100 mm.

Table D-2.9.1.

Minimum Cover to Principal Steel Reinforcement in Reinforced Concrete Beams, mm

| Type of Concrete | Fire-Resistance Rating |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | 30 min | 45 min | 1 h | 1.5 h | 2 h | 3 h | 4 h |
| Type S, N or L | 20 | 20 | 20 | 25 | 25 | 39 | 50 |

D-2.9.2. Maximum Rating

No rating over 2 h may be assigned on the basis of Table D-2.9.1. to a beam or joist where the average width of the part that projects below the slab is less than 140 mm, and no rating over 3 h may be assigned where the average width of the part that projects below the slab is less than 165 mm.

D-2.9.3. Beam Integrated in Floor or Roof Slab

For the purposes of these ratings, a beam may be either independent of or integral with a floor or roof slab assembly.

D-2.9.4. Minimum Thickness

Where the upper extension or top flange of a joist or T-beam in a floor assembly contributes wholly or partly to the thickness of the slab above, the total thickness at any point shall be not less than the minimum thickness described in Table D-2.2.1.-A for the fire-resistance rating required.

D-2.9.5. Effect of Plaster

The addition of plaster finish to a reinforced concrete beam may be taken into account in determining the cover over principal reinforcing steel by applying the multiplying factors described in Subsection D-1.7.

D-2.10. Prestressed Concrete Beams

D-2.10.1. Minimum Cross-Sectional Area and Thickness of Cover

The minimum cross-sectional area and thickness of concrete cover over steel tendons in prestressed concrete beams for fire-resistance ratings from 30 min to 4 h are shown in Table D-2.10.1.

Table D-2.10.1.

Minimum Thickness of Concrete Cover over Steel Tendons in Prestressed Concrete Beams, mm(1)

| Type of Concrete | Area of Beam, cm2 | Fire-Resistance Rating |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | 30 min | 45 min | 1 h | 1.5 h | 2 h | 3 h | 4 h |
| Type S or N | 260 to 970 | 25 | 39 | 50 | 64 | — | — | — |
|  | Over 970 to 1 940 | 25 | 26 | 39 | 45 | 64 | — | — |
|  | Over 1 940 | 25 | 26 | 39 | 39 | 50 | 77 | 102 |
| Type L | Over 970 | 25 | 25 | 25 | 39 | 50 | 77 | 102 |

Notes to Table D-2.10.1.:

(1) Where the thickness of concrete cover over the tendons exceeds 64 mm, a wire mesh reinforcement with 1.57 mm diam wire and 100 mm by 100 mm openings shall be incorporated in the beams to retain the concrete in position around the tendons. The mesh reinforcement shall be located midway in the cover.

D-2.10.2. Minimum Cover Thickness

The cover for an individual tendon shall be the minimum thickness of concrete between the surface of the tendon and the fire-exposed surface of the beam, except that for ungrouted ducts the assumed cover thickness shall be the minimum thickness of concrete between the surface of the duct and the surface of the beam. For beams in which several tendons are used, the cover is assumed to be the average of the minimum cover of the individual tendons. The cover for any individual tendon shall be not less than half the value given in Table D-2.10.1. nor less than 25 mm.

D-2.10.3. Applicability of Ratings

The ratings in Table D-2.10.1. apply to a beam that is either independent of or integral with a floor or roof slab assembly. Minimum thickness of slab and minimum cover to steel tendons in prestressed concrete slabs are contained in Subsection D-2.2.

D-2.10.4. Effect of Plaster

The addition of plaster finish to a prestressed concrete beam may be taken into account in determining the cover over steel tendons by applying the multiplying factors described in Subsection D-1.7.

D-2.10.5. Minimum Cover

1)    Except as provided in Sentence (2), in unbonded post-tensioned prestressed concrete beams, the concrete cover to the tendon at the anchor shall be not less than 15 mm greater than the minimum required away from the anchor. The concrete cover to the anchorage bearing plate and to the end of the tendon, if it projects beyond the bearing plate, shall be not less than 25 mm.

2)    The requirements in Sentence (1) do not apply to those portions of beams not likely to be exposed to fire (such as the ends and the tops of flanges of beams immediately below slabs).

D-2.11. Mass Timber Elements

D-2.11.1. Determination of Ratings

1)    The calculation methods described in this Subsection are intended to be used to determine fire-resistance ratings for structural mass timber elements on the basis of the elements being subjected to the standard fire exposure conditions described in CAN/ULC-S101, “Standard Method of Fire Endurance Tests of Building Construction and Materials.”

2)    Loadbearing mass timber members, such as beams and columns, subjected to the conditions described in Sentence (1) are assigned a fire-resistance rating that relates to the time at which the applied load is no longer sustained.

3)    Mass timber wall, floor and roof assemblies subjected to the conditions described in Sentence (1) are assigned a fire-resistance rating that relates to the lesser of the times at which

a)    an average temperature rise of 140°C or a maximum temperature rise of 180°C at any individual location is recorded on the unexposed side of the assembly,

b)    there is passage of flame or gases hot enough to ignite cotton pads through the unexposed side of the assembly, or

c)    the applied load is no longer sustained, where the assembly is loadbearing.

D-2.11.2. Applicability of Calculation Methods

1)    Method A described in Article D-2.11.3. applies to glued-laminated timber beams and columns required to have fire-resistance ratings greater than those afforded under the provisions of Article 3.1.4.6.

2)    Method B described in Article D-2.11.4. applies to mass timber elements, including solid sawn timber and glued-laminated timber beams and columns, required to have fire-resistance ratings greater than those afforded under the provisions of Article 3.1.4.6.

3)    The calculation methods described in Articles D-2.11.3. and D-2.11.4. are separate and independent methods that use different approaches to determine fire-resistance ratings for mass timber elements.

D-2.11.3. Method A for Glued-Laminated Timber Beams and Columns

1)    The fire-resistance rating of glued-laminated timber beams and columns in minutes is permitted to be taken as equal to

a)    0.1 fB [4 − 2(B/D)] for beams that may be exposed to fire on 4 sides,

b)    0.1 fB [4 − (B/D)] for beams that may be exposed to fire on 3 sides,

c)    0.1 fB [3 − (B/D)] for columns that may be exposed to fire on 4 sides, and

d)    0.1 fB [3 − (B/2D)] for columns that may be exposed to fire on 3 sides,

where

f   = the load factor shown in Figure D-2.11.3.-A,

B   = the full dimension of the smaller side of a beam or column in millimetres before exposure to fire [see Figure D-2.11.3.-B],

D   = the full dimension of the larger side of a beam or column in millimetres before exposure to fire [see Figure D-2.11.3.-B],

k   = the effective length factor obtained from CSA O86, “Engineering design in wood,”

L   = the unsupported length of a column in millimetres.

Figure D-2.11.3.-A

Factors to compensate for partially loaded columns and beams

Notes to Figure D-2.11.3.-A:

(1) In the case of beams, use bending moment in place of load.

(2) See Sentence (2).

2)    The factored resistance of a beam or column shall be determined by using the specified strengths in CSA O86, “Engineering design in wood.”

Figure D-2.11.3.-B

Full dimensions of glued-laminated beams and columns

D-2.11.4. Method B for Mass Timber Elements

1)    The fire-resistance rating of structural mass timber members, such as beams and columns constructed of glued-laminated timber, solid sawn timber, or structural composite lumber, is permitted to be determined using the calculation method described in Annex B, Fire resistance of large cross-section wood elements, of CSA O86, “Engineering design in wood.”

2)    Except as provided in Sentences (3) to (6), the fire-resistance rating of mass timber wall, floor and roof assemblies, including those constructed of cross-laminated timber, is permitted to be determined using the calculation method described in Annex B, Fire resistance of large cross-section wood elements, of CSA O86, “Engineering design in wood.”

3)    Except as provided in Sentence (4), the assemblies described in Sentence (2) shall be protected to maintain the integrity and thermal insulation properties of the assembly for the time period corresponding to the calculated fire-resistance rating as follows:

a)    except as provided in Clause (b), for floor and roof assemblies, by applying at least one of the following layers to the unexposed surface of the assembly:

i)   OSB or plywood not less than 12.5 mm thick, with the joints in the layer staggered relative to those in the assembly,

ii)   concrete topping not less than 38 mm thick, or

iii)   gypsum-concrete topping not less than 25 mm thick,

b)    for plank decking designed in accordance with Clause B.10 of CSA O86, “Engineering design in wood,” by applying at least one of the layers described in Clause B.10.4 of CSA O86 to the unexposed surface of the assembly,

c)    for interior wall assemblies, by applying at least one of the following layers to at least one side of the assembly, with the joints in the layer staggered relative to those in the assembly:

i)   OSB or plywood not less than 12.5 mm thick, or

ii)   Type X gypsum board not less than 12.7 mm thick, and

d)    for exterior wall assemblies, by applying at least one of the following layers to at least one side of the assembly, with the joints in the layer staggered relative to those in the assembly:

i)   OSB or plywood not less than 12.5 mm thick,

ii)   Type X gypsum board not less than 12.7 mm thick,

iii)   gypsum sheathing not less than 12.7 mm thick applied to the exterior (unexposed) side of the assembly, or

iv)   rock or slag insulation sheathing not less than 50 mm thick applied to the exterior (unexposed) side of the assembly.

4)    For wall, floor and roof assemblies constructed of cross-laminated timber, the joints between cross-laminated timber panels in the assembly need not be protected in accordance with Sentence (3), provided the joints are either lapped or splined to maintain the integrity and thermal insulation properties of the assembly for the time period corresponding to the calculated fire-resistance rating. (See Figure D-2.11.4.(4).)

Figure D-2.11.4.(4)

Joints between cross-laminated timber panels in wall, floor and roof assemblies

5)    For interior wall assemblies, the additional times assigned in Clause B.8.1 of CSA O86, “Engineering design in wood,” shall only be applied to the calculated fire-resistance rating where both sides of the assembly are protected in accordance with Clause B.8 of CSA O86. Where the level of protection differs on the two sides, the additional time corresponding to the lesser level of protection shall be applied.

6)    For exterior wall assemblies, the additional times assigned in Clause B.8.1 of CSA O86, “Engineering design in wood,” shall only be applied to the calculated fire-resistance rating where

a)    the interior (fire-exposed) side of the assembly is protected in accordance with Clause B.8 of CSA O86, and

b)    except where the assembly is constructed of cross-laminated timber panels with lapped or splined joints as described in Sentence (4), the exterior (unexposed) side of the assembly is protected in accordance with Clause (3)(d).

Section  D-3  Flame-Spread Ratings and Smoke Developed Classifications

D-3.1. Interior Finish Materials

D-3.1.1. Scope of Information

Tables D-3.1.1.-A and D-3.1.1.-B show flame-spread ratings and smoke developed classifications for combinations of some common interior finish materials. The values are based on all the evidence available at present. Many materials have not been included because of lack of test evidence or because of inability to classify or describe the material in generic terms for the purpose of assigning ratings.

Table D-3.1.1.-A

Assigned Flame-Spread Ratings and Smoke Developed Classifications for Combinations of Wall and Ceiling Finish Materials and Surface Coatings(1)

| Materials | Applicable Material Standard | Minimum Thickness, mm | Surface Coating |  |
| --- | --- | --- | --- | --- |
|  |  |  | Unfinished | Paint or Varnish not more than 1.3 mm Thick, Cellulosic Wallpaper not more than One Layer(2)(3) |
| Brick, concrete, tile | None | None | 0/0 | 25/50 |
| Steel, copper, aluminum | None | 0.33 |  |  |
| Gypsum plaster | CSA A82.22-M | None |  |  |
| Gypsum board | CAN/CSA A82.27-M | 9.5 | 25/50 | 25/50 |
|  | ASTM C1396/C1396M |  |  |  |
| Lumber | None | 16 | 150/300 | 150/300 |
| Douglas Fir plywood(4) | CSA O121 | 11 | 150/100 | 150/300 |
| Poplar plywood(4) | CSA O153 |  |  |  |
| Plywood with Spruce face veneer(4) | CSA O151 |  |  |  |
| Douglas Fir plywood(4) | CSA O121 | 6 | 150/100 | 150/100 |
| Fibreboard low density | CAN/ULC-S706.1 | 11 | X/100 | 150/100 |
| Particleboard | ANSI A208.1 | 12.7 | 150/300 | (5) |
| Waferboard, OSB | CSA O437.0 | — | (5) | (5) |
|  | CSA O325 | — | (5) | (5) |

Notes to Table D-3.1.1.-A:

(1) See Sentence D-1.1.1.(5) for standards used to assign flame-spread ratings and smoke developed classifications.

(2) Flame-spread ratings and smoke developed classifications for paints and varnish are not applicable to shellac and lacquer.

(3) Flame-spread ratings and smoke developed classifications for paints apply only to alkyd and latex paints.

(4) The flame-spread ratings and smoke developed classifications shown are for those plywoods without a cellulose resin overlay.

(5) Insufficient test information available.

Table D-3.1.1.-B

Flame-Spread Ratings and Smoke-Developed Classifications for Combinations of Common Floor Finish Materials and Surface Coatings(1)

| Materials | Applicable Standard | FSR/SDC(2) |
| --- | --- | --- |
| Hardwood or softwood flooring either unfinished or finished with a spar or urethane varnish coating | None | 300/300 |
| Wool carpet (woven), pile weight not less than 1120 g/m2, applied with or without felt underlay(3) | CAN/CGSB-4.129 | 300/300 |
| Nylon carpet, pile weight not less than 610 g/m2 and not more than 800 g/m 2, applied with or without felt underlay(3) | CAN/CGSB-4.129 | 300/500 |
| Nylon carpet, pile weight not less than 610 g/m2 and not more than 1355 g/m 2, glued down to concrete | CAN/CGSB-4.129 | 300/500 |
| Wool/nylon blend carpet (woven) with not more than 20% nylon and pile weight not less than 1120 g/m 2 | CAN/CGSB-4.129 | 300/500 |
| Nylon/wool blend carpet (woven) with not more than 50% wool, pile weight not less than 610 g/m2 and not more than 800 g/m2 | CAN/CGSB-4.129 | 300/500 |
| Polypropylene carpet, pile weight not less than 500 g/m2 and not more than 1200 g/m2, glued down to concrete | CAN/CGSB-4.129 | 300/500 |

Notes to Table D-3.1.1.-B:

(1) Tested on the floor of the tunnel in conformance with provisions of CAN/ULC-S102.2, “Standard Method of Test for Surface Burning Characteristics of Flooring, Floor Coverings, and Miscellaneous Materials and Assemblies.”

(2) Flame-Spread Rating/Smoke Developed Classification.

(3) Type 1 or 2 underlay as described in CGSB 4-GP-36M, “Carpet Underlay, Fiber Type.”

D-3.1.2. Ratings

The ratings shown in Tables D-3.1.1.-A and D-3.1.1.-B are arranged in groups corresponding to the provisions of this Code. The ratings apply to materials falling within the general categories indicated.

D-3.1.3. Table Entries

In Tables D-3.1.1.-A and D-3.1.1.-B, the first number of each entry relates to flame spread and the second number to smoke developed limit. For example:

25/50 represents a flame-spread rating of 0 to 25 and a smoke developed classification of 0 to 50,

150/300 represents a flame-spread rating of 75 to 150 and a smoke developed classification of 100 to 300, and

X/X applied to walls and ceilings means a flame-spread rating over 150 and a smoke developed classification over 300.

D-3.1.4. Effect of Surface Coatings

Thin surface coatings can modify flame-spread characteristics either upward or downward. Table D-3.1.1.-A includes a number of thin coatings that increase the flame-spread rating of the base material, so that these may be considered where more precise control over flame-spread hazard is desired.

D-3.1.5. Proprietary Materials

1)    Information on flame-spread rating of proprietary materials and fire-retardant treatments that cannot be described in sufficient detail to ensure reproducibility is available through the listing and labeling services of ULC Standards, Intertek Testing Services NA Ltd., or other recognized testing laboratory.

2)    A summary of flame-spread test results published prior to 1965 has been prepared by NRC (see Item (1) in Subsection D-7.1.).

D-3.1.6. Limitations and Conditions

1)    The propagation of flame along a surface in the standard test involves some finite depth of the material or materials behind the surface, and this involvement extends to the depth to which temperature variations are to be found during the course of the test; for many commonly used lining materials, such as wood, the depth involved is about 25 mm.

2)    For all the combustible materials described in Table D-3.1.1.-A, a minimum dimension is shown, and this represents the thickness of the test samples on which the rating has been based; when used in greater thicknesses than that shown, these materials may have a slightly lower flame-spread rating, and thinner specimens may have higher flame-spread ratings.

3)    No rating has been included for foamed plastic materials because it is not possible at this time to identify these products with sufficient accuracy on a generic basis. Materials of this type that melt when exposed to the test flame generally show an increase in flame-spread rating as the thickness of the test specimen increases.

D-3.1.7. Referenced Standards

In Tables D-3.1.1.-A and D-3.1.1.-B, the standards applicable to the materials described are noted because the ratings depend on conformance with these specifications.

Section  D-4  Noncombustibility

D-4.1. Test Method

D-4.1.1. Determination of Noncombustibility

1)    Noncombustibility is required of certain components of buildings by the provisions of this Code, which specifies noncombustibility by reference to CAN/ULC-S114, “Standard Method of Test for Determination of Non-Combustibility in Building Materials.”

2)    The test to which reference is made in Sentence (1) is severe, and it may be assumed that any building material containing even a small proportion of combustibles will itself be classified as combustible. The specimen, 38 mm by 51 mm, is exposed to a temperature of 750°C in a small furnace. The essential criteria for noncombustibility are that the specimen does not flame or contribute to temperature rise.

D-4.2. Materials Classified as Combustible

D-4.2.1. Combustible Materials

Most materials from animal or vegetable sources will be classed as combustible by CAN/ULC-S114, “Standard Method of Test for Determination of Non-Combustibility in Building Materials,” and wood, wood fibreboard, paper, felt made from animal or vegetable fibres, cork, plastics, asphalt and pitch would therefore be classed as combustible.

D-4.2.2. Composite Materials

Materials that consist of combustible and noncombustible elements in combination will in many cases also be classed as combustible, unless the proportion of combustibles is very small. Some mineral wool insulations with combustible binder, cinder concrete, cement and wood chips and wood-fibred gypsum plaster would also be classed as combustible.

D-4.2.3. Effect of Chemical Additives

The addition of a fire-retardant chemical is not sufficient to change a combustible product to a noncombustible product.

D-4.3. Materials Classified as Noncombustible

D-4.3.1. Typical Examples

Noncombustible materials include brick, ceramic tile, concrete made from Portland cement with noncombustible aggregate, plaster made from gypsum with noncombustible aggregate, metals commonly used in buildings, glass, granite, sandstone, slate, limestone and marble.

Section  D-5  Protection of Openings in Fire-Rated Assemblies

D-5.1. Scope

D-5.1.1. Installation Information

1)    The information in this Section specifies requirements for the installation of fire doors and fire dampers in gypsum-board-protected stud wall assemblies.

D-5.2. Installation of Fire Doors and Fire Dampers

D-5.2.1. References

1)    Fire doors and fire dampers in gypsum-board-protected steel stud non-loadbearing walls required to have a fire-resistance rating shall be installed in conformance with Section 9.24. and the applicable requirements of NFPA 80, “Standard for Fire Doors and Other Opening Protectives.”

2)    Fire doors and fire dampers in gypsum-board-protected wood stud walls required to have a fire-resistance rating shall be installed in conformance with Section 9.23. and the applicable requirements of NFPA 80, “Standard for Fire Doors and Other Opening Protectives.”

Section  D-6  Fire Performance of Exterior Wall Assemblies

D-6.1. Scope

D-6.1.1. Exterior Wall Assemblies

Table D-6.1.1. shows construction specifications for exterior wall assemblies that are deemed to satisfy the criteria of Clause 3.1.5.5.(1)(b) when tested in accordance with CAN/ULC-S134, “Standard Method of Fire Test of Exterior Wall Assemblies.”

Table D-6.1.1.

Construction Specifications for Exterior Wall Assemblies that Are Deemed to Satisfy the Criteria of Clause 3.1.5.5.(1)(b) when Tested in Accordance with CAN/ULC-S134

| Wall Number | Structural Members | Absorptive Material | Sheathing | Cladding | Design |
| --- | --- | --- | --- | --- | --- |
| EXTW-1 | 38 mm × 89 mm wood studs spaced at 400 mm o.c.(1)(2) | 89 mm thick rock or slag fibre in cavities formed by studs(3)(4) | — | 12.7 mm thick fire-retardant-treated plywood siding(5) |  |
| EXTW-2 | 38 mm × 140 mm wood studs spaced at 400 mm o.c.(1)(2) | 140 mm thick rock or slag fibre in cavities formed by studs(3)(4) | Gypsum sheathing ≥ 12.7 mm thick | Noncombustible exterior cladding |  |
| EXTW-3 | 38 mm × 140 mm wood studs spaced at 400 mm o.c.(1)(2) | 140 mm thick rock or slag fibre in cavities formed by studs(3)(4) | 15.9 mm thick fire-retardant- treated plywood(6) | Noncombustible exterior cladding |  |
| EXTW-4 | 38 mm × 140 mm wood studs spaced at 600 mm o.c.(1)(7) attached to cross-laminated timber (CLT) wall panels ≥ 38 mm thick(8) | 140 mm thick glass, rock or slag fibre in cavities formed by studs(3) | Gypsum sheathing ≥ 12.7 mm thick | Noncombustible exterior cladding |  |
| EXTW-5 | 89 mm horizontal Z-bars spaced at 600 mm o.c. attached to CLT wall panels ≥ 105 mm thick(8) | 89 mm thick rock or slag fibre in cavities formed by Z-bars(3)(4) | — | Noncombustible exterior cladding attached to 19 mm vertical hat channels spaced at 600 mm o.c. |  |

Notes to Table D-6.1.1.:

(1) The stated stud dimensions are maximum values. Where wood studs with a smaller depth are used, the thickness of the absorptive material in the cavities formed by the studs must be reduced accordingly.

(2) Horizontal blocking between the vertical studs or horizontal stud plates must be installed at vertical intervals of not more than 2 324 mm, such that the maximum clear length between the horizontal blocking or stud plates is 2 286 mm.

(3) The absorptive material must conform to CAN/ULC-S702.1, “Standard for Mineral Fibre Thermal Insulation for Buildings, Part 1: Material Specification.”

(4) The absorptive material must have a density not less than 32 kg/m3.

(5) The fire-retardant-treated plywood siding must conform to the requirements of Article 3.1.4.5. and must have been conditioned in conformance with ASTM D2898, “Standard Practice for Accelerated Weathering of Fire-Retardant-Treated Wood for Fire Testing,” before being tested in accordance with CAN/ULC-S102, “Standard Method of Test for Surface Burning Characteristics of Building Materials and Assemblies.”

(6) The fire-retardant-treated plywood must conform to the requirements of Article 3.1.4.5.

(7) Horizontal blocking between the vertical studs or horizontal stud plates must be installed at vertical intervals of not more than 2 438 mm, such that the maximum clear length between the horizontal blocking or stud plates is 2 400 mm.

(8) A water-resistant barrier is permitted to be attached to the face of the CLT wall panels.

Section  D-7  Background Information

D-7.1. Fire Test Reports

Summaries of available fire test information have been published by NRC as follows:

(1) M. Galbreath, Flame Spread Performance of Common Building Materials. Technical Paper No. 170, Division of Building Research, National Research Council Canada, Ottawa, April 1964. NRCC 7820.

(2) M. Galbreath and W.W. Stanzak, Fire Endurance of Protected Steel Columns and Beams. Technical Paper No. 194, Division of Building Research, National Research Council Canada, Ottawa, April 1965. NRCC 8379.

(3) T.Z. Harmathy and W.W. Stanzak, Elevated-Temperature Tensile and Creep Properties of Some Structural and Prestressing Steels. American Society for Testing and Materials, Special Technical Publication 464, 1970, p. 186 (DBR Research Paper No. 424) NRCC 11163.

(4) T.Z. Harmathy, Thermal Performance of Concrete Masonry Walls in Fire. American Society for Testing and Materials, Special Technical Publication 464, 1970, p. 209 (DBR Research Paper No. 423) NRCC 11161.

(5) L.W. Allen, Fire Endurance of Selected Non-Loadbearing Concrete Masonry Walls. DBR Fire Study No. 25, Division of Building Research, National Research Council Canada, Ottawa, March 1970. NRCC 11275.

(6) A. Rose, Comparison of Flame Spread Ratings by Radiant Panel, Tunnel Furnace, and Pittsburgh-Corning Apparatus. DBR Fire Study No. 22, Division of Building Research, National Research Council Canada, Ottawa, June 1969. NRCC 10788.

(7) T.T. Lie and D.E. Allen, Calculation of the Fire Resistance of Reinforced Concrete Columns. DBR Technical Paper No. 378, Division of Building Research, National Research Council Canada, Ottawa, August 1972. NRCC 12797.

(8) W.W. Stanzak, Column Covers: A Practical Application of Sheet Steel as a Protective Membrane. DBR Fire Study No. 27, Division of Building Research, National Research Council Canada, Ottawa, February 1972. NRCC 12483.

(9) W.W. Stanzak, Sheet Steel as a Protective Membrane for Steel Beams and Columns. DBR Fire Study No. 23, Division of Building Research, National Research Council Canada, Ottawa, November 1969. NRCC 10865.

(10) W.W. Stanzak and T.T. Lie, Fire Tests on Protected Steel Columns with Different Cross-Sections. DBR Fire Study No. 30, Division of Building Research, National Research Council Canada, Ottawa, February 1973. NRCC 13072.

(11) G. Williams-Leir and L.W. Allen, Prediction of Fire Endurance of Concrete Masonry Walls. DBR Technical Paper No. 399, Division of Building Research, National Research Council Canada, Ottawa, November 1973. NRCC 13560.

(12) G. Williams-Leir, Prediction of Fire Endurance of Concrete Slabs. DBR Technical Paper No. 398, Division of Building Research, National Research Council Canada, Ottawa, November 1973. NRCC 13559.

(13) A. Rose, Flammability of Fibreboard Interior Finish Materials. Building Research Note No. 68, Division of Building Research, National Research Council Canada, Ottawa, October 1969.

(14) L.W. Allen, Effect of Sand Replacement on the Fire Endurance of Lightweight Aggregate Masonry Units. DBR Fire Study No. 26, Division of Building Research, National Research Council Canada, Ottawa, September 1971. NRCC 12112.

(15) L.W. Allen, W.W. Stanzak and M. Galbreath, Fire Endurance Tests on Unit Masonry Walls with Gypsum Wallboard. DBR Fire Study No. 32, Division of Building Research, National Research Council Canada, Ottawa, February 1974, NRCC 13901.

(16) W.W. Stanzak and T.T. Lie, Fire Resistance of Unprotected Steel Columns. Journal of Structural Division, Proc., Am. Soc. Civ. Eng., Vol. 99, No. ST5 Proc. Paper 9719, May 1973 (DBR Research Paper No. 577) NRCC 13589.

(17) T.T. Lie and T.Z. Harmathy, Fire Endurance of Concrete-Protected Steel Columns. A.C.I. Journal, January 1974, Title No. 71-4 (DBR Technical Paper No. 597) NRCC 13876.

(18) T.T. Lie, A Method for Assessing the Fire Resistance of Laminated Timber Beams and Columns. Can. J. Civ. Eng., Vol. 4, No. 2, June 1977 (DBR Technical Paper No. 718) NRCC 15946.

(19) T.T. Lie, Calculation of the Fire Resistance of Composite Concrete Floor and Roof Slabs. Fire Technology, Vol. 14, No. 1, February 1978 (DBR Technical Paper No. 772) NRCC 16658.

(20) M.A. Sultan, Y.P. Séguin and P. Leroux. Results of Fire Resistance Tests on Full-Scale Floor Assemblies, Institute for Research in Construction, National Research Council Canada, Ottawa, May 1998, IRC-IR-764.

(21) M.A. Sultan, J.C. Latour, P. Leroux, R.C. Monette, Y.P. Séguin and J.P. Henrie, Results of Fire Resistance Tests on Full-Scale Floor Assemblies - Phase II, Institute for Research in Construction, National Research Council Canada, Ottawa, March 2005, RR-184.

(22) M.A. Sultan and G.D. Lougheed, Results of Fire Resistance Tests on Full-Scale Gypsum Board Wall Assemblies, Institute for Research in Construction, National Research Council Canada, Ottawa, August 2002, IRC-IR-833.

(23) V.K.R. Kodur, M.A. Sultan, J.C. Latour, P. Leroux, R.C. Monette, Experimental Studies on the Fire Resistance of Load-Bearing Steel Stud Walls, Research Report, National Research Council Canada, Ottawa, August 2013, RR-343.

(24) E. Gibbs, B.C. Taber, G.D. Lougheed, J.Z. Su and N. Bénichou, Solutions for Mid-Rise Wood Construction: Full-Scale Standard Fire Test for Exterior Wall Assembly Using Lightweight Wood Frame Construction with Gypsum Sheathing (Test EXTW-1), Report to Research Consortium for Wood and Wood-Hybrid Mid-Rise Buildings, National Research Council Canada, Ottawa, December 2014, A1-100035-01.4.

(25) E. Gibbs, B.C. Taber, G.D. Lougheed, J.Z. Su and N. Bénichou, Solutions for Mid-Rise Wood Construction: Full-Scale Standard Fire Test for Exterior Wall Assembly Using a Simulated Cross-Laminated Timber Wall Assembly with Gypsum Sheathing (Test EXTW-2), Report to Research Consortium for Wood and Wood-Hybrid Mid-Rise Buildings, National Research Council Canada, Ottawa, December 2014, A1-100035-01.5.

(26) E. Gibbs, B.C. Taber, G.D. Lougheed, J.Z. Su and N. Bénichou, Solutions for Mid-Rise Wood Construction: Full-Scale Standard Fire Test for Exterior Wall Assembly Using Lightweight Wood Frame Construction with Interior Fire-Retardant-Treated Plywood Sheathing (Test EXTW-3), Report to Research Consortium for Wood and Wood-Hybrid Mid-Rise Buildings, National Research Council Canada, Ottawa, December 2014, A1-100035-01.6.

(27) E. Gibbs and J. Su, Full Scale Exterior Wall Test on Nordic Cross-Laminated Timber System, National Research Council Canada, Ottawa, January 2015, A1-006009.1.

D-7.2. Obsolete Materials and Assemblies

Building materials, components and structural members and assemblies in buildings constructed before 1995 may have been assigned ratings based on earlier editions of the Supplement to the National Building Code of Canada 1990 or older reports of fire tests. To assist users in determining the ratings of these obsolete assemblies and structural members, the following list of reference documents has been prepared. Although some of these publications are out of print, reference copies are available through NRC.

(1) M. Galbreath, Fire Endurance of Unit Masonry Walls. Technical Paper No. 207, Division of Building Research, National Research Council Canada, Ottawa, October 1965. NRCC 8740.

(2) M. Galbreath, Fire Endurance of Light Framed and Miscellaneous Assemblies. Technical Paper No. 222, Division of Building Research, National Research Council Canada, Ottawa, June 1966. NRCC 9085.

(3) M. Galbreath, Fire Endurance of Concrete Assemblies. Technical Paper No. 235, Division of Building Research, National Research Council Canada, Ottawa, November 1966. NRCC 9279.

(4) Guideline on Fire Ratings of Archaic Materials and Assemblies. Rehabilitation Guideline #8, U.S. Department of Housing and Urban Development, Germantown, Maryland 20767, October 1980.

(5) T.Z. Harmathy, Fire Test of a Plank Wall Construction. Fire Study No. 2, Division of Building Research, National Research Council Canada, Ottawa, July 1960. NRCC 5760.

(6) T.Z. Harmathy, Fire Test of a Wood Partition. Fire Study No. 3, Division of Building Research, National Research Council Canada, Ottawa, October 1960. NRCC 5769.

D-7.3. Assessment of Archaic Assemblies

Information in this document applies to new construction. Please refer to early editions of the Supplement to the National Building Code of Canada 1990 for the assessment or evaluation of assemblies that do not conform to the information in this edition of the National Building Code. As with other documents, this Code is revised according to the information presented to the standing committee responsible for its content, and with each update new material may be added and material that is not relevant may be deleted.

D-7.4. Development of the Component Additive Method

The component additive method was developed based upon the following observations and conclusions drawn from published as well as unpublished test information.

Study of the test data showed that structural failure preceded failure by other criteria (transmission of heat or hot gases) in most of the tests of loadbearing wood-framed assemblies. The major contributor to fire resistance was the membrane on the fire-exposed side.

Fire tests of wood joist floors without protective ceilings resulted in structural failure between 8 and 10 min. Calculation of the time for wood joists to approach breaking stress, based upon the charring rate of natural woods, suggested a time of 10 min for structural failure. This time was subtracted from the fire-resistance test results of wood joist floors and the remainder considered to be the contribution of the membrane.

The figures obtained for the contribution of membranes were then applied to the test results for open web steel joist floors and wood and steel stud walls and values of 20 min for the contribution of wood stud framing and 10 min for steel framing were derived.

The fire-resistance rating has been limited to 1.5 h as this method of developing ratings for framed assemblies was new and untried. Although this is the subject of current review, no decision has been made to extend the ratings beyond 1.5 h.

(1) M. Galbreath, G. C. Gosselin, and R. B. Chauhan, Historical Guide to Chapter 2 of the Supplement to the National Building Code of Canada, Committee Paper FPR 1-3, Prepared for the Standing Committee on Fire Performance Ratings, May 1987.

Example showing fire-resistance rating of a typical membrane assembly, calculated using the component additive method.

1 hour Gypsum Board/Wood Stud Interior Partition

A 1 h fire-resistance rating is required for an interior wood framed partition, using 12.7 mm Type X gypsum board.

(a)   Since gypsum board is used (Sentence D-2.3.4.(2) and Table D-2.3.4.-A) time assigned to 12.7 mm Type X gypsum board membrane on the fire-exposed side of the partition = 25 min

(b)   Time assigned to wood framing members at 400 mm o.c. (Sentence D-2.3.4.(3) and Table D-2.3.4.-E) = 20 min

(c)   Time assigned to insulation, if the spaces between the studs are filled with preformed insulation of rock or slag fibres conforming to CAN/ULC-S702.1, “Standard for Mineral Fibre Thermal Insulation for Buildings, Part 1: Material Specification,” (Sentence D-2.3.4.(4) and Table D-2.3.4.-G) = 15 min

(d)   Time assigned to the membrane on the non-fire-exposed side (Sentence D-2.3.5.(1)) = 0 min
Fire-resistance rating = 25 + 20 + 15 = 60 min