Part 3

Fire Protection, Occupant Safety and

Accessibility

(See Note A-3.)

Section  3.1.   General

3.1.1. Scope and Definitions

3.1.1.1. Scope

1)   The scope of this Part shall be as described in Subsection 1.3.3. of Division A.

3.1.1.2. Defined Words

1)   Words that appear in italics are defined in Article 1.4.1.2. of Division A.

3.1.1.3. Use of Term Storage Tank

1)   For the purposes of this Part, the term “storage tank” shall mean a vessel for flammable liquids or combustible liquids having a capacity of more than 230 L and designed to be installed in a fixed location.

3.1.1.4. Fire Protection Information

1)   Information to be submitted regarding major components of fire protection shall conform to the requirements of Subsection 2.2.3. of Division C.

3.1.2. Classification of Buildings or Parts of Buildings by Major Occupancy

(See Note A-3.1.2.)

3.1.2.1. Classification of Buildings

1)   Except as permitted by Articles 3.1.2.3. to 3.1.2.5., and 3.1.2.7., every building or part thereof shall be classified according to its major occupancy as belonging to one of the Groups or Divisions described in Table 3.1.2.1. (See Note A-3.1.2.1.(1).)

2)   A building intended for use by more than one major occupancy shall be classified according to all major occupancies for which it is used or intended to be used.

Table 3.1.2.1.

Major Occupancy Classification

Forming Part of Sentences 3.1.2.1.(1) and 3.1.2.2.(1)

| Group | Division | Description of Major Occupancies |
| --- | --- | --- |
| A | 1 | Assembly occupancies intended for the production and viewing of the performing arts |
| A | 2 | Assembly occupancies not elsewhere classified in Group A |
| A | 3 | Assembly occupancies of the arena type |
| A | 4 | Assembly occupancies in which occupants are gathered in the open air |
| B | 1 | Detention occupancies |
| B | 2 | Treatment occupancies |
| B | 3 | Care occupancies |
| C | — | Residential occupancies |
| D | — | Business and personal services occupancies |
| E | — | Mercantile occupancies |
| F | 1 | High-hazard industrial occupancies |
| F | 2 | Medium-hazard industrial occupancies |
| F | 3 | Low-hazard industrial occupancies |

3.1.2.2. Occupancies of Same Classification

1)   Any building is deemed to be occupied by a single major occupancy, notwithstanding its use for more than one major occupancy, provided that all occupancies are classified as belonging to the same Group classification or, where the Group is divided into Divisions, as belonging to the same Division classification described in Table 3.1.2.1.

3.1.2.3. Arena-Type Buildings

1)   An arena-type building intended for occasional use for trade shows and similar exhibition purposes shall be classified as a Group A, Division 3 occupancy. (See Note A-3.1.2.3.(1).)

3.1.2.4. Police Stations

1)   A police station with detention quarters is permitted to be classified as a Group B, Division 2 major occupancy provided the station is not more than 1 storey in building height and 600 m2 in building area.

3.1.2.5. Convalescent, Children's Custodial, and Residential Care Homes

1)   Convalescent homes and children's custodial homes are permitted to be classified as residential occupancies within the application of Part 3, provided that occupants are ambulatory and live as a single housekeeping unit in a suite with sleeping accommodation for not more than 10 persons.

2)   A care facility accepted for residential use pursuant to provincial legislation is permitted to be classified as a residential occupancy, provided

a)   occupants live as a single housekeeping unit in a dwelling unit with sleeping accommodation for not more than 10 persons,

b)   smoke alarms are installed in conformance with Article 3.2.4.20.,

c)   emergency lighting is provided in conformance with Subsection 3.2.7., and

d)   the building is sprinklered throughout.

3.1.2.6. Storage of Combustible Fibres

1)   Buildings or parts thereof used for the storage of baled combustible fibres shall be classified as medium-hazard industrial occupancies.

3.1.2.7. Group A, Division 2, Low Occupant Load

(See Note A-3.1.2.7.)

1)   A suite of Group A, Division 2 assembly occupancy, except a child or infant daycare facility, is permitted to be classified as a Group D, business and personal services occupancy provided

a)   the number of persons in the suite does not exceed 30, and

b)   except as permitted by Sentence (2), the suite is separated from the remainder of the building by a fire separation having a fire-resistance rating of not less than 1 hr.

2)    The fire separation required by Sentence (1) need not have a fire-resistance rating where the suite is located in a building that is sprinklered throughout.

3)   A permanent sign, with lettering not less than 50 mm high with a 12 mm stroke, indicating the lesser of the occupant load for the suite or 30 persons, shall be posted in a conspicuous location near the suite’s principal entrance.

3.1.2.8. Daycare Facilities for Children

(See Note A-3.1.2.8.)

1)   A daycare facility for children shall be classified as a Group A, Division 2 assembly occupancy. (See also Article 3.3.2.17.)

3.1.3. Multiple Occupancy Requirements

3.1.3.1. Separation of Major Occupancies

1)   Except as permitted by Sentences (2) and (3), major occupancies shall be separated from adjoining major occupancies by fire separations having fire-resistance ratings conforming to Table 3.1.3.1.

2)   In a building not more than 3 storeys in building height, if not more than two dwelling units are contained together with a Group E major occupancy, the fire-resistance rating of the fire separation between the two major occupancies need not be more than 1 h.

3)   In a building conforming to the requirements of Articles 3.2.8.2. to 3.2.8.8., the requirements of Sentence (1) for fire separations between major occupancies do not apply at the vertical plane around the perimeter of an opening through the horizontal fire separation.

Table 3.1.3.1.

Major Occupancy Fire Separations(1)

Forming Part of Sentence 3.1.3.1.(1)

| Major Occupancy | Minimum Fire-Resistance Rating of Fire Separation, h |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Adjoining Major Occupancy |  |  |  |  |  |  |  |  |  |  |  |  |
|  | A-1 | A-2 | A-3 | A-4 | B-1 | B-2 | B-3 | C | D | E | F-1 | F-2 | F-3 |
| A-1 | — | 1 | 1 | 1 | 2 | 2 | 2 | 1 | 1 | 2 | (2) | 2 | 1 |
| A-2 | 1 | — | 1 | 1 | 2 | 2 | 2 | 1(3) | 1(4) | 2 | (2) | 2 | 1 |
| A-3 | 1 | 1 | — | 1 | 2 | 2 | 2 | 1 | 1 | 2 | (2) | 2 | 1 |
| A-4 | 1 | 1 | 1 | — | 2 | 2 | 2 | 1 | 1 | 2 | (2) | 2 | 1 |
| B-1 | 2 | 2 | 2 | 2 | — | 2 | 2 | 2 | 2 | 2 | (2) | 2 | 2 |
| B-2 | 2 | 2 | 2 | 2 | 2 | — | 1 | 2 | 2 | 2 | (2) | 2 | 2 |
| B-3 | 2 | 2 | 2 | 2 | 2 | 1 | — | 1 | 2 | 2 | (2) | 2 | 2 |
| C | 1 | 1(3) | 1 | 1 | 2 | 2 | 1 | — | 1 | 2(5) | (2) | 2(6) | 1(7) |
| D | 1 | 1(4) | 1 | 1 | 2 | 2 | 2 | 1 | — | —(8) | 3 | —(8) | —(8) |
| E | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2(5) | —(8) | — | 3 | — | — |
| F-1 | (2) | (2) | (2) | (2) | (2) | (2) | (2) | (2) | 3 | 3 | — | 2 | 2 |
| F-2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2(6) | —(8) | — | 2 | — | — |
| F-3 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 1(7) | —(8) | — | 2 | — | — |

Notes to Table 3.1.3.1.:

(1) Section 3.3. contains requirements for the separation of occupancies and tenancies that are in addition to the requirements for the separation of major occupancies.

(2) See Sentence 3.1.3.2.(1).

(3) Where the building or part thereof is constructed in accordance with Article 3.2.2.48. or 3.2.2.51., a fire separation with a 2 h fire-resistance rating is required between the Group C and Group A, Division 2 major occupancies.

(4) Where the building or part thereof is constructed in accordance with Article 3.2.2.57. or 3.2.2.60., a fire separation with a 2 h fire-resistance rating is required between the Group D and Group A, Division 2 major occupancies.

(5) See Sentence 3.1.3.1.(2).

(6) See Sentence 3.1.3.2.(2).

(7) Where the building or part thereof is constructed in accordance with Article 3.2.2.48., a fire separation with a 2 h fire-resistance rating is required between the Group C major occupancy and a storage garage.

(8) Where the building or part thereof is constructed in accordance with Article 3.2.2.57., a fire separation with a 1 h fire-resistance rating is required between the Group D and Group E or Group F, Division 2 or 3 major occupancies.

3.1.3.2. Prohibition of Occupancy Combinations

1)   No major occupancy of Group F, Division 1 shall be contained within a building with any occupancy classified as Group A, B or C.

2)   Not more than one suite of residential occupancy shall be contained within a building classified as a Group F, Division 2 major occupancy.

3.1.4. Combustible Construction

3.1.4.1. Combustible Materials Permitted

1)   A building permitted to be of combustible construction is permitted to be constructed of combustible materials, with or without noncombustible components. (See Note A-3.1.4.1.(1).)

2)   The flame-spread rating on any exposed surface of foamed plastic insulation, and on any surface that would be exposed by cutting through the insulation in any direction, shall be not more than 500.

3.1.4.2. Protection of Foamed Plastics

(See Note A-3.1.4.2.)

1)   Except as permitted in Sentence (2), foamed plastics that form part of a wall or ceiling assembly in combustible construction shall be protected from adjacent spaces in the building, other than adjacent concealed spaces within attic or roof spaces, crawl spaces, and wall and ceiling assemblies,

a)   by one of the interior finishes described in Subsections 9.29.4. to 9.29.9.,

b)   provided the building does not contain a Group A, Group B or Group C major occupancy, by sheet metal

i)   mechanically fastened to the supporting assembly independent of the insulation,

ii)   not less than 0.38 mm thick, and

iii)   with a melting point not below 650°C, or

c)   by any thermal barrier that meets the requirements of Sentence 3.1.5.15.(2) (see Note A-3.1.4.2.(1)(c)).

(See Note A-3.1.4.2.(1).)

2)   A walk-in cooler or freezer consisting of factory-assembled wall, floor or ceiling panels containing foamed plastics is permitted in a building permitted to be of combustible construction, provided the panels

a)   are protected on both sides by sheet metal not less than 0.38 mm thick having a melting point not less than 650°C,

b)   do not contain an air space, and

c)   when a sample panel with an assembled joint typical of field installation is subjected to the applicable test described in Subsection 3.1.12., have a flame-spread rating not more than that permitted for the space in which they are located or the space that they bound, as applicable.

(See Note A-3.1.4.2.(2) and 3.1.5.7.(3).)

3)   The flame-spread rating of doors containing foamed plastics shall comply with Sentences 3.1.13.2.(1) to (3).

3.1.4.3. Wires and Cables

1)   Except as required by Sentence (2), optical fibre cables and electrical wires and cables with combustible insulation, jackets or sheathes that are installed in a building permitted to be of combustible construction shall

a)   not convey flame or continue to burn for more than 1 min when tested in conformance with the Vertical Flame Test (FT1 rating) in CSA C22.2 No. 0.3, “Test Methods for Electrical Wires and Cables,” or

b)   be located in

i)   totally enclosed noncombustible raceways (see Note A-3.1.4.3.(1)(b)(i)),

ii)   masonry walls,

iii)   concrete slabs, or

iv)   totally enclosed non-metallic raceways conforming to Clause 3.1.5.23.(1)(b).

(See Note A-3.1.4.3.(1).)

(See also Sentence 3.6.4.3.(1).)

2)   Except as permitted in Sentences (3) and (4), optical fibre cables and electrical wires and cables with combustible insulation, jackets or sheathes that are used for the transmission of voice, sound or data and are installed in a plenum in a building permitted to be of combustible construction shall exhibit the following characteristics when tested in conformance with CAN/ULC-S102.4, “Standard Method of Test for Fire and Smoke Characteristics of Electrical Wiring, Cables and Non-Metallic Raceways,” (FT6 rating):

a)   a horizontal flame distance of not more than 1.5 m,

b)   an average optical smoke density of not more than 0.15, and

c)   a peak optical smoke density of not more than 0.5.

3)   Except as permitted in Sentence (4), where totally enclosed noncombustible raceways are used in a plenum, exposed components of wiring systems with combustible insulation, jackets or sheathes, including optical fibre cables and electrical wires and cables that are used for the transmission of voice, sound or data, that are installed in the plenum or that extend not more than 9 m from the plenum, including drop down to the floor level, are permitted, provided they exhibit a vertical char of not more than 1.5 m when tested in conformance with the Vertical Flame Test – Cables in Cable Trays (FT4 rating) in CSA C22.2 No. 0.3, “Test Methods for Electrical Wires and Cables.”

4)   Cables or wires within plenums that are used for the transmission of signals in fire alarm systems need not comply with the requirements of Sentence (2).

3.1.4.4. Non-metallic Raceways

1)   Totally enclosed non-metallic raceways used in a plenum in a building permitted to be of combustible construction shall meet the requirements of Clause 3.1.5.23.(1)(a).

3.1.4.5. Fire-Retardant-Treated Wood

1)   If fire-retardant-treated wood is specified in this Part, the wood shall

a)   be pressure impregnated with fire-retardant chemicals in conformance with CAN/CSA-O80 Series, “Wood preservation,” and

b)   have a flame-spread rating not more than 25.

3.1.4.6. Heavy Timber Construction Alternative

1)   If combustible construction is permitted and is not required to have a fire-resistance rating more than 45 min, heavy timber construction is permitted to be used.

2)   If heavy timber construction is permitted, it shall conform to Article 3.1.4.7.

3.1.4.7. Heavy Timber Construction

1)   Wood elements in heavy timber construction shall be arranged in heavy solid masses and with essentially smooth flat surfaces to avoid thin sections and sharp projections.

2)   Except as permitted by Sentences (3) to (6) and (12), the minimum dimensions of wood elements in heavy timber construction shall conform to Table 3.1.4.7.

Table 3.1.4.7.

Heavy Timber Dimensions

Forming Part of Sentence 3.1.4.7.(2)

| Supported Assembly | Structural Element | Solid Sawn (width × depth), mm × mm | Glued-Laminated (width × depth), mm × mm | Round (diam), mm |
| --- | --- | --- | --- | --- |
| Roofs only | Columns | 140 × 191 | 130 × 190 | 180 |
|  | Arches supported on the tops of walls or abutments | 89 × 140 | 80 × 152 | — |
|  | Beams, girders and trusses | 89 × 140 | 80 × 152 | — |
|  | Arches supported at or near the floor line | 140 × 140 | 130 × 152 | — |
| Floors, floors plus roofs | Columns | 191 × 191 | 175 × 190 | 200 |
|  | Beams, girders, trusses and arches | 140 × 241 or | 130 × 228 or | — |
|  |  | 191 × 191 | 175 × 190 |  |

3)   Where splice plates are used at splices of roof arches supported on the tops of walls or abutments, roof trusses, roof beams and roof girders in heavy timber construction, they shall be not less than 64 mm thick.

4)   Floors in heavy timber construction shall be of glued-laminated or solid sawn plank not less than

a)   64 mm thick, splined or tongued and grooved, or

b)   38 mm wide and 89 mm deep set on edge and well spiked together.

5)   Floors in heavy timber construction shall be laid

a)   so that no continuous line of end joints will occur except at points of support, and covered with

i)   tongued and grooved flooring not less than 19 mm thick laid crosswise or diagonally, or

ii)   tongued and grooved phenolic-bonded plywood, strandboard or waferboard not less than 12.5 mm thick, and

b)   not closer than 15 mm to the walls to provide for expansion, with the gap covered at the top or bottom.

6)   Roofs in heavy timber construction shall be of tongued and grooved phenolic-bonded plywood, strandboard or waferboard not less than 28 mm thick, or glued-laminated or solid sawn plank that is

a)   not less than 38 mm thick, splined or tongued and grooved, or

b)   not less than 38 mm wide and 64 mm deep set on edge and laid so that no continuous line of end joints will occur except at the points of support.

7)   Wood columns in heavy timber construction shall be continuous or superimposed throughout all storeys.

8)   Superimposed wood columns in heavy timber construction shall be connected by

a)   reinforced concrete or metal caps with brackets,

b)   steel or iron caps with pintles and base plates, or

c)   timber splice plates fastened to the columns by metal connectors housed within the contact faces.

9)   Where beams and girders in heavy timber construction enter masonry, wall plates, boxes of the self-releasing type or hangers shall be used.

10)   Wood girders and beams in heavy timber construction shall be closely fitted to columns, and adjoining ends shall be connected by ties or caps to transfer horizontal loads across the joints.

11)   In heavy timber construction, intermediate wood beams used to support a floor shall be supported on top of the girders or on metal hangers into which the ends of the beams are closely fitted.

12)   Roof arches supported on the top of walls or abutments, roof trusses, roof beams and roof girders in heavy timber construction are permitted to be not less than 64 mm wide provided

a)   where two or more spaced members are used, the intervening spaces are

i)   blocked solidly throughout, or

ii)   tightly closed by a continuous wood cover plate not less than 38 mm thick secured to the underside of the members, or

b)   the underneath of the roof deck or sheathing is sprinklered.

3.1.4.8. Exterior Cladding

1)   Except as provided in Sentence (2), cladding on an exterior wall assembly of a building or part of a building conforming to Article 3.2.2.51. or 3.2.2.60. shall consist of

a)   noncombustible cladding, or

b)   except as provided in Sentence (4), a wall assembly that satisfies the criteria of Clause 3.1.5.5.(1)(b).

(See Note A-3.1.4.8.(1).) (See also Notes A-3.1.5.5.(1)(b)(i) and A-3.1.5.5.(1)(b)(ii).)

2)   For buildings described in Sentence (1), combustible cladding representing up to 10% of the cladding on the face of an exterior wall facing a street or access route shall be permitted, provided all portions of the combustible cladding are located not more than 15 m from a street or access route conforming to Article 3.2.5.6., measured horizontally from the face of the building.

3)   A wall assembly conforming to Clause (1)(b) that includes combustible cladding made of fire-retardant-treated wood shall be tested for fire exposure after the cladding has been subjected to the accelerated weathering test specified in ASTM D2898, “Standard Practice for Accelerated Weathering of Fire-Retardant-Treated Wood for Fire Testing.”

4)   Exterior wall assemblies constructed in accordance with Section D-6 of Appendix D are deemed to comply with Clause (1)(b).

5)   Cladding described in this Article must also comply with the requirements of Article 3.2.3.7.

3.1.5. Noncombustible Construction

3.1.5.1. Noncombustible Materials

(See Note A-3.1.4.1.(1).)

1)   Except as permitted by Sentences (2) to (4) and Articles 3.1.5.2. to 3.1.5.24., 3.1.13.4. and 3.2.2.16., a building or part of a building required to be of noncombustible construction shall be constructed with noncombustible materials. (See also Subsection 3.1.13. for the requirements regarding the flame-spread rating of interior finishes.)

2)   Notwithstanding the definition of noncombustible materials stated in Article 1.4.1.2. of Division A, a material is permitted to be used in noncombustible construction provided that, when tested in accordance with ULC-S135, “Standard Test Method for the Determination of Combustibility Parameters of Building Materials Using an Oxygen Consumption Calorimeter (Cone Calorimeter),” at a heat flux of 50 kW/m2,

a)   its average total heat release is not more than 3 MJ/m2,

b)   its average total smoke extinction area is not more than 1.0 m2, and

c)   the test duration is extended beyond the time stipulated in the referenced standard until it is clear that there is no further release of heat or smoke.

3)   If a material referred to in Sentence (2) consists of a number of discrete layers and testing reveals that the surface layer or layers protect the underlying layers such that complete combustion of the underlying layers does not occur, the test shall be repeated by removing the outer layers sequentially until all layers have been exposed during testing, or until complete combustion has occurred.

4)   The acceptance criteria for a material tested in accordance with Sentence (3) shall be based on the cumulative emissions from all layers, which must not exceed the criteria stated in Clauses (2)(a) and (b).

3.1.5.2. Minor Combustible Components

1)   The following minor combustible components are permitted in a building required to be of noncombustible construction:

a)   paint (see also Clause 3.1.13.1.(2)(b)),

b)   self-adhesive tapes, mastics and caulking materials, including foamed plastic air sealants, applied to provide a seal between the major components of exterior wall construction, (see also Article 3.6.4.3. for limits on the use of combustible materials in plenum spaces),

c)   firestops and fire blocks conforming to Sentence 3.1.9.1.(1) and Article 3.1.11.7.,

d)   tubing for pneumatic controls provided it has an outside diameter of not more than 10 mm,

e)   adhesives, vapour barriers and sheathing papers,

f)   electrical outlet and junction boxes,

g)   wood blocking intended for the attachment of window elements within exterior wall assemblies,

h)   wood blocking within wall assemblies intended for the attachment of handrails, fixtures, and similar items mounted on the surface of the wall, and

i)   similar minor components.

3.1.5.3. Combustible Roofing Materials

1)   Combustible roof covering that has an A, B, or C classification determined in conformance with Subsection 3.1.15. is permitted on a building required to be of noncombustible construction.

2)   Combustible roof sheathing and roof sheathing supports installed above a concrete deck are permitted on a building required to be of noncombustible construction provided

a)   the concrete deck is not less than 50 mm thick,

b)   the height of the roof space above the deck is not more than 1 m,

c)   the roof space is divided into compartments by fire blocks in conformance with Article 3.1.11.5.,

d)   openings through the concrete deck other than for noncombustible roof drains and plumbing piping are protected by masonry or concrete shafts

i)   constructed as fire separations having a fire-resistance rating not less than 1 h, and

ii)   extending from the concrete deck to not less than 150 mm above the adjacent roof sheathing,

e)   the perimeter of the roof is protected by a noncombustible parapet extending from the concrete deck to not less than 150 mm above the adjacent sheathing, and

f)   except as permitted by Clause (d), the roof space does not contain any building services.

3)   Combustible cant strips, roof curbs, nailing strips and similar components used in the installation of roofing are permitted on a building required to be of noncombustible construction.

4)   Wood nailer facings to parapets that are not more than 610 mm high are permitted on a building required to be of noncombustible construction, provided the facings and any roof membranes covering the facings are protected by sheet metal.

3.1.5.4. Combustible Windows, Glazing and Skylights

1)   Combustible skylight assemblies are permitted in a building required to be of noncombustible construction if the assemblies have a flame-spread rating not more than

a)   150 provided the assemblies

i)   have an individual area not more than 9 m2,

ii)   have an aggregate horizontal projected area of the openings through the ceiling not more than 25% of the area of the ceiling of the room or space in which they are located, and

iii)   are spaced not less than 2.5 m from adjacent assemblies and from required fire separations, or

b)   75 provided the assemblies

i)   have an individual area not more than 27 m2,

ii)   have an aggregate horizontal projected area of the openings through the ceiling not more than 33% of the area of the ceiling of the room or space in which they are located, and

iii)   are spaced not less than 1.2 m from adjacent assemblies and from required fire separations.

(See Note A-3.1.5.4.(1).)

2)   Combustible vertical glazing installed no higher than the second storey is permitted in a building required to be of noncombustible construction.

3)   Except as permitted by Sentence (4), the combustible vertical glazing permitted by Sentence (2) shall have a flame-spread rating not more than 75.

4)   The flame-spread rating of combustible glazing is permitted to be not more than 150 if the aggregate area of glazing is not more than 25% of the wall area of the storey in which it is located, and

a)   the glazing is installed in a building not more than 1 storey in building height,

b)   the glazing in the first storey is separated from the glazing in the second storey in accordance with the requirements of Article 3.2.3.17. for opening protection, or

c)   the building is sprinklered throughout.

5)   Combustible window sashes and frames are permitted in a building required to be of noncombustible construction, provided they are vertically non-contiguous between storeys.

3.1.5.5. Combustible Cladding on Exterior Walls

1)   Except as provided in Sentences (2) and (3), combustible cladding is permitted to be used on an exterior wall assembly in a building required to be of noncombustible construction, provided

a)   the building is

i)   not more than 3 storeys in building height, or

ii)   sprinklered throughout, and

b)   except as provided in Sentence (4), when tested in accordance with CAN/ULC-S134, “Standard Method of Fire Test of Exterior Wall Assemblies,” the wall assembly satisfies the following criteria for testing and conditions of acceptance (see Note A-3.1.5.5.(1)(b)):

i)   flaming on or in the wall assembly does not spread more than 5 m above the opening (see Note A-3.1.5.5.(1)(b)(i)), and

ii)   the heat flux during the flame exposure on the wall assembly is not more than 35 kW/m 2 measured at 3.5 m above the opening (see Note A-3.1.5.5.(1)(b)(ii)).

2)   Except as permitted by Articles 3.2.3.10. and 3.2.3.11., where the limiting distance in Tables 3.2.3.1.-B to 3.2.3.1.-E permits an area of unprotected openings of not more than 10% of the exposing building face, the construction requirements of Table 3.2.3.7. shall be met.

3)   A wall assembly permitted by Sentence (1) that includes combustible cladding of fire-retardant-treated wood shall be tested for fire exposure after the cladding has been subjected to an accelerated weathering test as specified in ASTM D2898, “Standard Practice for Accelerated Weathering of Fire-Retardant-Treated Wood for Fire Testing.”

4)   Exterior wall assemblies constructed in accordance with Section D-6 of Appendix D are deemed to comply with Clause (1)(b).

3.1.5.6. Combustible Components in Exterior Walls

1)   Combustible components, other than those permitted by Article 3.1.5.5. and Sentence 3.1.5.7.(2), are permitted to be used in an exterior wall assembly of a building required to be of noncombustible construction, provided

a)   the building is

i)   not more than 3 storeys in building height, or

ii)   sprinklered throughout, and

b)   the wall assembly

i)   except as provided in Sentence (2), satisfies the criteria of Clause 3.1.5.5.(1)(b), or

ii)   is protected by masonry or concrete cladding not less than 25 mm thick (see Note A-3.1.5.5.(1)(b)).

2)   Exterior wall assemblies constructed in accordance with Section D-6 of Appendix D are deemed to comply with Subclause (1)(b)(i).

3.1.5.7. Factory-Assembled Panels

1)   Except as provided in Sentence (2), factory-assembled wall and ceiling panels containing foamed plastic insulation with a flame-spread rating not more than 500 are permitted to be used in a building required to be of noncombustible construction, provided

a)   the building

i)   is sprinklered,

ii)   is not more than 18 m high, measured from grade to the underside of the roof, and

iii)   does not contain a Group A, Group B, or Group C major occupancy, and

b)   the panels

i)   do not contain an air space,

ii)   when tested in accordance with CAN/ULC-S138, “Standard Method of Test for Fire Growth of Insulated Building Panels in a Full-Scale Room Configuration,” meet the criteria defined therein, and

iii)   when a sample panel with an assembled joint typical of field installation is subjected to the applicable test described in Subsection 3.1.12., have a flame-spread rating not more than that permitted for the room or space that they bound.

2)   Factory-assembled exterior wall panels containing thermosetting foamed plastic insulation are permitted to be used in a building required to be of noncombustible construction, provided

a)   the building

i)   is not more than 18 m high, measured from grade to the underside of the roof, and

ii)   does not contain a Group B or Group C major occupancy, and

b)   the wall panels

i)   do not contain an air space,

ii)   are protected on both sides by sheet steel not less than 0.38 mm thick,

iii)   remain in place for not less than 10 min when tested in conformance with CAN/ULC-S101, “Standard Method of Fire Endurance Tests of Building Construction and Materials,” where the exposed surface includes typical vertical and horizontal joints, and

iv)   when a sample panel with an assembled joint typical of field installation is subjected to the applicable test described in Subsection 3.1.12., have a flame-spread rating not more than that permitted for the room or space that they bound.

3)   A walk-in cooler or freezer consisting of factory-assembled wall, floor or ceiling panels containing foamed plastic insulation with a flame-spread rating not more than 500 is permitted to be used in a building required to be of noncombustible construction, provided

a)   the building is sprinklered, and

b)   the panels

i)   are protected on both sides by sheet metal not less than 0.38 mm thick with a melting point not less than 650°C,

ii)   do not contain an air space,

iii)   when tested in accordance with CAN/ULC-S138, “Standard Method of Test for Fire Growth of Insulated Building Panels in a Full-Scale Room Configuration,” meet the criteria defined therein, and

iv)   when a sample panel with an assembled joint typical of field installation is subjected to the applicable test described in Subsection 3.1.12., have a flame-spread rating not more than that permitted for the space in which they are located or the space that they bound, as applicable.

(See Note A-3.1.4.2.(2) and 3.1.5.7.(3).)

3.1.5.8. Nailing Elements

1)   Wood nailing elements attached directly to or set into a continuous noncombustible backing for the attachment of interior finishes are permitted in a building required to be of noncombustible construction provided the concealed space created by the wood elements is not more than 50 mm thick.

3.1.5.9. Combustible Millwork

1)   Combustible millwork, including interior trim, doors and door frames, show windows together with their frames, aprons and backing, handrails, shelves, cabinets and counters, is permitted in a building required to be of noncombustible construction.

3.1.5.10. Combustible Flooring Elements

1)   Combustible stage flooring supported on noncombustible structural members is permitted in a building required to be of noncombustible construction.

2)   Wood members more than 50 mm but not more than 300 mm high applied directly to or set into a noncombustible floor slab are permitted for the construction of a raised platform in a building required to be of noncombustible construction provided the concealed spaces created are divided into compartments by fire blocks in conformance with Sentence 3.1.11.3.(2).

3)   The floor system for the raised platform referred to in Sentence (2) is permitted to include a combustible subfloor and combustible finished flooring.

4)   Combustible finished flooring is permitted in a building required to be of noncombustible construction.

3.1.5.11. Combustible Stairs in Dwelling Units

1)   Combustible stairs are permitted in a dwelling unit in a building required to be of noncombustible construction.

3.1.5.12. Combustible Interior Finishes

1)   Except as permitted in Sentences (2) and (3), combustible interior wall and ceiling finishes referred to in Clause 3.1.13.1.(2)(b) that are not more than 1 mm thick are permitted in a building required to be of noncombustible construction.

2)   Combustible interior wall finishes, other than foamed plastics, that are not more than 25 mm thick are permitted in a building required to be of noncombustible construction, provided they have a flame-spread rating not more than 150 on any exposed surface, or any surface that would be exposed by cutting through the material in any direction.

3)   Except as provided in Sentence (4), combustible interior ceiling finishes, other than foamed plastics, that are not more than 25 mm thick are permitted in a building required to be of noncombustible construction, provided they have a flame-spread rating not more than 25 on any exposed surface, or any surface that would be exposed by cutting through the material in any direction, except that not more than 10% of the ceiling area within each fire compartment is permitted to have a flame-spread rating not more than 150.

4)   Combustible interior ceiling finishes made of fire-retardant-treated wood are permitted in a building required to be of noncombustible construction, provided they are not more than 25 mm thick or are exposed fire-retardant-treated wood battens.

3.1.5.13. Gypsum Board

1)   Gypsum board with a tightly adhering paper covering not more than 1 mm thick is permitted in a building required to be of noncombustible construction provided the flame-spread rating on the surface is not more than 25.

3.1.5.14. Combustible Insulation

(See Notes A-3.1.4.2. and A-3.1.4.2.(1).)

1)   Foamed plastic insulation shall conform to Article 3.1.5.15.

2)   Combustible insulation with a flame-spread rating not more than 25 on any exposed surface, or any surface that would be exposed by cutting through the material in any direction, is permitted in a building required to be of noncombustible construction.

3)   Combustible insulation is permitted to be installed above roof decks, outside of foundation walls below ground level, and beneath concrete slabs-on-ground of buildings required to be of noncombustible construction.

4)   Except as provided in Sentences (5) and (6), combustible insulation with a flame-spread rating more than 25 but not more than 500 on any exposed surface, or any surface that would be exposed by cutting through the material in any direction, is permitted in a building required to be of noncombustible construction, provided the insulation is protected from adjacent space in the building, other than adjacent concealed spaces within wall assemblies, by a thermal barrier consisting of

a)   not less than 12.7 mm thick gypsum board mechanically fastened to a supporting assembly independent of the insulation,

b)   lath and plaster, mechanically fastened to a supporting assembly independent of the insulation,

c)   masonry, or

d)   concrete.

5)   Combustible insulation with a flame-spread rating more than 25 but not more than 500 on any exposed surface, or any surface that would be exposed by cutting through the material in any direction, is permitted in the exterior walls of a building required to be of noncombustible construction that is not sprinklered and is more than 18 m high, measured from grade to the underside of the roof, provided the insulation is protected from adjacent space in the building, other than adjacent concealed spaces within wall assemblies, by a thermal barrier consisting of

a)   gypsum board not less than 12.7 mm thick, mechanically fastened to a supporting assembly independent of the insulation and with all joints either backed or taped and filled,

b)   lath and plaster, mechanically fastened to a supporting assembly independent of the insulation,

c)   masonry or concrete not less than 25 mm thick, or

d)   any thermal barrier that, when tested in conformance with CAN/ULC-S101, “Standard Method of Fire Endurance Tests of Building Construction and Materials,” will not develop an average temperature rise more than 140°C or a maximum temperature rise more than 180°C at any point on its unexposed face within 10 min (see Note A-3.1.5.14.(5)(d)) (see also Article 3.2.3.7.).

6)   Combustible insulation with a flame-spread rating more than 25 but not more than 500 on any exposed surface, or any surface that would be exposed by cutting through the material in any direction, is permitted in the interior walls, within ceilings and within roof assemblies of a building required to be of noncombustible construction that is not sprinklered and is more than 18 m high, measured from grade to the underside of the roof, provided the insulation is protected from adjacent space in the building, other than adjacent concealed spaces within wall assemblies, by a thermal barrier consisting of

a)   Type X gypsum board not less than 15.9 mm thick, mechanically fastened to a supporting assembly independent of the insulation and with all joints either backed or taped and filled, conforming to

i)   ASTM C1177/C1177M, “Standard Specification for Glass Mat Gypsum Substrate for Use as Sheathing,”

ii)   ASTM C1178/C1178M, “Standard Specification for Coated Glass Mat Water-Resistant Gypsum Backing Panel,”

iii)   ASTM C1396/C1396M, “Standard Specification for Gypsum Board,”

iv)   ASTM C1658/C1658M, “Standard Specification for Glass Mat Gypsum Panels,” or

v)   CAN/CSA A82.27-M, “Gypsum Board,”

b)   non-loadbearing masonry or concrete not less than 50 mm thick,

c)   loadbearing masonry or concrete not less than 75 mm thick, or

d)   any thermal barrier that, when tested in conformance with CAN/ULC-S101, “Standard Method of Fire Endurance Tests of Building Construction and Materials,”

i)   does not develop an average temperature rise more than 140°C or a maximum temperature rise more than 180°C at any point on its unexposed face within 20 min, and

ii)   remains in place for not less than 40 min.

3.1.5.15. Foamed Plastic Insulation

(See Notes A-3.1.4.2. and A-3.1.4.2.(1).)

1)   Foamed plastic insulation is permitted to be installed above roof decks, outside of foundation walls below ground level, and beneath concrete slabs-on-ground of a building required to be of noncombustible construction.

2)   Except as provided in Sentences (3), (4) and 3.1.5.7.(1), foamed plastic insulation with a flame-spread rating not more than 500 on any exposed surface, or any surface that would be exposed by cutting through the material in any direction, is permitted in a building required to be of noncombustible construction, provided the insulation is protected from adjacent space in the building, other than adjacent concealed spaces within wall assemblies, by a thermal barrier consisting of

a)   not less than 12.7 mm thick gypsum board mechanically fastened to a supporting assembly independent of the insulation,

b)   lath and plaster, mechanically fastened to a supporting assembly independent of the insulation,

c)   masonry,

d)   concrete, or

e)   any thermal barrier that meets the requirements of classification B when tested in conformance with CAN/ULC-S124, “Standard Method of Test for the Evaluation of Protective Coverings for Foamed Plastic.”

3)   Foamed plastic insulation with a flame-spread rating more than 25 but not more than 500 on any exposed surface, or any surface that would be exposed by cutting through the material in any direction, is permitted in the exterior walls of a building required to be of noncombustible construction that is not sprinklered and is more than 18 m high, measured from grade to the underside of the roof, provided the insulation is protected from adjacent space in the building, other than adjacent concealed spaces within wall assemblies, by a thermal barrier consisting of

a)   gypsum board not less than 12.7 mm thick, mechanically fastened to a supporting assembly independent of the insulation and with all joints either backed or taped and filled,

b)   lath and plaster, mechanically fastened to a supporting assembly independent of the insulation,

c)   masonry or concrete not less than 25 mm thick, or

d)   any thermal barrier that, when tested in conformance with CAN/ULC-S101, “Standard Method of Fire Endurance Tests of Building Construction and Materials,” does not develop an average temperature rise more than 140°C or a maximum temperature rise more than 180°C at any point on its unexposed face within 10 min (see Note A-3.1.5.14.(5)(d)) (see also Article 3.2.3.7.).

4)   Foamed plastic insulation with a flame-spread rating more than 25 but not more than 500 on any exposed surface, or any surface that would be exposed by cutting through the material in any direction, is permitted in the interior walls, within ceilings and within roof assemblies of a building required to be of noncombustible construction that is not sprinklered and is more than 18 m high, measured from grade to the underside of the roof, provided the insulation is protected from adjacent space in the building, other than adjacent concealed spaces within wall assemblies, by a thermal barrier consisting of

a)   Type X gypsum board not less than 15.9 mm thick, mechanically fastened to a supporting assembly independent of the insulation and with all joints either backed or taped and filled, conforming to

i)   ASTM C1177/C1177M, “Standard Specification for Glass Mat Gypsum Substrate for Use as Sheathing,”

ii)   ASTM C1178/C1178M, “Standard Specification for Coated Glass Mat Water-Resistant Gypsum Backing Panel,”

iii)   ASTM C1396/C1396M, “Standard Specification for Gypsum Board,” or

iv)   CAN/CSA A82.27-M, “Gypsum Board,”

b)   non-loadbearing masonry or concrete not less than 50 mm thick,

c)   loadbearing masonry or concrete not less than 75 mm thick, or

d)   any thermal barrier that, when tested in conformance with CAN/ULC-S101, “Standard Method of Fire Endurance Tests of Building Construction and Materials,”

i)   does not develop an average temperature rise more than 140°C or a maximum temperature rise more than 180°C at any point on its unexposed face within 20 min, and

ii)   remains in place for not less than 40 min.

3.1.5.16. Combustible Elements in Partitions

1)   Except as permitted by Sentence (2), solid lumber partitions not less than 38 mm thick and wood framing in partitions located in a fire compartment not more than 600 m2 in area are permitted to be used in a building required to be of noncombustible construction in a floor area that is not sprinklered throughout provided the partitions

a)   are not required fire separations, and

b)   are not located in a care, treatment or detention occupancy.

2)   Partitions installed in a building of noncombustible construction are permitted to contain wood framing provided

a)   the building is not more than 3 storeys in building height,

b)   the partitions are not located in a care, treatment or detention occupancy, and

c)   the partitions are not installed as enclosures for exits or vertical service spaces.

3)   Solid lumber partitions not less than 38 mm thick and partitions that contain wood framing are permitted to be used in a building required to be of noncombustible construction provided

a)   the building is sprinklered throughout, and

b)   the partitions are not

i)   located in a care, treatment or detention occupancy,

ii)   installed as enclosures for exits or vertical service spaces, or

iii)   used to satisfy the requirements of Clause 3.2.8.1.(1)(a).

3.1.5.17. Storage Lockers in Residential Buildings

1)   Storage lockers in storage rooms are permitted to be constructed of wood in a building of residential occupancy required to be of noncombustible construction.

3.1.5.18. Combustible Ducts

1)   Except as required by Sentence 3.6.4.3.(1), combustible ducts, including plenums and duct connectors, are permitted to be used in a building required to be of noncombustible construction provided these ducts and duct connectors are used only in horizontal runs.

2)   Combustible duct linings, duct coverings, duct insulation, vibration isolation connectors, duct tape, pipe insulation and pipe coverings are permitted to be used in a building required to be of noncombustible construction provided they conform to the appropriate requirements of Subsection 3.6.5.

3)   In a building required to be of noncombustible construction, combustible ducts need not comply with the requirements of Sentences 3.6.5.1.(1) and (2) provided the ducts are

a)   part of a duct system conveying only ventilation air, and

b)   contained entirely within a dwelling unit.

3.1.5.19. Combustible Piping Materials

1)   Except as permitted by Clause 3.1.5.2.(1)(d) and Sentences (2) and (3), combustible piping and tubing and associated adhesives are permitted to be used in a building required to be of noncombustible construction provided that, except when concealed in a wall or concrete floor slab, they

a)   have a flame-spread rating not more than 25, and

b)   if used in a building described in Subsection 3.2.6., have a smoke developed classification not more than 50.

2)   Combustible sprinkler piping is permitted to be used within a sprinklered floor area in a building required to be of noncombustible construction. (See also Article 3.2.5.13.)

3)   Polypropylene pipes and fittings are permitted to be used for drain, waste and vent piping for the conveyance of highly corrosive materials and for piping used to distribute distilled or dialyzed water in laboratory and hospital facilities in a building required to be of noncombustible construction, provided

a)   the building is sprinklered throughout,

b)   the piping is not located in a vertical shaft, and

c)   piping that penetrates a fire separation is sealed at the penetration by a firestop that has an FT rating not less than the fire-resistance rating of the fire separation when subjected to the fire test method in CAN/ULC-S115, “Standard Method of Fire Tests of Firestop Systems,” with a pressure differential of 50 Pa between the exposed and unexposed sides, with the higher pressure on the exposed side.

3.1.5.20. Combustible Plumbing Fixtures

1)   Combustible plumbing fixtures, including wall and ceiling enclosures that form part of the plumbing fixture, are permitted in a building required to be of noncombustible construction provided they are constructed of material having a flame-spread rating and smoke developed classification not more than that permitted for the wall surface of the room or space in which they are installed.

3.1.5.21. Wires and Cables

1)   Except as required by Sentence (2) and Article 3.1.5.22., optical fibre cables and electrical wires and cables with combustible insulation, jackets or sheathes are permitted in a building required to be of noncombustible construction, provided

a)   the wires and cables exhibit a vertical char of not more than 1.5 m when tested in conformance with the Vertical Flame Test – Cables in Cable Trays (FT4 rating) in CSA C22.2 No. 0.3, “Test Methods for Electrical Wires and Cables,”

b)   the wires and cables are located in

i)   totally enclosed noncombustible raceways (see Note A-3.1.4.3.(1)(b)(i)),

ii)   masonry walls,

iii)   concrete slabs,

iv)   a service room separated from the remainder of the building by a fire separation having a fire-resistance rating not less than 1 h, or

v)   totally enclosed non-metallic raceways conforming to Clause 3.1.5.23.(1)(b), or

c)   the wires and cables are communication cables used at the service entry to a building and are not more than 3 m long.

(See Note A-3.1.5.21.(1).)

2)   Except as permitted in Sentences (3) and (4), optical fibre cables and electrical wires and cables with combustible insulation, jackets or sheathes that are used for the transmission of voice, sound or data and are not located in totally enclosed noncombustible raceways are permitted to be installed in a plenum in a building required to be of noncombustible construction, provided the wires and cables exhibit a horizontal flame distance of not more than 1.5 m, an average optical smoke density of not more than 0.15, and a peak optical smoke density of not more than 0.5 when tested in conformance with CAN/ULC-S102.4, “Standard Method of Test for Fire and Smoke Characteristics of Electrical Wiring, Cables and Non-Metallic Raceways,” (FT6 rating).

3)   Except as permitted in Sentence (4), where totally enclosed noncombustible raceways are used in a plenum, exposed components of wiring systems with combustible insulation, jackets or sheathes, including optical fibre cables and electrical wires and cables that are used for the transmission of voice, sound or data, that are installed in the plenum or that extend not more than 9 m from the plenum including drop down to the floor level, are permitted provided they exhibit a vertical char of not more than 1.5 m when tested in conformance with the Vertical Flame Test – Cables in Cable Trays (FT4 rating) in CSA C22.2 No. 0.3, “Test Methods for Electrical Wires and Cables.”

4)   Cables or wires within plenums that are used for the transmission of signals in fire alarm systems need not comply with the requirements of Sentences (2) and (3).

3.1.5.22. Combustible Travelling Cables for Elevators

1)   Combustible travelling cables are permitted on elevating devices in a building required to be of noncombustible construction.

3.1.5.23. Non-metallic Raceways

1)   Except as required in Sentence (2), subject to the limits on the size of elements that penetrate fire separations when complying with Article 3.1.9.2., within a fire compartment of a building required to be of noncombustible construction, totally enclosed non-metallic raceways not more than 175 mm in outside diameter, or of an equivalent rectangular area, are permitted to be used to enclose optical fibre cables and electrical wires and cables, provided

a)   where the wires and cables in the raceways meet or exceed the requirements of Clause 3.1.5.21.(1)(a), the non-metallic raceways meet the requirements for at least an FT4 rating in

i)   CAN/CSA-C22.2 No. 262, “Optical Fiber Cable and Communication Cable Raceway Systems,” or

ii)   CAN/ULC-S143, “Standard Method of Fire Tests for Non-Metallic Electrical and Optical Fibre Cable Raceway Systems,” and

b)   where the wires and cables in the raceways do not meet or exceed the requirements of Clause 3.1.5.21.(1)(a), the non-metallic raceways exhibit a vertical char of not more than 1.5 m when tested in conformance with the Vertical Flame Test (FT4) – Conduit or Tubing on Cable Tray in Clause 6.16 of CSA C22.2 No. 211.0, “General Requirements and Methods of Testing for Nonmetallic Conduit.”

2)   Totally enclosed non-metallic raceways used in a plenum in a building required to be of noncombustible construction shall exhibit a horizontal flame distance of not more than 1.5 m, an average optical smoke density of not more than 0.15, and a peak optical smoke density of not more than 0.5 when tested in conformance with CAN/ULC-S102.4, “Standard Method of Test for Fire and Smoke Characteristics of Electrical Wiring, Cables and Non-Metallic Raceways,” (FT6 rating).

3.1.5.24. Decorative Wood Cladding

1)   On buildings required to be of noncombustible construction, decorative wood cladding is permitted to be used on the exterior fascias and soffits of marquees or canopies on the building face of a storey having direct access to a street or access route, provided the wood cladding is fire-retardant-treated wood that has been conditioned in conformance with ASTM D2898, “Standard Practice for Accelerated Weathering of Fire-Retardant-Treated Wood for Fire Testing,” before being tested in accordance with CAN/ULC-S102, “Standard Method of Test for Surface Burning Characteristics of Building Materials and Assemblies.”

3.1.6. Encapsulated Mass Timber Construction

(See Note A-3.1.6.)

3.1.6.1. Scope

1)   Encapsulated mass timber construction permitted in this Part shall conform to this Subsection.

3.1.6.2. Materials Permitted

1)   Except as otherwise provided in this Part and Sentence 6.4.3.1.(1), materials used in a building or part of a building permitted to be of encapsulated mass timber construction shall conform to Subsection 3.1.5.

3.1.6.3. Structural Mass Timber Elements

(See Note A-3.1.6.3.)

1)   Except as otherwise provided in this Subsection and Articles 3.2.2.16. and 3.2.3.19., a building or part of a building permitted to be of encapsulated mass timber construction is permitted to include structural mass timber elements, including beams, columns, arches, and wall, floor and roof assemblies, provided they comply with Sentences (2) and (3).

2)   Structural mass timber elements referred to in Sentence (1) shall

a)   except as provided in Sentence (4), be arranged in heavy solid masses containing no concealed spaces,

b)   have essentially smooth flat surfaces with no thin sections or sharp projections, and

c)   except as provided in Sentence 3.1.6.17.(1), conform to the minimum dimensions stated in Table 3.1.6.3.

3)   Adhesives used in structural mass timber elements referred to in Sentence (1) that are constructed of cross‐laminated timber shall conform to the elevated temperature performance requirements in ANSI/APA PRG 320, “Standard for Performance-Rated Cross-Laminated Timber.”

4)   Concealed spaces are permitted within structural mass timber elements referred to in Sentence (2) and need not conform to Sentence 3.1.6.4.(1), provided the concealed spaces are

a)   sprinklered and divided into compartments by fire blocks in conformance with Subsection 3.1.11.,

b)   completely filled with rock or slag fibre insulation conforming to CAN/ULC-S702.1, “Standard for Mineral Fibre Thermal Insulation for Buildings, Part 1: Material Specification,” and having a density not less than 32 kg/m3,

c)   if horizontal, lined with not less than a single layer of 12.7 mm thick Type X gypsum board or noncombustible material providing an encapsulation rating of not less than 25 min, or

d)   if vertical, lined with not less than a single layer of 12.7 mm thick Type X gypsum board or noncombustible material providing an encapsulation rating of not less than 25 min and vertically divided into compartments by fire blocks in conformance with Subsection 3.1.11.

Table 3.1.6.3.

Minimum Dimensions of Structural Mass Timber Elements in Encapsulated Mass Timber Construction

Forming Part of Sentences 3.1.6.3.(2), 3.1.6.8.(1) and 3.1.6.17.(1)

| Structural Wood Elements | Minimum Thickness, mm | Minimum Width × Depth, mm × mm |
| --- | --- | --- |
| Walls that are fire separations or exterior walls (1-sided fire exposure) | 96 | — |
| Walls that require a fire-resistance rating, but are not fire separations (2-sided fire exposure) | 192 | — |
| Floors(1) and roofs (1-sided fire exposure) | 96 | — |
| Beams, columns and arches (2- or 3-sided fire exposure) | — | 192 × 192 |
| Beams, columns and arches (4-sided fire exposure) | — | 224 × 224 |

Notes to Table 3.1.6.3.:

(1) The minimum dimensions for floor assemblies are also applicable to mezzanines and exterior balconies.

3.1.6.4. Encapsulation of Mass Timber Elements

(See also Note A-3.1.6.3.)

1)   Except as provided in Sentences (3) to (6), 3.1.6.3.(4), 3.1.6.16.(2) and 3.1.6.17.(2), and Articles 3.1.6.7. and 3.1.6.12., the exposed surfaces of structural mass timber elements conforming to Article 3.1.6.3. shall be protected from adjacent spaces in the building, including adjacent concealed spaces within wall, floor and roof assemblies, by a material or assembly of materials conforming to Sentence (2) that provides an encapsulation rating of not less than 50 min. (See Note A-3.1.6.4.(1).)

2)   Except as provided in Sentence 3.1.6.11.(1), the material or assembly of materials referred to in Sentence (1) shall consist of

a)   gypsum board,

b)   gypsum concrete,

c)   noncombustible materials,

d)   materials that conform to Sentences 3.1.5.1.(2) to (4), or

e)   any combination of the materials listed in Clauses (a) to (d).

3)   Except as provided in Sentence (5), the exposed surfaces of mass timber beams, columns and arches within a suite or fire compartment need not be protected in accordance with Sentence (1), provided

a)   their aggregate surface area does not exceed 10% of the total wall area of the perimeter of the suite or fire compartment in which they are located, and

b)   the flame-spread rating on any exposed surface is not more than 150.

(See Note A-3.1.6.4.(3) to (6).)

4)   Except as provided in Sentences (5) and (6), the exposed surfaces of mass timber walls within a suite need not be protected in accordance with Sentence (1), provided

a)   each exposed surface faces the same direction, and

b)   the flame-spread rating on any exposed surface is not more than 150.

(See Notes A-3.1.6.4.(4) and A-3.1.6.4.(3) to (6).)

5)   The aggregate exposed surface area of mass timber elements within a suite permitted in Sentences (3) and (4) shall not exceed 35% of the total wall area of the perimeter of the suite. (See Note A-3.1.6.4.(3) to (6).)

6)   The exposed surfaces of mass timber ceilings within a suite need not be protected in accordance with Sentence (1), provided their aggregate area does not exceed

a)   10% of the total ceiling area of the suite, where the exposed surfaces have a flame-spread rating not more than 150, or

b)   25% of the total ceiling area of the suite, where

i)   the suite contains no mass timber walls with exposed surfaces, and

ii)   the exposed surfaces of the mass timber ceiling have a flame-spread rating not more than 75.

(See Note A-3.1.6.4.(3) to (6).)

3.1.6.5. Determination of Encapsulation Ratings

1)   Except as provided in Article 3.1.6.6., the rating of a material or assembly of materials that is required to have an encapsulation rating shall be determined on the basis of the results of tests conducted in conformance with CAN/ULC-S146, “Standard Method of Test for the Evaluation of Encapsulation Materials and Assemblies of Materials for the Protection of Structural Timber Elements.”

3.1.6.6. Encapsulation Materials

(See Note A-3.1.6.6.)

1)   Gypsum‐concrete topping and concrete not less than 38 mm thick are deemed to have an encapsulation rating of 50 min when installed on the upper side of a mass timber floor or roof assembly.

2)   Two layers of Type X gypsum board each not less than 12.7 mm thick are deemed to have an encapsulation rating of 50 min when installed on a mass timber element, provided they

a)   are fastened with a minimum of two rows of screws in each layer

i)    directly to the mass timber element with screws of sufficient length to penetrate not less than 20 mm into the mass timber element that are spaced not more than 400 mm o.c. and 20 mm to 38 mm from the boards' edges, or

ii)   to wood furring or resilient metal or steel furring channels not more than 25 mm thick spaced not more than 400 mm o.c. on the mass timber element,

b)   are installed with the joints in each layer staggered from those in the adjacent layer,

c)   are installed in conformance with ASTM C840, “Standard Specification for Application and Finishing of Gypsum Board,” except that their joints need not be taped and finished, and

d)   conform to

i)   ASTM C1396/C1396M, “Standard Specification for Gypsum Board,” or

ii)   CAN/CSA A82.27-M, “Gypsum Board.”

(See Note A-3.1.6.6.(2).)

3.1.6.7. Combustible Roofing Materials

1)   Wood roof sheathing and roof sheathing supports that do not conform to Articles 3.1.6.3. and 3.1.6.4. are permitted in a building or part of a building permitted to be of encapsulated mass timber construction, provided they are installed

a)   above a concrete deck in accordance with Sentence 3.1.5.3.(2), or

b)   above a deck of encapsulated mass timber construction, where

i)   said deck is permitted to be encapsulated between the roof sheathing supports by a material or assembly of materials conforming to Sentence 3.1.6.4.(2) that provides an encapsulation rating of not less than 50 min,

ii)   the height of the roof space is not more than 1 m,

iii)   the roof space is divided into compartments by fire blocks in conformance with Article 3.1.11.5.,

iv)   openings through the deck other than for noncombustible roof drains and plumbing piping are protected by shafts constructed as fire separations having a fire-resistance rating not less than 1 h that extend from the deck to not less than 150 mm above the adjacent sheathing, and

v)   except as permitted by Subclause (b)(iv), the roof space does not contain any building services.

2)   Combustible cant strips, roof curbs, nailing strips and similar components used in the installation of roofing are permitted on a building or part of a building permitted to be of encapsulated mass timber construction.

3)   Wood nailer facings to parapets that are not more than 610 mm high are permitted on a building or part of a building permitted to be of encapsulated mass timber construction, provided the facings and any roof membranes covering the facings are protected by sheet metal.

3.1.6.8. Combustible Window Sashes and Frames

1)   Combustible window sashes and frames are permitted in a building or part of a building permitted to be of encapsulated mass timber construction, provided

a)   each window in an exterior wall face is an individual unit separated from every other opening in the wall by noncombustible wall construction or mass timber wall construction conforming to the dimensions stated in Table 3.1.6.3.,

b)   windows in exterior walls in contiguous storeys are separated by not less than 1 m of noncombustible wall construction or mass timber wall construction conforming to the dimensions stated in Table 3.1.6.3., and

c)   the aggregate area of openings in an exterior wall face of a fire compartment is not more than 40% of the area of the wall face.

3.1.6.9. Exterior Cladding

1)   Except as provided in Sentences (2), (3) and (6), cladding on an exterior wall assembly of a building or part of a building permitted to be of encapsulated mass timber construction shall be noncombustible. (See Note A-3.1.6.9.(1) and (2).)

2)   Except as provided in Sentences (3) to (5), cladding on an exterior wall assembly of a building or part of a building permitted to be of encapsulated mass timber construction is permitted to consist of

a)   combustible cladding that

i)   is not contiguous over more than 4 storeys,

ii)   represents not more than 10% of the cladding on each exterior wall of each storey,

iii)   is not more than 1.2 m in width,

iv)   has a flame-spread rating not more than 75 on any exposed surface, or any surface that would be exposed by cutting through the material in any direction,

v)   is separated from other portions of combustible cladding on adjacent storeys by a horizontal distance of not less than 2.4 m, and

vi)   is separated from other portions of combustible cladding by a horizontal distance of not less than 1.2 m,

b)   combustible cladding that

i)   is not contiguous across adjacent storeys,

ii)   represents not more than 10% of the cladding on each exterior wall of each storey,

iii)   has a flame-spread rating not more than 75 on any exposed surface, or any surface that would be exposed by cutting through the material in any direction, and

iv)   is separated from other portions of combustible cladding on adjacent storeys by a horizontal distance of not less than 2.4 m,

c)   combustible cladding representing up to 100% of the cladding on exterior walls of the first storey, provided all portions of the cladding can be directly accessed and are located not more than 15 m from a street or access route conforming to Article 3.2.5.6., measured horizontally from the face of the building,

d)   except as provided in Sentence (4), a wall assembly that satisfies the criteria of Clause 3.1.5.5.(1)(b), or

e)   a combination of noncombustible cladding and the cladding described in Clauses (a) to (d).

(See Note A-3.1.6.9.(1) and (2).)

3)   The permitted area of combustible cladding in Clause (2)(a) or (b) shall not exceed 5% of the cladding on each exterior wall of each storey where the time from receipt of notification of a fire by the fire department until the arrival of the first fire department vehicle at the building exceeds 10 min in 10% or more of all fire department calls to the building. (See Note A-3.2.3.1.(8).)

4)   An exterior wall assembly constructed in conformance with Section D-6 of Appendix D is deemed to satisfy the criteria of Clause (2)(d).

5)   Except as provided in Article 3.2.3.10., where the limiting distance in Table 3.2.3.1.-D or 3.2.3.1.-E permits an area of unprotected openings of not more than 10% of the exposing building face, the construction requirements of Table 3.2.3.7. shall be met.

6)   A wall assembly conforming to Clause (2)(d) that includes combustible cladding made of fire-retardant-treated wood shall be tested for fire exposure after the cladding has been subjected to the accelerated weathering test specified in ASTM D2898, “Standard Practice for Accelerated Weathering of Fire-Retardant-Treated Wood for Fire Testing.”

7)   Where combustible cladding conforming to Clause (2)(a) or (b) on an exterior wall of a fire compartment is exposed to combustible cladding conforming to Clause (2)(a) or (b) on an exterior wall of the same fire compartment or of another fire compartment, and the planes of the two walls are parallel or at an angle less than 135° measured from the exterior of the building, the different portions of combustible cladding shall

a)   be separated by a horizontal distance of not less than 3 m, and

b)   not be contiguous over more than 2 storeys.

3.1.6.10. Combustible Components in Exterior Walls

1)   Except as provided in Sentence (2), combustible components, other than those permitted by Article 3.1.6.9., are permitted to be used in an exterior wall assembly of a building or part of a building permitted to be of encapsulated mass timber construction, provided the wall assembly meets the requirements of Clause 3.1.6.9.(2)(d).

2)   An exterior wall assembly constructed in conformance with Section D-6 of Appendix D is deemed to satisfy the criteria of Sentence (1).

3)   Non-loadbearing wood elements permitted in Article 3.1.5.6. need not conform to Article 3.1.6.3. in a building or part of a building permitted to be of encapsulated mass timber construction.

3.1.6.11. Nailing Elements

1)   Wood nailing elements are permitted to be used for the attachment of a material or assembly of materials used to provide an encapsulation rating in a building or part of a building permitted to be of encapsulated mass timber construction, provided the concealed space created by the wood nailing elements is not more than 25 mm deep.

2)   Except as permitted by Sentence 3.1.6.16.(2) and Article 3.1.6.6., wood nailing elements are permitted to be used for the attachment of interior finishes in a building or part of a building permitted to be of encapsulated mass timber construction, provided the concealed space created by the wood nailing elements is not more than 50 mm deep and

a)   exposed surfaces in the concealed space have a flame-spread rating not more than 25, or

b)   the concealed space is filled with noncombustible insulation.

3.1.6.12. Combustible Flooring Elements

1)   Wood members that are more than 50 mm but not more than 300 mm high are permitted to be used for the construction of a raised platform in a building or part of a building permitted to be of encapsulated mass timber construction, and they need not conform to Articles 3.1.6.3. and 3.1.6.4., provided

a)   the concealed spaces created by the wood members are divided into compartments by fire blocks in conformance with Sentence 3.1.11.3.(4), and

b)   the wood members are

i)   applied directly to or set into a noncombustible floor slab, or

ii)   applied directly to a mass timber floor assembly that conforms to the requirements of Article 3.1.6.3.

2)   The upper surface of the mass timber floor assembly referred to in Subclause (1)(b)(ii) is permitted to be encapsulated only between the wood members by a material or assembly of materials conforming to Sentences 3.1.6.4.(1) and (2).

3)   The floor system for the raised platform referred to in Sentence (1) is permitted to include a combustible subfloor and combustible finished flooring.

3.1.6.13. Combustible Stairs

1)   Wood stairs and landings conforming to the requirements for floor assemblies in Article 3.1.6.3. and Sentences 3.1.6.4.(1) and (2) are permitted in an exit stairwell in a building or part of a building permitted to be of encapsulated mass timber construction.

2)   Wood stairs in a suite in a building or part of a building permitted to be of encapsulated mass timber construction need not conform to Articles 3.1.6.3. and 3.1.6.4.

3.1.6.14. Combustible Interior Finishes

1)   Except as provided in Sentences (2) and (3), combustible interior wall and ceiling finishes referred to in Clause 3.1.13.1.(2)(b) that are not more than 1 mm thick are permitted in a building or part of a building permitted to be of encapsulated mass timber construction.

2)   Except as provided in Sentences 3.1.6.4.(3) and (4), combustible interior wall finishes, other than foamed plastics, that are not more than 25 mm thick are permitted in a building or part of a building permitted to be of encapsulated mass timber construction, provided they have a flame-spread rating not more than 150 on any exposed surface, or any surface that would be exposed by cutting through the material in any direction.

3)   Except as provided in Sentences (4) and 3.1.6.4.(3) and (6), combustible interior ceiling finishes, other than foamed plastics, that are not more than 25 mm thick are permitted in a building or part of a building permitted to be of encapsulated mass timber construction, provided they have a flame-spread rating not more than 25 on any exposed surface, or any surface that would be exposed by cutting through the material in any direction, except that not more than 10% of the ceiling area within each fire compartment is permitted to have a flame-spread rating not more than 150. (See Note A-3.1.11.3.(3).)

4)   Combustible interior ceiling finishes made of fire-retardant-treated wood are permitted in a building or part of a building permitted to be of encapsulated mass timber construction, provided they are not more than 25 mm thick or are exposed fire-retardant-treated wood battens.

3.1.6.15. Combustible Elements in Partitions

1)   Solid lumber partitions not less than 38 mm thick and partitions containing wood framing that do not conform to Article 3.1.6.3. are permitted in a building or part of a building permitted to be of encapsulated mass timber construction, provided the partitions are

a)   protected on each face with not less than

i)   a single layer of 12.7 mm thick Type X gypsum board, with all joints either backed or taped and filled, conforming to ASTM C1396/C1396M, “Standard Specification for Gypsum Board,” or CAN/CSA A82.27-M, “Gypsum Board,”

ii)   a single layer of 19 mm thick fire-retardant-treated wood, on solid lumber partitions, or

iii)   a single layer of 19 mm thick fire-retardant-treated wood, on partitions containing wood framing, where the wood stud cavities are filled with noncombustible insulation, and

b)   not installed as enclosures for exits or vertical service spaces.

3.1.6.16. Exposed Construction Materials and Components in Concealed Spaces

1)   Except as provided in Sentence (2) and Article 3.1.11.7., and except as otherwise provided in this Subsection, only construction materials and components permitted in noncombustible construction shall be permitted to have exposed surfaces in concealed spaces within floor, roof, and wall assemblies in a building or part of a building permitted to be of encapsulated mass timber construction.

2)   Exposed surfaces are permitted in a concealed space created by the attachment of a material or assembly of materials conforming to Sentence 3.1.6.4.(1), provided the concealed space is not more than 25 mm deep.

3.1.6.17. Penetration by Outlet Boxes

1)   The minimum dimensions stated in Table 3.1.6.3. need not apply at cutouts in vertical or horizontal structural mass timber elements where outlet boxes are installed in accordance with Article 3.1.9.3. (See also Note A-3.1.9.2.(1).)

2)   The exposed surfaces of the cutouts described in Sentence (1) need not be protected in accordance with Sentence 3.1.6.4.(1).

3)   Outlet boxes on opposite sides of a structural mass timber element having a fire-resistance rating shall be separated by a distance of not less than 600 mm.

3.1.7. Fire-Resistance Ratings

3.1.7.1. Determination of Ratings

1)   Except as permitted by Sentence (2) to (4), and Articles 3.1.7.2. and 3.6.3.5., the rating of a material, assembly of materials or a structural member that is required to have a fire-resistance rating, shall be determined on the basis of the results of tests conducted in conformance with CAN/ULC-S101, “Standard Method of Fire Endurance Tests of Building Construction and Materials.”

2)   A material, assembly of materials or a structural member is permitted to be assigned a fire-resistance rating on the basis of Appendix D.

3)   A ceiling assembly is permitted to be assigned a fire-resistance rating on the basis of Assembly Number R1 in Table A-9.10.3.1.-B.

4)   A ceiling membrane is permitted to be assigned a fire-resistance rating on the basis of Assembly Number M1 or M2 in Table A-9.10.3.1.-B.

3.1.7.2. Exception for Exterior Walls

1)   The limit on the rise of temperature on the unexposed surface of an assembly as required by the tests referred to in Sentence 3.1.7.1.(1) shall not apply to an exterior wall that has a limiting distance of 1.2 m or more, provided correction is made for radiation from the unexposed surface in accordance with Sentence 3.2.3.1.(9).

3.1.7.3. Exposure Conditions for Rating

1)   Floor, roof and ceiling assemblies shall be rated for exposure to fire on the underside.

2)   Firewalls and interior vertical fire separations shall be rated for exposure to fire on each side.

3)   Exterior walls shall be rated for exposure to fire from inside the building.

3.1.7.4. Minimum Fire-Resistance Rating

1)   The use of materials or assemblies having a greater fire-resistance rating than required shall impose no obligation to exceed in whole or in part the minimum fire-resistance ratings required by this Part.

3.1.7.5. Rating of Supporting Construction

1)   Except as permitted by Sentence (2) and by Articles 3.2.2.20. to 3.2.2.92. for mixed types of construction, all loadbearing walls, columns and arches in the storey immediately below a floor or roof assembly required to have a fire-resistance rating shall have a fire-resistance rating not less than that required for the supported floor or roof assembly.

2)   Loadbearing walls, columns and arches supporting a service room or service space need not conform to Sentence (1).

3)   Except as provided in Sentence (4) and except for noncombustible roof assemblies required by Clauses 3.2.2.51.(2)(c) and 3.2.2.60.(2)(c), if an assembly is required to be of noncombustible construction and have a fire-resistance rating, it shall be supported by noncombustible construction.

4)   Except for portions of a building constructed in accordance with Article 3.2.2.7. that are required to be of noncombustible construction, assemblies of noncombustible construction in buildings or portions of buildings permitted to be of encapsulated mass timber construction are permitted to be supported by encapsulated mass timber construction.

3.1.8. Fire Separations and Closures

3.1.8.1. General Requirements

1)   Any wall, partition or floor assembly required to be a fire separation shall

a)   except as permitted by Sentence (2), be constructed as a continuous element in conformance with Article 3.1.8.3., and

b)   as required in this Part, have a fire-resistance rating as specified (see Note A-3.1.8.1.(1)(b)) .

2)   Openings in a fire separation shall be protected with closures, shafts or other means in conformance with Articles 3.1.8.4. to 3.1.8.19. and Subsections 3.1.9. and 3.2.8. (See Note A-3.1.8.1.(2).)

3.1.8.2. Combustible Construction Support

1)   Combustible construction that abuts on or is supported by a noncombustible fire separation shall be constructed so that its collapse under fire conditions will not cause the collapse of the fire separation.

3.1.8.3. Continuity of Fire Separations

1)   Except as permitted by Sentence 3.6.4.2.(2), a horizontal service space or other concealed space located above a required vertical fire separation, including the walls of a vertical shaft, shall be divided at the fire separation by an equivalent fire separation within the service space.

2)   Except as provided in Sentence (5), the continuity of a fire separation having a fire-resistance rating that abuts another fire separation, a floor, a ceiling, or a roof shall be maintained by a firestop conforming to Sentence (3). (See Note A-3.1.8.3.(2).)

3)   The firestop required in Sentence (2) shall have an FT rating not less than the fire-resistance rating of the abutting fire separation when subjected to the fire test method in CAN/ULC-S115, “Standard Method of Fire Tests of Firestop Systems.”

4)   Except as provided in Sentence (5), joints located in a horizontal plane between a floor and an exterior wall shall be sealed by a firestop that, when subjected to the fire test method in ASTM E2307, “Standard Test Method for Determining Fire Resistance of Perimeter Fire Barriers Using Intermediate-Scale, Multi-storey Test Apparatus,” has an F rating not less than the fire-resistance rating of the horizontal fire separation.

5)   Joints between ceilings and walls, between floors and walls, and between walls at corners need not comply with Sentences (2) and (4) where such joints consist of gypsum board that is attached to framing members and arranged so as to restrict the passage of flame and smoke through the joints. (See Note A-3.1.8.3.(5).)

3.1.8.4. Determination of Ratings and Classifications

1)   Except as permitted by Sentences (2) and 3.1.8.16.(1), the fire-protection rating of a closure shall be determined in accordance with

a)   CAN/ULC-S104, “Standard Method for Fire Tests of Door Assemblies,”

b)   CAN/ULC-S106, “Standard Method for Fire Tests of Window and Glass Block Assemblies,” or

c)   CAN/ULC-S112, “Standard Method of Fire Test of Fire Damper Assemblies.”

(See Articles 3.1.8.17. to 3.1.8.19. for additional requirements for closures.)

2)   Except as permitted by Sentence 3.1.8.12.(1), the fire-protection rating of a closure shall conform to Table 3.1.8.4. for the required fire-resistance rating of the fire separation.

3)   The leakage rate of smoke dampers and combination smoke/fire dampers shall

a)   be determined in accordance with the applicable provisions in CAN/ULC-S112.1, “Standard for Leakage Rated Dampers for Use in Smoke Control Systems,” and

b)   conform to Class I, II or III of that standard.

4)   The leakage rate of a door assembly shall be determined in accordance with ANSI/UL 1784, “Standard for Air Leakage Tests of Door Assemblies and Other Opening Protectives.”

Table 3.1.8.4.

Fire-Protection Rating of Closures

Forming Part of Sentence 3.1.8.4.(2)

| Fire-Resistance Rating of Fire Separation | Minimum Fire-Protection Rating of Closure |
| --- | --- |
| 45 min | 45 min |
| 1 h | 45 min |
| 1.5 h | 1 h |
| 2 h | 1.5 h |
| 3 h | 2 h |
| 4 h | 3 h |

3.1.8.5. Installation of Closures

1)   Except where fire dampers, window assemblies and glass block are used as closures, closures of the same fire-protection rating installed on opposite sides of the same opening are deemed to have a fire-protection rating equal to the sum of the fire-protection ratings of the closures. (See Note A-3.1.8.1.(2).)

2)   Except as otherwise specified in this Part, every door, fire damper, window assembly or glass block used as a closure in a required fire separation shall be installed in conformance with NFPA 80, “Standard for Fire Doors and Other Opening Protectives.” (See Note A-3.1.8.1.(2).)

3)   Except as otherwise specified in this Part, every smoke damper or combination smoke/fire damper used as a closure in a required fire separation shall be installed in conformance with NFPA 105, “Standard for Smoke Door Assemblies and Other Opening Protectives.”

4)   If a door is installed such that it could damage the integrity of a fire separation if its swing is unrestricted, door stops shall be installed to prevent the damage.

5)   Protective guarding devices shall be

a)   provided where necessary to prevent damage to the mechanical components of doors in fire separations, and

b)   installed so as not to interfere with the proper operation of the doors.

6)   A leakage-rated door assembly complying with Sentence 3.1.8.4.(4) shall be installed in

a)   fire separations in protected floor areas referred to in Clause 3.3.1.7.(1)(b),

b)   fire separations in care or treatment occupancies referred to in Sentence 3.3.3.5.(4),

c)   except as provided in Sentence (8), fire separations of public corridors serving dwelling units in storeys that are not sprinklered, and

d)   firewalls that are a horizontal exit referred to in Sentence 3.3.3.5.(3).

7)   Leakage-rated door assemblies required by Sentence (6) shall be installed in accordance with NFPA 105, “Standard for Smoke Door Assemblies and Other Opening Protectives.”

8)   A leakage-rated door assembly need not be installed where a dwelling unit served by a public corridor has

a)   a second and separate means of egress, or

b)   an open-air balcony that is sized to accommodate the number of occupants for which the dwelling unit is intended.

3.1.8.6. Maximum Openings

1)   The size of an opening in an interior fire separation required to be protected with a closure shall be not more than 11 m2, with no dimension more than 3.7 m, if a fire compartment on either side of the fire separation is not sprinklered.

2)   The size of an opening in an interior fire separation required to be protected with a closure shall be not more than 22 m2, with no dimension more than 6 m, provided the fire compartments on both sides of the fire separation are sprinklered.

3.1.8.7. Location of Fire Dampers and Smoke Dampers

1)   Except as provided in Article 3.1.8.8., a fire damper having a fire-protection rating conforming to Sentence 3.1.8.4.(2) shall be installed in conformance with Article 3.1.8.10. in ducts or air-transfer openings that penetrate an assembly required to be a fire separation.

2)   Except as provided in Article 3.1.8.9., a smoke damper or a combination smoke/fire damper shall be installed in conformance with Article 3.1.8.11. in ducts or air-transfer openings that penetrate an assembly required to be a fire separation, where the fire separation

a)   separates a public corridor,

b)   contains an egress door referred to in Sentence 3.4.2.4.(2),

c)   serves an assembly, care, treatment, detention or residential occupancy, or

d)   is installed to meet the requirements of Clause 3.3.1.7.(1)(b) or Sentence 3.3.3.5.(4).

3.1.8.8. Fire Dampers Waived

1)   Except as provided in Sentence (2), the requirement for fire dampers stated in Sentence 3.1.8.7.(1) is permitted to be waived for

a)   ducts that serve commercial cooking equipment (see also Article 6.3.1.6.),

b)   continuous noncombustible ducts having a melting point above 760°C that penetrate a vertical fire separation required by Sentence 3.3.1.1.(1) between suites of assembly, mercantile, low-hazard industrial, medium-hazard industrial or high-hazard industrial occupancy,

c)   ducts or air-transfer openings that penetrate a vertical fire separation not required to have a fire-resistance rating, or

d)   noncombustible ducts or air-transfer openings that penetrate a horizontal fire separation not required to have a fire-resistance rating.

2)   The requirement for fire dampers stated in Sentence 3.1.8.7.(1) is permitted to be waived for noncombustible branch ducts having a melting point above 760°C that penetrate a fire separation,

a)   provided the ducts

i)   have a cross-sectional area not more than 0.013 m2 and serve only air-conditioning units or combined air-conditioning and heating units discharging air not more than 1.2 m above the floor, or

ii)   extend not less than 500 mm inside exhaust duct risers that are under negative pressure and in which the airflow is upward as required by Article 3.6.3.4., or

b)   where the fire separation separates a vertical service space from the remainder of the building, provided each individual duct exhausts directly to the outdoors at the top of the vertical service space.

3.1.8.9. Smoke Dampers Waived

1)   Except as provided in Sentence (2), the requirement for smoke dampers or combination smoke/fire dampers stated in Sentence 3.1.8.7.(2) is permitted to be waived for ducts

a)   that serve commercial cooking equipment (see also Article 6.3.1.6.),

b)   in which all inlet and outlet openings serve not more than one fire compartment, or

c)   that penetrate a vertical fire separation referred to in Clause 3.3.1.7.(1)(b) or in Sentence 3.3.3.5.(4), provided

i)   the movement of air is continuous, and

ii)   the configuration of the air-handling system prevents the recirculation of exhaust or return air under fire emergency conditions.

2)   The requirement for smoke dampers or combination smoke/fire dampers stated in Sentence 3.1.8.7.(2) is permitted to be waived for noncombustible branch ducts having a melting point above 760°C that penetrate a fire separation,

a)   provided the ducts

i)   have a cross-sectional area not more than 0.013 m2 and serve only air-conditioning units or combined air-conditioning and heating units discharging air not more than 1.2 m above the floor,

ii)   extend not less than 500 mm inside exhaust duct risers that are under negative pressure and in which the airflow is upward as required by Article 3.6.3.4., or

iii)   are required to function as part of a smoke control system, or

b)   where the fire separation separates a vertical service space from the remainder of the building, provided each individual duct exhausts directly to the outdoors at the top of the vertical service space.

3.1.8.10. Installation of Fire Dampers

1)   A fire damper shall be installed in the plane of the fire separation so as to stay in place should the duct become dislodged during a fire. (See Note A-3.1.8.10.(1).)

2)   A fire damper shall be arranged so as to close automatically upon the operation of a fusible link conforming to ULC-S505, “Standard for Fusible Links for Fire Protection Services,” or other heat-actuated or smoke-actuated device.

3)   A heat-actuated device referred to in Sentence (2) shall

a)   be located where it is readily affected by an abnormal rise in temperature in the duct, and

b)   have a temperature rating approximately 30°C above the maximum temperature that would exist in the system, whether it is in operation or shut down.

4)   A fire damper tested in the vertical or horizontal position shall be installed in the position in which it was tested.

5)   A tightly fitted access door shall be installed for each fire damper to provide access for the inspection of the damper and the resetting of the release device. (See Note A-3.1.8.10.(5).)

3.1.8.11. Installation of Smoke Dampers

1)   Where smoke dampers are used as a closure in an air-transfer opening, they shall be installed in the plane of the fire separation.

2)   Where combination smoke/fire dampers are used as a closure in a duct, they shall be installed within 610 mm of the plane of the fire separation, provided there is no inlet or outlet opening between the fire separation and the damper.

3)   Except as required by a smoke control system, smoke dampers and combination smoke/fire dampers shall be configured so as to close automatically upon a signal from an adjacent smoke detector located as described in CAN/ULC-S524, “Standard for Installation of Fire Alarm Systems,” within 1.5 m horizontally of the duct or air-transfer opening in the fire separation

a)   on both sides of the air-transfer opening, or

b)   in the duct downstream of the smoke damper or combination smoke/fire damper.

4)   Smoke dampers or combination smoke/fire dampers shall be installed in the vertical or horizontal position in which they were tested.

5)   A tightly fitted access door shall be installed for each smoke damper and combination smoke/fire damper to provide access for their inspection and the resetting of the release device. (See Note A-3.1.8.10.(5).)

3.1.8.12. Twenty-Minute Closures

1)   A door assembly having a fire-protection rating not less than 20 min is permitted to be used as a closure in

a)   a fire separation not required to have a fire-resistance rating more than 1 h, located between

i)   a public corridor and a suite,

ii)   a corridor and adjacent sleeping rooms, or

iii)   a corridor and adjacent classrooms, offices and libraries in Group A, Division 2 major occupancies, or

b)   a fire separation not required to have a fire-resistance rating more than 45 min, located in a building not more than 3 storeys in building height.

2)   The requirements for noncombustible sills and combustible floor coverings in NFPA 80, “Standard for Fire Doors and Other Opening Protectives,” do not apply to a door described in Sentence (1).

3)   A door described in Sentence (1) shall have clearances of not more than 6 mm at the bottom and not more than 3 mm at the sides and top.

3.1.8.13. Self-closing Devices

1)   Except as permitted by Sentence (2), every door in a fire separation, other than doors to freight elevators and dumbwaiters, shall be equipped with a self-closing device designed to return the door to the closed position after each use.

2)   A self-closing device need not be provided on a door that is located between

a)   a classroom and a corridor providing access to exit from the classroom in a building that is not more than 3 storeys in building height,

b)   a public corridor and an adjacent room of business and personal services occupancy in a building that is not more than 3 storeys in building height provided the door is not located in a dead-end portion of the corridor,

c)   a patients' sleeping room and a corridor serving the patients' sleeping room, provided the room and corridor are within a fire compartment in a hospital or nursing home with treatment that complies with the requirements of Article 3.3.3.5., or

d)   a patients' sleeping room and an adjacent room that serves the patients' sleeping room, provided these rooms are within a fire compartment in a hospital or nursing home with treatment that complies with the requirements of Article 3.3.3.5.

3.1.8.14. Hold-Open Devices

1)   Except as provided in Sentences 3.1.8.10.(2) and 3.1.8.11.(3), a hold-open device is permitted to be used on a closure in a required fire separation, other than on an exit stair door in a building more than 3 storeys in building height and on a door for a vestibule required by Article 3.3.5.7., provided the device is designed to release the closure in conformance with this Article.

2)   Except as provided in Sentences (5) and (6), where the building is provided with a fire alarm system, a hold-open device permitted by Sentence (1) shall release

a)   in a single-stage system, upon any signal from the fire alarm system, and

b)    in a 2-stage system,

i)   upon any alert signal from the fire alarm system, or

ii)   upon actuation of any adjacent smoke detectors.

3)   Where the building is provided with a fire alarm system, a hold-open device permitted by Sentence (1) shall release upon a signal from a smoke detector connected to the fire alarm system and located as described in CAN/ULC-S524, “Standard for Installation of Fire Alarm Systems,” where the hold-open device is used on

a)   an exit door,

b)   a door opening into a public corridor,

c)   an egress door referred to in Sentence 3.4.2.4.(2),

d)   a closure serving an assembly, care, treatment, detention, or residential occupancy,

e)   a door in a fire separation referred to in Clause 3.3.1.7.(1)(b) or Sentence 3.3.3.5.(4), or

f)   a door required to function as part of a smoke control system.

4)   Where the building is not provided with a fire alarm system, a hold-open device permitted by Sentence (1) shall release upon a signal from a smoke alarm located on each side of the fire separation at ceiling level within 1.5 m horizontally of the closure opening in the fire separation, where the hold-open device is used on closures described in Clauses (3)(a) to (e).

5)   Where a hold-open device is used on closures other than those described in Sentences (3) and (4), it is permitted to be released upon actuation of a heat-actuated device.

6)   A hold-open device used on a door located between a corridor used by the public and an adjacent sleeping room in a treatment occupancy need not release automatically as stated in Sentence (2).

3.1.8.15. Door Latches

1)   Except as permitted by Article 3.3.3.5., a swing-type door in a fire separation shall be equipped with a positive latching mechanism designed to hold the door in the closed position after each use.

3.1.8.16. Wired Glass and Glass Block

1)   Except as permitted by Articles 3.1.8.18. and 3.1.8.19. for the separation of exits, an opening in a fire separation having a fire-resistance rating not more than 1 h is permitted to be protected with fixed wired glass assemblies or glass blocks installed in conformance with NFPA 80, “Standard for Fire Doors and Other Opening Protectives.” (See also Article 3.3.2.17.)

2)   Wired glass assemblies permitted by Sentence (1) and described in Appendix D are permitted to be used as closures in vertical fire separations without being tested in accordance with Sentence 3.1.8.4.(1).

3)   Glass blocks permitted by Sentence (1) shall be installed in accordance with Subsection 4.3.2. and reinforced with steel reinforcement in each horizontal joint.

3.1.8.17. Temperature Rise Limit for Doors

1)   Except as permitted by Article 3.1.8.19., the maximum temperature rise on the opaque portion of the unexposed side of a door used as a closure in a fire separation in a location shown in Table 3.1.8.17. shall conform to the Table when tested in conformance with Sentence 3.1.8.4.(1).

Table 3.1.8.17.

Restrictions on Temperature Rise and Glazing for Closures

Forming Part of Articles 3.1.8.17. and 3.1.8.18.

| Location | Minimum Required Fire-Protection Rating of Door | Maximum Temperature Rise on Opaque Portion of Unexposed Side of Door, °C | Maximum Aggregate Area of Wired Glass or Safety Glazing in a Door, m2 | Maximum Aggregate Area of Glass Block, Wired Glass or Safety Glazing Panels Not in a Door, m2 |
| --- | --- | --- | --- | --- |
| Between a dead-end corridor and an adjacent occupancy where the corridor provides the only access to exit and is required to have a fire-resistance rating | Less than 45 min | No limit | No limit | No limit |
|  | 45 min | 250 after 30 min | 0.0645 | 0.0645 |
| Between an exit enclosure and the adjacent floor area in a building not more than 3 storeys in building height | All ratings | No limit | 0.8 | 0.8 |
| Between an exit enclosure and the adjacent floor area (except as permitted above) | 45 min | 250 after 30 min | 0.0645 | 0.0645 |
|  | 1.5 h | 250 after 1 h | 0.0645 | 0.0645 |
|  | 2 h | 250 after 1 h | 0.0645 | 0.0645 |
| In a firewall | 45 min | 250 after 30 min | 0.0645 | 0 |
|  | 1.5 h | 250 after 30 min | 0.0645 | 0 |
|  | 3 h | 250 after 1 h | 0 | 0 |

3.1.8.18. Area Limits for Wired Glass, Glass Block and Safety Glazing

1)   Except as permitted by Article 3.1.8.19., the maximum aggregate area of wired glass or safety glazing in a door used in the locations shown in Table 3.1.8.17. shall conform to the Table. (See Note A-3.1.8.18.(1).)

2)   Except as permitted by Article 3.1.8.19., the maximum aggregate area of glass block, wired glass or safety glazing panels not in a door used in the locations shown in Table 3.1.8.17. shall conform to the Table.

3.1.8.19. Temperature Rise and Area Limits Waived

1)   The temperature rise limits and glass area limits required by Articles 3.1.8.17. and 3.1.8.18. are waived for a closure between an exit enclosure and an enclosed vestibule or corridor, provided

a)   the vestibule or corridor is separated from the remainder of the floor area by a fire separation having a fire-resistance rating not less than 45 min,

b)   the fire separation required by Clause (a) contains no wired glass, glass block or safety glazing within 3 m of the closure into the exit enclosure, and

c)   the vestibule or corridor contains no occupancy.

(See Note A-3.1.8.19.(1).)

3.1.9. Penetrations in Fire Separations and Fire-Rated Assemblies

(See Note A-3.1.9.)

3.1.9.1. Firestops

1)   Except as provided in Sentences (2) to (7) and Article 3.1.9.3., penetrations of a fire separation or a membrane forming part of an assembly required to have a fire-resistance rating shall be

a)   sealed by a firestop that, when subjected to the fire test method in CAN/ULC-S115, “Standard Method of Fire Tests of Firestop Systems,” has an F rating not less than the required fire-resistance rating of the fire separation, or

b)   cast in place, where the item penetrating the fire separation is steel, ferrous, copper, concrete or masonry (see Note A-3.1.9.1.(1)(b)).

(See also Article 3.1.9.4. for requirements regarding penetrations by combustible drain, waste and vent piping.)

2)   Except as permitted in Sentence (6), penetrations of a firewall or a horizontal fire separation that is required to have a fire-resistance rating in conformance with Article 3.2.1.2. shall be sealed at the penetration by a firestop that, when subjected to the fire test method in CAN/ULC-S115, “Standard Method of Fire Tests of Firestop Systems,” has an FT rating not less than the fire-resistance rating for the fire separation.

3)   Except as permitted in Sentences (6) and (7), penetrations of a fire separation in conformance with Sentence 3.6.4.2.(2) shall be sealed by a firestop that, when subjected to the fire test method in CAN/ULC-S115, “Standard Method of Fire Tests of Firestop Systems,” has an FT rating not less than the fire-resistance rating for the fire separation of the assembly.

4)   Sprinklers are permitted to penetrate a fire separation or a membrane forming part of an assembly required to have a fire-resistance rating without having to meet the firestop requirements of Sentences (1) to (3), provided the annular space created by the penetration of a fire sprinkler is covered by a metal escutcheon plate in accordance with NFPA 13, “Standard for the Installation of Sprinkler Systems.”

5)   Unless specifically designed with a firestop, fire dampers are permitted to penetrate a fire separation or a membrane forming part of an assembly required to have a fire-resistance rating without having to meet the firestop requirements of Sentences (1) to (3), provided the fire damper is installed in conformance with NFPA 80, “Standard for Fire Doors and Other Opening Protectives.”

6)   Service equipment penetrations through a horizontal fire separation having a fire-resistance rating as described in Sentences (2) and (3) that are contained within the cavity of a wall above and below the horizontal fire separation are permitted to be sealed at the penetration by a firestop that, when subjected to the fire test method in CAN/ULC-S115, “Standard Method of Fire Tests of Firestop Systems,” has an F rating not less than the fire-resistance rating for the fire separation.

7)   Service equipment penetrations through a horizontal fire separation having a fire-resistance rating as described in Sentence (3) are permitted to be sealed at the penetration by a firestop that, when subjected to the fire test method in CAN/ULC-S115, “Standard Method of Fire Tests of Firestop Systems,” has an F rating not less than the fire-resistance rating for the fire separation, provided the penetration

a)   is contained within the concealed space of a floor or ceiling assembly having a fire-resistance rating,

b)   is located above a ceiling membrane that is a horizontal fire separation, or

c)   is contained within a horizontal service space conforming to Subsection 3.6.4. that is directly above or below the floor.

3.1.9.2. Service Equipment Penetrations

1)   Ducts, electrical outlet boxes, pipes, totally enclosed raceways, optical fibre cables, electrical wires and cables, and other similar service equipment are permitted to penetrate a fire separation or a membrane forming part of an assembly required to have a fire-resistance rating, provided they are protected at the penetration with a firestop conforming to Sentence 3.1.9.1.(1). (See Note A-3.1.9.2.(1).)

2)   Combustible totally enclosed raceways that are embedded in a concrete floor slab are permitted in an assembly required to have a fire-resistance rating, provided the concrete cover between the raceway and the bottom of the slab is not less than 50 mm.

3.1.9.3. Penetration by Outlet Boxes

(See Note A-3.1.9.3.) (See also Note A-3.1.9.2.(1).)

1)   Except as provided in Sentence (3), outlet boxes are permitted to penetrate the membrane of an assembly required to have a fire-resistance rating, provided they are sealed at the penetration by a firestop that has an FT rating not less than the fire-resistance rating of the fire separation when subjected to the fire test method in CAN/ULC-S115, “Standard Method of Fire Tests of Firestop Systems.”

2)   Combustible outlet boxes are permitted to penetrate the membrane of an assembly required to have a fire-resistance rating, provided they are sealed at the penetration by a firestop that, when subjected to the fire test method in CAN/ULC-S115, “Standard Method of Fire Tests of Firestop Systems,” has an FT rating not less than the fire-resistance rating for the fire separation.

3)   Except as provided in Sentences 3.1.9.1.(2) and (3), noncombustible outlet boxes that penetrate a vertical fire separation or a membrane forming part of an assembly required to have a fire-resistance rating need not conform to Sentence (1), provided

a)   they do not exceed

i)   0.016 m2 in area, and

ii)   an aggregate area of 0.065 m2 in any 9.3 m2 of surface area, and

b)   the annular space between the membrane and the noncombustible electrical outlet boxes does not exceed 3 mm.

4)   Outlet boxes on opposite sides of a vertical fire separation having a fire-resistance rating shall be separated by

a)   a horizontal distance of not less than 600 mm,

b)   a fire block conforming to Article 3.1.11.7., or

c)   a firestop installed on each outlet box that has an FT rating not less than the fire-resistance rating of the fire separation when subjected to the fire test method in CAN/ULC-S115, “Standard Method of Fire Tests of Firestop Systems.”

3.1.9.4. Combustible Piping Penetrations

1)   Combustible sprinkler piping is permitted to penetrate a fire separation provided the fire compartments on each side of the fire separation are sprinklered.

2)   Combustible water distribution piping is permitted to penetrate a fire separation that is required to have a fire-resistance rating, provided the piping is protected at the penetration with a firestop in conformance with Clause (4)(a) or (b).

3)   Except as permitted by Sentences (4), (5), (7) and (8), combustible piping shall not be used in a drain, waste and vent piping system if any part of that system penetrates

a)   a fire separation required to have a fire-resistance rating, or

b)   a membrane that forms part of an assembly required to have a fire-resistance rating.

4)   Combustible drain, waste and vent piping is permitted to penetrate a fire separation required to have a fire-resistance rating or a membrane that forms part of an assembly required to have a fire-resistance rating, provided

a)   except as provided in Clause (b), the piping is sealed at the penetration by a firestop that has an F rating not less than the fire-resistance rating required for the fire separation when subjected to the fire test method in CAN/ULC-S115, “Standard Method of Fire Tests of Firestop Systems,”

b)   in buildings more than 3 storeys in building height, the piping is sealed at the penetration by a firestop that has an F rating not less than the fire-resistance rating required for the fire separation when subjected to the fire test method in CAN/ULC-S115, “Standard Method of Fire Tests of Firestop Systems,” with a pressure differential of 50 Pa between the exposed and unexposed sides, with the higher pressure on the exposed side, and

c)   the piping is not located in a vertical service space.

5)   Combustible drain, waste and vent piping is permitted on one side of a vertical fire separation provided it is not located in a vertical service space.

6)   Combustible piping for central vacuum systems is permitted to penetrate a fire separation, provided the installation conforms to the requirements that apply to combustible drain, waste and vent piping specified in Sentence (4).

7)   Except as provided in Sentence (8), penetrations of a fire separation that incorporate transitions between combustible and noncombustible drain, waste and vent piping shall be sealed by a firestop that has an F rating not less than the fire-resistance rating required for the fire separation when subjected to the fire test method in CAN/ULC-S115, “Standard Method of Fire Tests of Firestop Systems,” with a pressure differential of 50 Pa between the exposed and unexposed sides, with the higher pressure on the exposed side.

8)   Transitions between vertical noncombustible drain, waste and vent piping and combustible branches for drain, waste and vent piping are permitted on either side of a fire separation, provided they are not located in a vertical service space. (See Note A-3.1.9.4.(8).)

3.1.9.5. Openings through a Membrane Ceiling

1)   A membrane ceiling forming part of an assembly assigned a fire-resistance rating on the basis of Appendix D is permitted to be penetrated by openings leading into ducts within the ceiling space, provided

a)   the ducts are sheet steel, and

b)   the number of openings and their protection conform to the requirements of Appendix D.

3.1.9.6. Plenums

1)   A ceiling assembly used as a plenum shall conform to Article 3.6.4.3.

3.1.10. Firewalls

3.1.10.1. Prevention of Firewall Collapse

1)   Except as permitted by Sentence (2), the connections and supports for structural framing members that are connected to or supported on a firewall and have a fire-resistance rating less than that required for the firewall, shall be designed so that the failure of the framing systems during a fire will not affect the integrity of the firewall during the fire.

2)   Sentence (1) does not apply to a firewall consisting of two separate wall assemblies each tied to its respective building frame but not to each other, provided each wall assembly is

a)   a fire separation having one half of the fire-resistance rating required for the firewall by Sentences 3.1.10.2.(1) and (2), and

b)   designed so that the collapse of one wall assembly will not cause collapse of the other.

3)   A firewall is permitted to be supported on the structural frame of a building of noncombustible construction provided the supporting frame has a fire-resistance rating not less than that required for the firewall.

4)   Piping, ducts and totally enclosed noncombustible raceways shall be installed so that their collapse will not cause collapse of the firewall.

3.1.10.2. Rating of Firewalls

1)   A firewall that separates a building or buildings with floor areas containing a Group E or a Group F, Division 1 or 2 major occupancy shall be constructed as a fire separation of noncombustible construction having a fire-resistance rating not less than 4 h, except that where the upper portion of a firewall separates floor areas containing other than Group E or Group F, Division 1 or 2 major occupancies, the fire-resistance rating of the upper portion of the firewall is permitted to be not less than 2 h.

2)   A firewall that separates a building or buildings with floor areas containing major occupancies other than Group E or Group F, Division 1 or 2 shall be constructed as a fire separation of noncombustible construction having a fire-resistance rating not less than 2 h.

3)   Except as permitted by Sentence (4), the required fire-resistance rating of a firewall, except for closures, shall be provided by masonry or concrete.

4)   A firewall permitted to have a fire-resistance rating not more than 2 h need not be constructed of masonry or concrete, provided

a)   the assembly providing the fire-resistance rating is protected against damage that would compromise the integrity of the assembly, and

b)   the design conforms to Article 4.1.5.17.

(See Note A-3.1.10.2.(4).)

3.1.10.3. Continuity of Firewalls

1)   A firewall shall extend from the ground continuously through, or adjacent to, all storeys of a building or buildings so separated, except that a firewall located above a basement storage garage conforming to Article 3.2.1.2. is permitted to commence at the floor assembly immediately above the storage garage. (See also Sentence 3.1.10.1.(3).)

2)   A firewall is permitted to terminate on the underside of a reinforced concrete roof slab, provided

a)   the roof slab on both sides of the firewall has a fire-resistance rating not less than

i)   1 h if the firewall is required to have a fire-resistance rating not less than 2 h, or

ii)   2 h if the firewall is required to have a fire-resistance rating not less than 4 h, and

b)   there are no concealed spaces within the roof slab in that portion immediately above the firewall.

3.1.10.4. Parapets

1)   Except as permitted by Sentences (2) and 3.1.10.3.(2), a firewall shall extend above the roof surface to form a parapet not less than

a)   150 mm high for a firewall required to have a fire-resistance rating not less than 2 h, and

b)   900 mm high for a firewall required to have a fire-resistance rating not less than 4 h.

2)   A firewall that separates 2 buildings with roofs at different elevations need not extend above the upper roof surface to form a parapet, provided the difference in elevation between the roofs is more than 3 m.

3.1.10.5. Maximum Openings

1)   Openings in a firewall shall conform to the size limits described in Article 3.1.8.6.

2)   The aggregate width of openings in a firewall within a storey shall be not more than 25% of the entire length of the firewall.

3.1.10.6. Exposure Protection for Adjacent Walls

1)   The requirements of Article 3.2.3.14. shall apply to the external walls of 2 buildings that meet at a firewall at an angle less than 135°.

3.1.10.7. Combustible Projections

1)   Combustible material shall not extend across the end of a firewall but is permitted to extend across a roof above a firewall that is terminated in conformance with Sentence 3.1.10.3.(2).

2)   If buildings are separated by a firewall, combustible projections on the exterior of one building, including balconies, platforms, canopies, eave projections and stairs, that extend outward beyond the end of the firewall, shall not be permitted within 2.4 m of combustible projections and window or door openings of the adjacent building. (See also Article 3.2.3.6.)

3.1.11. Fire Blocks in Concealed Spaces

3.1.11.1. Separation of Concealed Spaces

1)   Concealed spaces in interior wall, ceiling and crawl spaces shall be separated from concealed spaces in exterior walls and attic or roof spaces by fire blocks conforming to Article 3.1.11.7.

3.1.11.2. Fire Blocks in Wall Assemblies

1)   Except as permitted by Sentence (2), fire blocks conforming to Article 3.1.11.7. shall be provided to block off concealed spaces within a wall assembly

a)   at every floor level,

b)   at every ceiling level where the ceiling forms part of an assembly required to have a fire-resistance rating, and

c)   so that the maximum horizontal dimension is not more than 20 m and the maximum vertical dimension is not more than 3 m.

2)   Fire blocks conforming to Sentence (1) are not required, provided

a)   the wall space is filled with insulation,

b)   the exposed construction materials and any insulation within the wall space are noncombustible,

c)   the exposed materials within the space, including insulation but not including wiring, piping or similar services, have a flame-spread rating not more than 25 on any exposed surface, or any surface that would be exposed by cutting through the material in any direction, and fire blocks are installed so that the vertical distance between them is not more than 10 m, or

d)   the insulated wall assembly contains not more than one concealed air space, and the horizontal thickness of that air space is not more than 25 mm.

3.1.11.3. Fire Blocks between Nailing and Supporting Elements

1)   In a building required to be of noncombustible construction, a concealed space in which there is an exposed ceiling finish with a flame-spread rating more than 25 shall be provided with fire blocks conforming to Article 3.1.11.7. between wood nailing elements so that the maximum area of the concealed space is not more than 2 m2.

2)   In a building required to be of noncombustible construction, fire blocks conforming to Article 3.1.11.7. shall be provided in the concealed spaces created by the wood members permitted by Sentence 3.1.5.10.(2) so that the maximum area of a concealed space is not more than 10 m 2.

3)   In a building or part of a building permitted to be of encapsulated mass timber construction, a concealed space in which there is an exposed ceiling finish with a flame-spread rating more than 25 shall be provided with fire blocks conforming to Article 3.1.11.7. between wood nailing elements so that the maximum area of the concealed space is not more than 2 m2. (See Note A-3.1.11.3.(3).)

4)   In a building or part of a building permitted to be of encapsulated mass timber construction, fire blocks conforming to Article 3.1.11.7. shall be provided in the concealed spaces created by the wood members permitted by Sentence 3.1.6.12.(1) so that the maximum area of a concealed space is not more than 10 m2.

3.1.11.4. Fire Blocks between Vertical and Horizontal Spaces

1)   Fire blocks conforming to Article 3.1.11.7. shall be provided

a)   at all interconnections between concealed vertical and horizontal spaces in interior coved ceilings, drop ceilings and soffits in which the exposed construction materials within the space have a flame-spread rating more than 25, and

b)   at the end of each run and at each floor level in concealed spaces between stair stringers in which the exposed construction materials within the space have a flame-spread rating more than 25.

3.1.11.5. Fire Blocks in Horizontal Concealed Spaces

1)   Except for crawl spaces conforming to Sentence 3.1.11.6.(1) and as required in Sentence (3), horizontal concealed spaces within a floor assembly or roof assembly of combustible construction, in which sprinklers are not installed, shall be separated by construction conforming to Article 3.1.11.7. into compartments

a)   not more than 600 m2 in area with no dimension more than 60 m if the exposed construction materials within the space have a flame-spread rating not more than 25, and

b)   not more than 300 m2 in area with no dimension more than 20 m if the exposed construction materials within the space have a flame-spread rating more than 25.

(See Note A-3.1.11.5.(1).)

2)   A concealed space in an exterior cornice, a mansard-style roof, a balcony or a canopy in which exposed construction materials within the space have a flame-spread rating more than 25, shall be separated by construction conforming to Article 3.1.11.7.

a)   at locations where the concealed space extends across the ends of required vertical fire separations, and

b)   so that the maximum dimension in the concealed space is not more than 20 m.

3)   Except as provided in Sentence (5), in buildings or parts thereof conforming to Article 3.2.2.51. or 3.2.2.60., horizontal concealed spaces within a floor assembly or roof assembly of combustible construction shall be separated by construction conforming to Article 3.1.11.7. into compartments that are

a)   not more than 600 m2 in area with no dimension more than 60 m, if the exposed construction materials within the space have a flame-spread rating not more than 25, and

b)   not more than 300 m2 in area with no dimension more than 20 m, if the exposed construction materials within the space have a flame-spread rating more than 25.

(See Note A-3.1.11.5.(3) and (4).)

4)   Except for crawl spaces conforming to Sentence 3.1.11.6.(1) and except as provided in Sentence (5), in buildings or parts thereof conforming to Article 3.2.2.48. or 3.2.2.57., horizontal concealed spaces within a floor assembly or roof assembly of encapsulated mass timber construction shall be separated by construction conforming to Article 3.1.11.7. into compartments that are

a)   not more than 600 m2 in area with no dimension more than 60 m, if the exposed construction materials within the space have a flame-spread rating not more than 25, and

b)   not more than 300 m2 in area with no dimension more than 20 m, if the exposed construction materials within the space have a flame-spread rating more than 25.

(See Note A-3.1.11.5.(3) and (4).)

5)   Fire blocks conforming to Sentences (3) and (4) are not required where the horizontal concealed space within the floor or roof assembly is entirely filled with noncombustible insulation such that any air gap between the top of the insulation and the floor or roof deck does not exceed 50 mm.

3.1.11.6. Fire Blocks in Crawl Spaces

1)   A crawl space that is not considered as a basement by Article 3.2.2.9. and in which sprinklers are not installed shall be separated by construction conforming to Article 3.1.11.7. into compartments not more than 600 m2 in area with no dimension more than 30 m.

3.1.11.7. Fire Block Materials

1)   Except as permitted by Sentences (2) to (5) and (8), fire blocks shall remain in place and prevent the passage of flames for not less than 15 min when subjected to the standard fire exposure in CAN/ULC-S101, “Standard Method of Fire Endurance Tests of Building Construction and Materials.”

2)   Gypsum board not less than 12.7 mm thick and sheet steel not less than 0.38 mm thick need not be tested in conformance with Sentence (1), provided all joints have continuous support.

3)   In a building required to be of noncombustible construction, wood nailing elements described in Article 3.1.5.8. need not be tested in conformance with Sentence (1).

4)   In a building or part of a building permitted to be of encapsulated mass timber construction, wood nailing elements referred to in Article 3.1.6.11. need not be tested in conformance with Sentence (1).

5)   In a building permitted to be of combustible construction, in a combustible roof system permitted by Sentences 3.1.5.3.(2) and 3.1.6.7.(1), and in a raised platform permitted by Sentences 3.1.5.10.(2) and 3.1.6.12.(1), fire blocks are permitted to be

a)   solid lumber or a structural composite lumber product conforming to ASTM D5456, “Standard Specification for Evaluation of Structural Composite Lumber Products,” not less than 38 mm thick,

b)   phenolic bonded plywood, waferboard, or oriented strandboard not less than 12.5 mm thick with joints supported, or

c)   two thicknesses of lumber or a structural composite lumber product conforming to ASTM D5456, “Standard Specification for Evaluation of Structural Composite Lumber Products,” each not less than 19 mm thick with joints staggered, where the width or height of the concealed space requires more than one piece of lumber or structural composite lumber product not less than 38 mm thick to block off the space.

6)   Openings through materials referred to in Sentences (1) to (5) shall be protected to maintain the integrity of the construction.

7)   Where materials referred to in Sentences (1) to (5) are penetrated by construction elements or by service equipment, a firestop shall be used to seal the penetration. (See Note A-3.1.11.7.(7).)

8)   In buildings permitted to be of combustible construction, semi-rigid fibre insulation board produced from glass, rock or slag is permitted to be used to block the vertical space in a double stud wall assembly formed at the intersection of the floor assembly and the walls, provided the width of the vertical space does not exceed 25 mm and the insulation board

a)   has a density not less than 45 kg/m3,

b)   is securely fastened to one set of studs,

c)   extends from below the bottom of the top plates in the lower storey to above the top of the bottom plate in the upper storey, and

d)   completely fills the portion of the vertical space between the headers and between the wall plates.

(See Note A-3.1.11.7.(8).)

3.1.12. Flame-Spread Rating and Smoke Developed Classification

3.1.12.1. Determination of Ratings

1)   Except as required by Sentence (2) and as permitted by Sentence (3), the flame-spread rating and smoke developed classification of a material, assembly, or structural member shall be determined on the basis of not less than three tests conducted in conformance with CAN/ULC-S102, “Standard Method of Test for Surface Burning Characteristics of Building Materials and Assemblies.”

2)   The flame-spread rating and smoke developed classification of a material or assembly shall be determined on the basis of not less than three tests conducted in conformance with CAN/ULC-S102.2, “Standard Method of Test for Surface Burning Characteristics of Flooring, Floor Coverings, and Miscellaneous Materials and Assemblies,” if the material or assembly

a)   is designed for use in a relatively horizontal position with only its top surface exposed to air,

b)   cannot be tested in conformance with Sentence (1) without the use of supporting material that is not representative of the intended installation, or

c)   is thermoplastic.

3)   A material, assembly, or structural member is permitted to be assigned a flame-spread rating and smoke developed classification on the basis of Appendix D.

3.1.13. Interior Finish

3.1.13.1. Interior Finishes, Furnishings and Decorative Materials

1)   Except as otherwise provided by this Subsection, interior finishes, furnishings and decorative materials shall conform to Section 2.3. of Division B of the NFC.

2)   Interior finish material shall include any material that forms part of the interior surface of a floor, wall, partition or ceiling, including

a)   interior cladding of plaster, wood or tile,

b)   surfacing of fabric, paint, plastic, veneer or wallpaper,

c)   doors, windows and trim,

d)   lighting elements such as light diffusers and lenses forming part of the finished surface of the ceiling, and

e)   carpet material that overlies a floor that is not intended as the finished floor.

3.1.13.2. Flame-Spread Rating

1)   Except as otherwise required or permitted by this Subsection, the flame-spread rating of interior wall and ceiling finishes, including glazing and skylights, shall be not more than 150 and shall conform to Table 3.1.13.2.

Table 3.1.13.2.

Flame-Spread Ratings

Forming Part of Sentence 3.1.13.2.(1)

| Occupancy, Location or Element | Maximum Flame-Spread Rating for Walls and Ceilings |  |
| --- | --- | --- |
|  | Sprinklered | Not Sprinklered |
| Group A, Division 1 occupancies, including doors, skylights, glazing and light diffusers and lenses | 150 | 75 |
| Group B occupancies | 150 | 75 |
| Exits(1) | 25 | 25 |
| Lobbies described in Sentence 3.4.4.2.(2) | 25 | 25 |
| Covered vehicular passageways, except for roof assemblies of heavy timber construction in the passageways | 25 | 25 |
| Vertical service spaces | 25 | 25 |

Notes to Table 3.1.13.2.:

(1) See Articles 3.1.13.8. and 3.1.13.10.

2)   Except as permitted by Sentence (3), doors, other than those in Group A, Division 1 occupancies, need not conform to Sentence (1) provided they have a flame-spread rating not more than 200. (See Note A-3.1.13.2.(2).)

3)   Doors within a dwelling unit need not conform to Sentences (1) and (2).

4)   Up to 10% of the total wall area and 10% of the total ceiling area of a wall or ceiling finish that is required by Sentence (1) to have a flame-spread rating less than 150 is permitted to have a flame-spread rating not more than 150, except that up to 25% of the total wall area of lobbies described in Sentence 3.4.4.2.(2) is permitted to have a flame-spread rating not more than 150.

5)   Except in the case of Group A, Division 1 occupancies, combustible doors, skylights, glazing and light diffusers and lenses shall not be considered in the calculation of wall and ceiling areas described in Sentence (4).

3.1.13.3. Bathrooms in Residential Suites

1)   The flame-spread rating of interior wall and ceiling finishes for a bathroom within a suite of residential occupancy shall be not more than 200.

3.1.13.4. Light Diffusers and Lenses

1)   The flame-spread rating of combustible light diffusers and lenses in all occupancies other than Group A, Division 1 is permitted to be more than the flame-spread rating limits required elsewhere in this Subsection, provided the light diffusers and lenses

a)   have a flame-spread rating not more than 250 and a smoke developed classification not more than 600 when tested in conformance with CAN/ULC-S102.2, “Standard Method of Test for Surface Burning Characteristics of Flooring, Floor Coverings, and Miscellaneous Materials and Assemblies,”

b)   fall to the bottom of the test apparatus before igniting when tested in conformance with CAN/ULC-S102.3, “Standard Method of Fire Test of Light Diffusers and Lenses,”

c)   are not prevented from falling from the ceiling by construction located beneath the elements, and

d)   are not used in a corridor that is required to be separated from the remainder of the building by a fire separation or in an exit shaft unless individual diffusers or lenses are not more than 1 m2 in area and are not less than 1.2 m apart.

3.1.13.5. Skylights

1)   Individual combustible skylights in a corridor that is required to be separated from the remainder of the building by a fire separation shall be not more than 1 m2 in area and not less than 1.2 m apart.

3.1.13.6. Corridors

1)   Except as permitted by Sentences (2) and (3), the flame-spread rating shall be not more than 75 for the interior wall finish of

a)   a public corridor,

b)   a corridor used by the public in an assembly occupancy, or

c)   a corridor serving classrooms.

2)   The flame-spread rating for corridors specified in Sentence (1) is permitted to be waived, provided the flame-spread rating is not more than

a)   25 on the upper half of the wall, and

b)   150 on the lower half of the wall.

3)   Where the floor area is sprinklered throughout, the flame-spread ratings for corridors specified in Sentences (1) and (2) shall be not more than 150.

4)   The flame-spread ratings specified in Sentences (1), (2) and (3) apply to occupancies in the corridor as well as to the corridor itself.

5)   Except as provided in Sentence (6), the interior ceiling finish of corridors and occupancies referred to in Sentences (1) and (4) shall have a flame-spread rating not more than 25.

6)   Where the floor area is sprinklered throughout, the flame-spread rating of the interior ceiling finish of corridors and occupancies referred to in Sentences (1) and (4) shall be not more than 150.

3.1.13.7. High Buildings

1)   Except as permitted by Sentences (2) to (4), the interior wall, ceiling and floor finishes in a building regulated by the provisions of Subsection 3.2.6. shall conform to the flame-spread rating requirements in Articles 3.1.13.2. and 3.1.13.11. and to the flame-spread rating and smoke developed classification values in Table 3.1.13.7.

Table 3.1.13.7.

Flame-Spread Rating and Smoke Developed Classification in High Buildings

Forming Part of Sentence 3.1.13.7.(1)

| Location or Element | Maximum Flame-Spread Rating |  |  | Maximum Smoke Developed Classification |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | Wall Surface | Ceiling Surface(1) | Floor Surface | Wall Surface | Ceiling Surface(1) | Floor Surface |
| Exit stairways, vestibules to exit stairs and lobbies described in Sentence 3.4.4.2.(2) | 25 | 25 | 25 | 50 | 50 | 50 |
| Corridors not within suites | (2) | (2) | 300 | 100 | 50 | 500 |
| Elevator cars | 75 | 75 | 300 | 450 | 450 | 450 |
| Elevator vestibules | 25 | 25 | 300 | 100 | 100 | 300 |
| Service spaces and service rooms | 25 | 25 | 25 | 50 | 50 | 50 |
| Other locations and elements | (2) | (2) | No Limit | 300 | 50 | No Limit |

Notes to Table 3.1.13.7.:

(1) See Article 3.1.13.4. for lighting elements.

(2) Other requirements of this Part apply.

2)   Except for a building of Group B major occupancy and elevator cars, the flame-spread rating and smoke developed classification of interior wall, floor and ceiling finishes need not conform to the values in Table 3.1.13.7., provided the building is sprinklered.

3)   Trim and millwork in an exit stairway, a vestibule to an exit stairway, a lobby described in Sentence 3.4.4.2.(2), or a corridor not within a suite need not conform to the flame-spread rating and smoke developed classification requirements of Sentence (1) provided they have

a)   a flame-spread rating not more than 150,

b)   a smoke developed classification not more than 300, and

c)   an aggregate area not more than 10% of the area of the wall or ceiling on which they occur.

4)   A door serving an exit stairway, a vestibule to an exit stairway, a lobby described in Sentence 3.4.4.2.(2), or a corridor not within a suite need not conform to the flame-spread rating and smoke developed classification requirements of Sentence (1) provided

a)   it has a flame-spread rating not more than 200,

b)   it has a smoke developed classification not more than 300, and

c)   the aggregate area of all doors is not more than 10% of the area of the wall in which they are located.

3.1.13.8. Noncombustible Construction

1)   In a building required to be of noncombustible construction,

a)   the flame-spread ratings required by Subsection 3.1.5. shall apply in addition to the requirements in this Subsection, and

b)   the flame-spread ratings for exits in this Subsection shall also apply to any surface in the exit that would be exposed by cutting through the material in any direction, except that this requirement does not apply to doors, heavy timber construction in a sprinklered building and fire-retardant-treated wood.

3.1.13.9. Underground Walkways

1)   Except for paint, the interior wall and ceiling finishes of an underground walkway shall be of noncombustible materials.

3.1.13.10. Exterior Exit Passageway

1)   The wall and ceiling finishes of an exterior exit passageway that provides the only means of egress from the rooms or suites it serves, including the soffit beneath and the guard on the passageway, shall have a flame-spread rating not more than 25, except that a flame-spread rating not more than 150 is permitted for up to 10% of the total wall area and for up to 10% of the total ceiling area.

3.1.13.11. Elevator Cars

1)   The wall and ceiling surfaces of elevator cars shall have a flame-spread rating not more than 75.

2)   The wall, ceiling and floor surfaces of elevator cars shall have a smoke developed classification not more than 450.

3.1.13.12. Encapsulated Mass Timber Construction

1)   In a building or part of a building permitted to be of encapsulated mass timber construction,

a)   the flame-spread ratings required by Subsection 3.1.6. shall apply in addition to the requirements in this Subsection, and

b)   the flame-spread ratings for exits required by this Subsection shall also apply to any surface in the exit that would be exposed by cutting through the material in any direction, except that this requirement does not apply to doors, structural mass timber elements conforming to Sentence 3.1.6.4.(3), heavy timber construction, and fire-retardant-treated wood.

3.1.14. Roof Assemblies

3.1.14.1. Fire-Retardant-Treated Wood Roof Systems

1)   If a fire-retardant-treated wood roof system is used to comply with the requirements of Subsection 3.2.2., the roof deck assembly shall meet the conditions of acceptance of CAN/ULC-S126, “Standard Method of Test for Fire Spread Under Roof-Deck Assemblies.”

2)   Supports for the roof deck assembly referred to in Sentence (1) shall consist of

a)   fire-retardant-treated wood,

b)   heavy timber construction,

c)   noncombustible construction, or

d)   a combination thereof.

3.1.14.2. Metal Roof Deck Assemblies

1)   Except as permitted by Sentence (2), a metal roof deck assembly shall meet the conditions of acceptance of CAN/ULC-S126, “Standard Method of Test for Fire Spread Under Roof-Deck Assemblies,” if

a)   it supports a combustible material above the deck that could propagate a fire beneath the roof deck assembly, and

b)   the deck is used to comply with the requirements of Sentences 3.2.2.25.(2), 3.2.2.32.(2), 3.2.2.62.(2), 3.2.2.68.(2), 3.2.2.78.(2) and 3.2.2.85.(2) for noncombustible construction.

2)   The requirements of Sentence (1) are waived provided

a)   the combustible material above the roof deck is protected by not less than 12.7 mm thick gypsum board, mechanically fastened to a supporting assembly if located beneath the roof deck, or by a thermal barrier conforming to one of Clauses 3.1.5.15.(2)(c) to (e) that is located

i)   on the underside of the combustible material, or

ii)   beneath the roof deck,

b)   the building is sprinklered throughout, or

c)   the roof assembly has a fire-resistance rating not less than 45 min.

3.1.15. Roof Covering

3.1.15.1. Roof Covering Classification

1)   A roof covering classification shall be determined in conformance with CAN/ULC-S107, “Standard Methods of Fire Tests of Roof Coverings.”

3.1.15.2. Roof Coverings

1)   Except as provided in Sentences (2) to (4), every roof covering shall have a Class A, B or C classification as determined in accordance with Article 3.1.15.1.

2)   A roof covering is not required to have a Class A, B or C classification for

a)   a tent,

b)   an air-supported structure,

c)   a building of Group A, Division 2 occupancy not more than 2 storeys in building height and not more than 1 000 m2 in building area provided the roof covering is underlaid with noncombustible material, or

d)   a steel building system referred to in Article 4.3.4.3., provided the roof covering consists of brick, masonry, concrete, metal sheets or metal shingles.

3)   Except as provided in Sentence (5), roof coverings on buildings conforming to Article 3.2.2.51. or 3.2.2.60. shall have a Class A classification where the roof height is greater than 25 m measured from the floor of the first storey to the highest point of the roof.

4)   Except as provided in Sentence (5), roof coverings in buildings or parts of buildings permitted to be of encapsulated mass timber construction shall have a Class A classification where the roof height is greater than 25 m measured from the floor of the first storey to the highest point of the roof.

5)   Where buildings or parts thereof conforming to Article 3.2.2.48., 3.2.2.51., 3.2.2.57. or 3.2.2.60. include non-contiguous roof assemblies at different elevations, the roof coverings referred to in Sentences (3) and (4) are permitted to be evaluated separately to determine the roof covering classification required.

3.1.16. Fabrics

3.1.16.1. Fabric Canopies and Marquees

1)   Fabrics used as part of an awning, canopy or marquee that is located within or attached to a building of any type of construction shall conform to CAN/ULC-S109, “Standard Method for Flame Tests of Flame-Resistant Fabrics and Films.”

3.1.17. Occupant Load

3.1.17.1. Occupant Load Determination

1)   The occupant load of a floor area or part of a floor area shall be based on

a)   the number of seats in an assembly occupancy having fixed seats,

b)   2 persons per sleeping room in a dwelling unit, or

c)   the number of persons for which the area is designed, but not less than that determined from Table 3.1.17.1. for occupancies other than those described in Clauses (a) and (b), unless it can be shown that the area will be occupied by fewer persons.

2)   If a floor area or part thereof has been designed for an occupant load other than that determined from Table 3.1.17.1., a permanent sign indicating that occupant load shall be posted in a conspicuous location.

3)   For the purposes of this Article, mezzanines, tiers and balconies shall be regarded as part of the floor area.

4)   If a room or group of rooms is intended for different occupancies at different times, the value to be used from Table 3.1.17.1. shall be the value which gives the greatest number of persons for the occupancies concerned.

Table 3.1.17.1.

Occupant Load

Forming Part of Article 3.1.17.1.

| Type of Use of Floor Area or Part Thereof | Area per person, m2 |
| --- | --- |
| Assembly uses space with fixed seats | (1) |
| space with non-fixed seats | 0.75 |
| stages for theatrical performances | 0.75 |
| space with non-fixed seats and tables | 0.95 |
| standing space | 0.40 |
| stadia and grandstands | 0.60 |
| bowling alleys, pool and billiard rooms | 9.30 |
| classrooms | 1.85 |
| school shops and vocational rooms | 9.30 |
| reading or writing rooms or lounges | 1.85 |
| dining, beverage and cafeteria space | 1.20 |
| laboratories in schools | 4.60 |
| Care, treatment or detention uses suites | (2) |
| care, treatment and sleeping room areas | 10.00 |
| detention quarters | 11.60 |
| Residential uses dwelling units | (2) |
| dormitories | 4.60 |
| Business and personal services uses personal services shops | 4.60 |
| offices | 9.30 |
| Mercantile uses basements and first storeys | 3.70 |
| second storeys having a principal entrance from a pedestrian thoroughfare or a parking area | 3.70 |
| other storeys | 5.60 |
| Industrial uses manufacturing or process rooms | 4.60 |
| storage garages | 46.00 |
| storage spaces (warehouse) | 28.00 |
| aircraft hangars | 46.00 |
| Other uses cleaning and repair goods | 4.60 |
| kitchens | 9.30 |
| storage | 46.00 |
| public corridors intended for occupancies in addition to pedestrian travel | 3.70(3) |

Notes to Table 3.1.17.1.:

(1) See Clause 3.1.17.1.(1)(a).

(2) See Clause 3.1.17.1.(1)(b) (apply values for dwelling units to suites of care occupancy).

(3) See Note A-3.3.

3.1.18. Tents and Air-Supported Structures

(See Note A-3.1.18.)

3.1.18.1. Means of Egress

1)   Tents and air-supported structures shall conform to Sections 3.3. and 3.4.

3.1.18.2. Restrictions

1)   An air-supported structure shall not be located above the first storey on any building.

2)   An air-supported structure shall not be used for Groups B, C, or Group F, Division 1 major occupancies or for classrooms.

3)   An air-supported structure shall be designed as open floor space without interior walls, mezzanines, intermediate floors or similar construction.

3.1.18.3. Clearance to Other Structures

1)   Except as permitted by Sentences (2) to (4), every tent and air-supported structure shall conform to Subsection 3.2.3.

2)   Tents and air-supported structures

a)   shall not be erected closer than 3 m to other structures on the same property except as permitted by Sentences (3) and (4), and

b)   shall be sufficiently distant from one another to provide an area to be used as a means of emergency egress.

3)   Tents and air-supported structures not occupied by the public

a)   need not be separated from one another, and

b)   are permitted to be erected less than 3 m from other structures on the same property provided this spacing does not create a hazard to the public.

4)   Tents not more than 120 m2 in ground area, located on fair grounds or similar open spaces, need not be separated from one another provided this does not create a hazard to the public.

3.1.18.4. Clearance to Flammable Material

1)   The ground enclosed by a tent or air-supported structure and not less than 3 m of ground outside the structure shall be cleared of all flammable material or vegetation that will spread fire.

3.1.18.5. Flame Resistance

1)   Every tent and air-supported structure and all tarpaulins and decorative materials used in connection with these structures shall conform to CAN/ULC-S109, “Standard Method for Flame Tests of Flame-Resistant Fabrics and Films.”

3.1.18.6. Emergency Air Supply

1)   An air-supported structure used as a place of assembly for more than 200 persons shall have either

a)   an automatic emergency engine-generator set capable of powering one blower continuously for 4 h, or

b)   a supplementary blower powered by an automatic internal combustion engine.

3.1.18.7. Electrical Systems

1)   The electrical system and equipment in a tent or air-supported structure, including electrical fuses and switches, shall be inaccessible to the public.

2)   Cables on the ground in areas used by the public in a tent or air-supported structure shall be placed in trenches or protected by covers to prevent damage from traffic.

Section  3.2.   Building Fire Safety

3.2.1. General

3.2.1.1. Exceptions in Determining Building Height

1)   A rooftop enclosure shall not be considered as a storey in calculating the building height if it is provided for

a)   elevator machinery,

b)   a service room,

c)   a stairway used for no purpose other than for access or egress,

d)   an elevator lobby used for no purpose other than for access or egress, or

e)   a combination thereof.

2)   Space under tiers of seats in a building of the arena type shall not be considered as adding to the building height provided the space is used only for dressing rooms, concession stands and similar purposes incidental to the major occupancy of the building.

3)   Except as required by Sentence (5), the space above a mezzanine need not be considered as a storey in calculating the building height, provided

a)   the aggregate area of mezzanines that are not superimposed does not exceed 40% of the open area of the room in which they are located (see Note A-3.2.1.1.(3)(a)), and

b)   except as permitted in Sentences (7) and 3.3.2.13.(3), the space above the mezzanine is used as an open area without partitions or subdividing walls higher than 1 070 mm above the mezzanine floor.

4)   Except as required by Sentence (5), the space above a mezzanine need not be considered as a storey in calculating the building height, provided

a)   the aggregate area of mezzanines that are not superimposed and do not meet the conditions of Sentence (3) does not exceed 10% of the floor area in which they are located, and

b)   the area of a mezzanine in a suite does not exceed 10% of the area of that suite.

5)   Except as permitted by Sentence (6), each level of mezzanine that is partly or wholly superimposed above the first level of mezzanine shall be considered as a storey in calculating the building height.

6)   Platforms intended solely for periodic inspection and elevated maintenance catwalks need not be considered as floor assemblies or mezzanines for the purpose of calculating building height, provided

a)   they are not used for storage, and

b)   they are constructed with noncombustible materials, unless the building is permitted to be of combustible construction.

7)   The space above a mezzanine conforming to Sentence (3) is permitted to include an enclosed space whose area does not exceed 10% of the open area of the room in which the mezzanine is located provided the enclosed space does not obstruct visual communication between the open space above the mezzanine and the room in which it is located. (See Note A-3.2.1.1.(3)(a).)

8)   A service space in which facilities are included to permit a person to enter and to undertake maintenance and other operations pertaining to building services from within the service space need not be considered a storey if it conforms to Articles 3.2.5.14. and 3.3.1.25., and Sentences 3.2.4.18.(11), 3.2.7.3.(2), 3.3.1.3.(7), 3.4.2.4.(3) and 3.4.4.4.(9). (See Note A-3.2.1.1.(8).)

3.2.1.2. Storage Garage Considered as a Separate Building

1)   A basement used primarily as a storage garage is permitted to be considered as a separate building for the purposes of Subsection 3.2.2. and Sentences 3.2.5.12.(2) and (3), provided the floor and roof assemblies above the basement and the exterior walls of the basement above the adjoining ground level are constructed as fire separations of noncombustible construction having a fire-resistance rating not less than 2 h and protected in conformance with Clause 3.1.10.2.(4)(a), except as permitted by Sentence (2). (See Notes A-3.1.10.2.(4) and A-3.2.5.12.(2).)

2)   The exterior wall of a basement that is required to be a fire separation with a fire-resistance rating in accordance with Sentence (1) is permitted to be penetrated by openings that are not protected by closures provided

a)   the storage garage is sprinklered throughout,

b)   every opening in the exterior wall is separated from storeys above the opening by a projection of the floor or roof assembly above the basement, extending not less than

i)   1 m beyond the exterior face of the storage garage if the upper storeys are required to be of noncombustible construction, or

ii)   2 m beyond the exterior face of the storage garage if the upper storeys are permitted to be of combustible construction or encapsulated mass timber construction, or

c)   the exterior walls of any storeys located above the floor or roof assembly referred to in Sentence (1) are recessed behind the outer edge of the assembly by not less than

i)   1 m if the upper storeys are required to be of noncombustible construction, or

ii)   2 m if the upper storeys are permitted to be of combustible construction or encapsulated mass timber construction.

3)   The floor or roof assembly projection referred to in Clause (2)(b) shall have a fire-resistance rating not less than 2 h and shall have no openings within the projection.

3.2.1.3. Roof Considered as a Wall

1)   For the purposes of this Section any part of a roof that is pitched at an angle of 60° or more to the horizontal and is adjacent to a space intended for occupancy within a building shall be considered as part of an exterior wall of the building.

3.2.1.4. Floor Assembly over Basement

1)   Except as permitted by Sentence 3.2.2.47.(3), 3.2.2.49.(3), 3.2.2.50.(3), 3.2.2.52.(3), 3.2.2.53.(3), 3.2.2.54.(3) or 3.2.2.55.(3), a floor assembly immediately above a basement shall be constructed as a fire separation having a fire-resistance rating conforming to the requirements of Articles 3.2.2.20. to 3.2.2.92. for a floor assembly, but not less than 45 min.

2)   All loadbearing walls, columns and arches supporting a floor assembly immediately above a basement shall have a fire-resistance rating not less than that required by Sentence (1) for the floor assembly.

3.2.1.5. Fire Containment in Basements

1)   Except as permitted by Sentences (2) and 3.2.2.15.(3), in a building in which an automatic sprinkler system is not required to be installed by Article 3.2.2.18., every basement shall

a)   be sprinklered throughout, or

b)   be subdivided into fire compartments not more than 600 m2 in area by a fire separation having a fire-resistance rating not less than that required for the floor assembly immediately above the basement.

2)   An open-air storey need not conform to Sentence (1).

3.2.1.6. Mezzanines

1)   The floor assembly of a mezzanine that is required to be considered as a storey in calculating the building height shall be constructed in conformance with the fire separation requirements for floor assemblies stated in Articles 3.2.2.20. to 3.2.2.92.

3.2.2. Building Size and Construction Relative to Occupancy

3.2.2.1. Application

1)   Except as permitted by Article 3.2.2.3., a building shall be constructed in conformance with this Subsection to prevent fire spread and collapse caused by the effects of fire. (See Subsection 3.1.3. for fire separations between major occupancies.)

3.2.2.2. Special and Unusual Structures

1)   A structure that cannot be identified with the characteristics of a building in Articles 3.2.2.20. to 3.2.2.92. shall be protected against fire spread and collapse in conformance with good fire protection engineering practice. (See Note A-3.2.2.2.(1).) (See also Notes A-3 and A-3.2.5.12.(1).)

3.2.2.3. Exceptions to Structural Fire Protection

1)   Fire protection is not required for

a)   steel lintels above openings not more than 2 m wide in loadbearing walls and not more than 3 m wide in non-loadbearing walls,

b)   steel lintels above openings more than 2 m wide in loadbearing walls and more than 3 m wide in non-loadbearing walls provided the lintels are supported at intervals of not more than 2 m by structural members with the required fire-resistance rating,

c)   the bottom flanges of shelf angles and plates that are not a part of the structural frame,

d)   steel members for framework around elevator hoistway doorways, steel for the support of elevator and dumbwaiter guides, counterweights and other similar equipment, that are entirely enclosed in a hoistway and are not a part of the structural frame of the building,

e)   steel members of stairways and escalators that are not a part of the structural frame of a building,

f)   steel members of porches, exterior balconies, exterior stairways, fire escapes, cornices, marquees and other similar appurtenances, provided they are outside an exterior wall of a building, and

g)   loadbearing steel or concrete members wholly or partly outside a building face in a building not more than 4 storeys in building height and classified as Group A, B, C, D or F, Division 3 major occupancy provided the members are

i)   not less than 1 m away from any unprotected opening in an exterior wall, or

ii)   shielded from heat radiation in the event of a fire within the building by construction that will provide the same degree of protection that would be necessary if the member was located inside the building, with the protection extending on either side of the member a distance equal to the projection of the member from the face of the wall.

(See also Article 3.2.3.9.)

3.2.2.4. Buildings with Multiple Major Occupancies

1)   The requirements restricting fire spread and collapse for a building of a single major occupancy classification are provided in this Subsection according to its building height and building area.

2)   If a building contains more than one major occupancy, classified in more than one Group or Division, the requirements of this Subsection concerning building size and construction relative to major occupancy shall apply according to Articles 3.2.2.5. to 3.2.2.8.

3.2.2.5. Applicable Building Height and Area

1)   In determining the fire safety requirements of a building in relation to each of the major occupancies contained therein, the building height and building area of the entire building shall be used.

3.2.2.6. Multiple Major Occupancies

1)   Except as permitted by Articles 3.2.2.7. and 3.2.2.8., and Sentences 3.2.2.48.(4), 3.2.2.51.(5), 3.2.2.57.(3) and 3.2.2.60.(4), in a building containing more than one major occupancy, the requirements of this Subsection for the most restricted major occupancy contained shall apply to the whole building.

3.2.2.7. Superimposed Major Occupancies

1)   Except as provided in Article 3.2.2.8. and Sentences 3.2.2.18.(2), 3.2.2.48.(4), 3.2.2.51.(5), 3.2.2.57.(3) and 3.2.2.60.(4), in a building in which one major occupancy is located entirely above another major occupancy, the requirements in this Subsection for each portion of the building containing a major occupancy shall apply to that portion as if the entire building were of that major occupancy.

2)   If one major occupancy is located above another major occupancy, the fire-resistance rating of the floor assembly between the major occupancies shall be determined on the basis of the requirements of this Subsection for the lower major occupancy. (See also Article 3.1.3.1.)

3.2.2.8. Exceptions for Major Occupancies

1)   In a building in which the aggregate area of all major occupancies in a particular Group or Division is not more than 10% of the floor area of the storey in which they are located, these major occupancies need not be considered as major occupancies for the purposes of this Subsection, provided they are not classified as Group F, Division 1 or 2 occupancies.

3.2.2.9. Crawl Spaces

1)   For the purposes of Articles 3.1.11.6., 3.2.1.4. and 3.2.1.5., a crawl space shall be considered as a basement if it is

a)   more than 1.8 m high between the lowest part of the floor assembly and the ground or other surface below,

b)   used for any occupancy,

c)   used for the passage of flue pipes, or

d)   used as a plenum in combustible construction.

2)   A floor assembly immediately above a crawl space is not required to be constructed as a fire separation and is not required to have a fire-resistance rating provided the crawl space is not required to be considered as a basement by Sentence (1).

3.2.2.10. Streets

1)   Every building shall face a street located in conformance with the requirements of Articles 3.2.5.4. and 3.2.5.5. for access routes.

2)   For the purposes of Subsections 3.2.2. and 3.2.5. an access route conforming to Subsection 3.2.5. is permitted to be considered as a street.

3)   Reserved.

4)   A building is considered to face 2 streets provided not less than 50% of the building perimeter is located within 15 m of the street or streets.

5)   A building is considered to face 3 streets provided not less than 75% of the building perimeter is located within 15 m of the street or streets.

6)   Enclosed spaces, tunnels, bridges and similar structures, even though used for vehicular or pedestrian traffic, are not considered as streets for the purpose of this Part.

3.2.2.11. Exterior Balconies

1)   Except as provided in Sentence (2), an exterior balcony shall be constructed in accordance with the type of construction required by Articles 3.2.2.20. to 3.2.2.92., as applicable to the occupancy classification of the building.

2)   The floor assembly of an exterior balcony in a building or part of a building conforming to Article 3.2.2.48. or 3.2.2.57. shall

a)   be of noncombustible construction, or

b)   be constructed in accordance with Article 3.1.6.3., but need not comply with Sentence 3.1.6.4.(1).

3.2.2.12. Exterior Passageways

1)   An elevated exterior passageway used as part of a means of egress shall conform to the requirements of Articles 3.2.2.20. to 3.2.2.92. for mezzanines.

3.2.2.13. Occupancy on Roof

1)    A portion of a roof that supports an occupancy shall be constructed in conformance with the fire separation requirements of Articles 3.2.2.20. to 3.2.2.92. for floor assemblies, and not the fire-resistance rating for roof assemblies.

3.2.2.14. Rooftop Enclosures

1)   A rooftop enclosure for elevator machinery, an elevator lobby, or for a service room shall be constructed in accordance with the type of construction required by Articles 3.2.2.20. to 3.2.2.92.

2)   A rooftop enclosure for elevator machinery, an elevator lobby, or for a service room, not more than one storey high, and that does not serve as part of a means of egress for an occupancy on a roof in accordance with Sentences 3.3.1.3.(4) to (6), is not required to have a fire-resistance rating.

3)   A rooftop enclosure for a stairway shall be constructed in accordance with the type of construction required by Articles 3.2.2.20. to 3.2.2.92.

4)   A rooftop enclosure for a stairway or an elevator lobby serving an occupancy on a roof that serves only one dwelling unit need not have a fire-resistance rating nor be constructed as a fire separation.

3.2.2.15. Storeys below Ground

1)   If a building is erected entirely below the adjoining finished ground level and does not extend more than one storey below that ground level, the minimum precautions against fire spread and collapse shall be the same as are required for basements under a building of 1 storey in building height having the same occupancy and building area.

2)   If any portion of a building is erected entirely below the adjoining finished ground level and extends more than one storey below that ground level, the following minimum precautions against fire spread and collapse shall be taken:

a)   except as permitted by Sentence (3), the basements shall be sprinklered throughout,

b)   a floor assembly below the ground level shall be constructed as a fire separation with a fire-resistance rating not less than

i)   3 h if the basements are used as Group E or Group F, Division 1 or 2 occupancies, or

ii)   2 h if the basements are not used as Group E or Group F, Division 1 or 2 occupancies, and

c)   all loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the construction that they support.

3)   If the first storey of a building is not required to be sprinklered, sprinklers are not required in the storey immediately below the first storey provided the storey below

a)   contains only residential occupancies, and

b)   has at least one unobstructed access opening conforming to Sentence 3.2.5.1.(2) installed on that storey for each 15 m of wall length in at least one wall required by this Subsection to face a street.

3.2.2.16. Heavy Timber Roof Permitted

1)   Unless otherwise permitted by Articles 3.2.2.20. to 3.2.2.92., a roof assembly in a building up to 2 storeys in building height is permitted to be of heavy timber construction regardless of building area or type of construction required, provided the building is sprinklered throughout.

2)   If Sentence (1) permits a roof assembly to be of heavy timber construction, structural members in the storey immediately below the roof assembly are permitted to be of heavy timber construction.

3.2.2.17. Roof Assemblies and Mezzanines in Gymnasiums, Swimming Pools, Arenas and Rinks

1)   The requirements for a roof assembly to have a fire-resistance rating stated in Articles 3.2.2.25., 3.2.2.30. and 3.2.2.32. are permitted to be waived for gymnasiums, swimming pools, arenas, and rinks, provided

a)   the roof carries no loads other than normal roof loads, including permanent access walks, and ventilating, sound and lighting equipment, and

b)   except as provided in Sentence (3), no part of the roof assembly is less than 6 m above the main floor or balcony.

(See Note A-3.2.2.17.(1).)

2)   The requirements for a mezzanine to have a fire-resistance rating stated in Articles 3.2.2.25., 3.2.2.30. and 3.2.2.32. are permitted to be waived for gymnasiums, swimming pools, arenas, and rinks, provided

a)   the mezzanine is not required to be considered as a storey as per Sentences 3.2.1.1.(3) to (5),

b)   the mezzanine is used only for ventilating, sound and lighting equipment, and

c)   except as provided in Sentence (3), no part of the mezzanine is less than 6 m above the main floor or balcony.

3)   The restrictions concerning minimum distance stated in Clauses (1)(b) and (2)(c) shall not apply to

a)   an inclined and stepped floor ascending from the main floor that is used for seating purposes only, or

b)   a balcony used for seating purposes only.

3.2.2.18. Automatic Sprinkler System Required

1)   Except as permitted by Sentence (2), an automatic sprinkler system conforming to the requirements of Articles 3.2.4.7., 3.2.4.8., 3.2.4.9. and 3.2.5.12. shall be installed throughout a building regulated by one or more of Articles 3.2.2.20., 3.2.2.21., 3.2.2.22., 3.2.2.23., 3.2.2.24., 3.2.2.26., 3.2.2.27., 3.2.2.29., 3.2.2.31., 3.2.2.33., 3.2.2.36., 3.2.2.37., 3.2.2.38., 3.2.2.39., 3.2.2.40., 3.2.2.41., 3.2.2.42., 3.2.2.43., 3.2.2.44., 3.2.2.45., 3.2.2.46., 3.2.2.47., 3.2.2.48., 3.2.2.49., 3.2.2.51., 3.2.2.52., 3.2.2.55., 3.2.2.56., 3.2.2.57., 3.2.2.59., 3.2.2.60., 3.2.2.61., 3.2.2.63., 3.2.2.65., 3.2.2.66., 3.2.2.67., 3.2.2.69., 3.2.2.71., 3.2.2.72., 3.2.2.73., 3.2.2.74., 3.2.2.76., 3.2.2.77., 3.2.2.79., 3.2.2.81., 3.2.2.82., 3.2.2.84., 3.2.2.86., 3.2.2.88. and 3.2.2.90.

2)   If a storey in a building or a floor area is required to have an automatic sprinkler system installed throughout in accordance with one or more of Articles 3.2.2.20. to 3.2.2.92. or Section 3.3., the automatic sprinkler system shall also be installed throughout all lower storeys in the building notwithstanding permission in Articles 3.2.2.20. to 3.2.2.92. to construct one or more of those storeys without installing automatic sprinkler protection. (See Note A-3.2.2.18.(2).)

3.2.2.19. Buildings Containing Impeded Egress Zones

1)   A building containing an impeded egress zone and conforming to the appropriate requirements of Articles 3.2.2.20. to 3.2.2.92. is not required to conform to the requirements of Articles 3.2.2.36. and 3.2.2.37. for a Group B, Division 1 major occupancy provided

a)   the building is sprinklered throughout,

b)   it is not more than 1 storey in building height,

c)   it does not include

i)   a contained use area,

ii)   sleeping accommodation,

iii)   a high-hazard industrial occupancy, or

iv)   a mercantile occupancy,

d)   the building area is not more than 6 400 m2 if the building includes a medium-hazard industrial occupancy,

e)   the impeded egress zone does not extend beyond the boundaries of the fire compartment in which it is located, and

f)   the occupant load of the impeded egress zone is not more than 100.

3.2.2.20. Group A, Division 1, Any Height, Any Area, Sprinklered

1)   Except as permitted by Articles 3.2.2.21. and 3.2.2.22., a building classified as Group A, Division 1 shall conform to Sentence (2).

2)   Except as permitted by Article 3.2.2.16., the building referred to in Sentence (1) shall be of noncombustible construction, and

a)   except as permitted by Sentences 3.2.2.7.(1) and 3.2.2.18.(2), the building shall be sprinklered throughout,

b)   floor assemblies shall be fire separations with a fire-resistance rating not less than 2 h,

c)   mezzanines shall have a fire-resistance rating not less than 1 h, and

d)   loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

3.2.2.21. Group A, Division 1, One Storey, Limited Area, Sprinklered

1)   A building classified as Group A, Division 1 is permitted to conform to Sentence (2) provided

a)   except as permitted by Sentences 3.2.2.7.(1) and 3.2.2.18.(2), the building is sprinklered throughout,

b)   it is not more than 1 storey in building height,

c)   it has less than 40% of the area of the building as 2 storeys for the purpose of

i)   development of productions, including preparation of scenery and costumes and rehearsal of performers,

ii)   organization of performers, scenery and sound equipment,

iii)   preparation by performers for a performance,

iv)   managerial functions, or

v)   toilets, rest rooms and similar public facilities,

d)   it has no occupancy above or below the auditorium other than one which serves it or is dependent on it,

e)   it is not more than 600 m2 in building area, and

f)   the occupant load is not more than 600.

2)   The building referred to in Sentence (1) is permitted to be of heavy timber construction or noncombustible construction used singly or in combination, and

a)   floor assemblies shall be fire separations

i)   with a fire-resistance rating not less than 45 min, or

ii)   of heavy timber construction, and

b)   loadbearing walls, columns and arches shall

i)   have a fire-resistance rating not less than that required for the supported assembly, or

ii)   be of heavy timber construction.

3.2.2.22. Group A, Division 1, One Storey, Sprinklered

1)   A building classified as Group A, Division 1 is permitted to conform to Sentence (2) provided

a)   except as permitted by Sentences 3.2.2.7.(1) and 3.2.2.18.(2), the building is sprinklered throughout,

b)   it is not more than 1 storey in building height,

c)   no part of an auditorium floor is more than 5 m above or below grade,

d)   no occupancy is above or below the auditorium other than one which serves it or is dependent on it, and

e)   the occupant load of the auditorium floor is not more than 300.

2)   The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly, or in combination, and

a)   floor assemblies shall be fire separations with a fire-resistance rating not less than 45 min,

b)   mezzanines shall have, if of combustible construction, a fire-resistance rating not less than 45 min,

c)   loadbearing walls, columns and arches supporting an assembly required to have a fire-resistance rating shall

i)   have a fire-resistance rating not less than 45 min, or

ii)   be of noncombustible construction, and

d)   loadbearing walls, columns and arches supporting a fire separation shall have a fire-resistance rating not less than that required for the fire separation.

3.2.2.23. Group A, Division 2, Any Height, Any Area, Sprinklered

1)   Except as permitted by Articles 3.2.2.24. to 3.2.2.28., a building classified as Group A, Division 2 shall conform to Sentence (2).

2)   Except as permitted by Article 3.2.2.16., the building referred to in Sentence (1) shall be of noncombustible construction, and

a)   except as permitted by Sentences 3.2.2.7.(1) and 3.2.2.18.(2), the building shall be sprinklered throughout,

b)   floor assemblies shall be fire separations with a fire-resistance rating not less than 2 h,

c)   mezzanines shall have a fire-resistance rating not less than 1 h, and

d)   loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

3.2.2.24. Group A, Division 2, up to 6 Storeys, Any Area, Sprinklered

1)   A building classified as Group A, Division 2, that is not limited by building area, is permitted to conform to Sentence (2), provided

a)   except as permitted by Sentences 3.2.2.7.(1) and 3.2.2.18.(2), the building is sprinklered throughout, and

b)   it is not more than 6 storeys in building height.

2)   Except as permitted by Article 3.2.2.16., the building referred to in Sentence (1) shall be of noncombustible construction, and

a)   floor assemblies shall be fire separations with a fire-resistance rating not less than 1 h,

b)   mezzanines shall have a fire-resistance rating not less than 1 h, and

c)   loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

3.2.2.25. Group A, Division 2, up to 2 Storeys

1)   A building classified as Group A, Division 2 is permitted to conform to Sentence (2) provided

a)   it is not more than 2 storeys in building height, and

b)   it has a building area not more than the value in Table 3.2.2.25.

Table 3.2.2.25.

Maximum Building Area, Group A, Division 2, up to 2 Storeys

Forming Part of Sentence 3.2.2.25.(1)

| No. of Storeys | Maximum Area, m2 |  |  |
| --- | --- | --- | --- |
|  | Facing 1 Street | Facing 2 Streets | Facing 3 Streets |
| 1 | 1 600 | 2 000 | 2 400 |
| 2 | 800 | 1 000 | 1 200 |

2)   The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and

a)   floor assemblies shall be fire separations and, if of combustible construction, shall have a fire-resistance rating not less than 45 min,

b)   except as permitted by Article 3.2.2.17., mezzanines shall have, if of combustible construction, a fire-resistance rating not less than 45 min,

c)   except as permitted by Article 3.2.2.17., roof assemblies shall have, if of combustible construction, a fire-resistance rating not less than 45 min, except that in a building not more than 1 storey in building height, the fire-resistance rating is permitted to be waived provided the roof assembly is constructed as a fire-retardant-treated wood roof system conforming to Article 3.1.14.1., and the building area is not more than

i)   800 m2 if facing one street,

ii)   1 000 m2 if facing 2 streets, or

iii)   1 200 m2 if facing 3 streets, and

d)   loadbearing walls, columns and arches supporting an assembly required to have a fire-resistance rating shall

i)   have a fire-resistance rating not less than 45 min, or

ii)   be of noncombustible construction.

3.2.2.26. Group A, Division 2, up to 2 Storeys, Increased Area, Sprinklered

1)   A building classified as Group A, Division 2 is permitted to conform to Sentence (2) provided

a)   except as permitted by Sentences 3.2.2.7.(1) and 3.2.2.18.(2), the building is sprinklered throughout,

b)   it is not more than 2 storeys in building height, and

c)   it has a building area not more than

i)   4 800 m2 if 1 storey in building height, or

ii)   2 400 m2 if 2 storeys in building height.

2)   The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and

a)   floor assemblies shall be fire separations and, if of combustible construction, shall have a fire-resistance rating not less than 45 min,

b)   mezzanines shall have, if of combustible construction, a fire-resistance rating not less than 45 min, and

c)   loadbearing walls, columns and arches supporting an assembly required to have a fire-resistance rating shall

i)   have a fire-resistance rating not less than 45 min, or

ii)   be of noncombustible construction.

3.2.2.27. Group A, Division 2, up to 2 Storeys, Sprinklered

1)   A building classified as Group A, Division 2 is permitted to be of combustible construction or noncombustible construction, used singly or in combination, provided

a)   except as permitted by Sentences 3.2.2.7.(1) and 3.2.2.18.(2), the building is sprinklered throughout,

b)   it is not more than 2 storeys in building height, and

c)   it has a building area not more than

i)   2 400 m2 if 1 storey in building height with no basement,

ii)   1 200 m2 if 1 storey in building height, or

iii)   600 m2 if 2 storeys in building height.

3.2.2.28. Group A, Division 2, One Storey

1)   A building classified as Group A, Division 2 is permitted to be of combustible construction or noncombustible construction, used singly or in combination, provided

a)   it is not more than 1 storey in building height, and

b)   except as permitted by Sentence (2), it has a building area not more than

i)   400 m2 if facing one street,

ii)   500 m2 if facing 2 streets, or

iii)   600 m2 if facing 3 streets.

2)   In a building referred to in Sentence (1) without a basement, the building area limits of Sentence (1) are permitted to be doubled provided a fire separation with a fire-resistance rating not less than 1 h is used to separate the building into fire compartments, each one of which does not exceed the limits of Clause (1)(b).

3.2.2.29. Group A, Division 3, Any Height, Any Area, Sprinklered

1)   Except as permitted by Articles 3.2.2.30. to 3.2.2.34., a building classified as Group A, Division 3 shall conform to Sentence (2).

2)   Except as permitted by Article 3.2.2.16., the building referred to in Sentence (1) shall be of noncombustible construction, and

a)   except as permitted by Sentences 3.2.2.7.(1) and 3.2.2.18.(2), the building shall be sprinklered throughout,

b)   floor assemblies shall be fire separations with a fire-resistance rating not less than 2 h,

c)   mezzanines shall have a fire-resistance rating not less than 1 h, and

d)   loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

3.2.2.30. Group A, Division 3, up to 2 Storeys

1)   A building classified as Group A, Division 3 is permitted to conform to Sentence (2) provided

a)   it is not more than 2 storeys in building height, and

b)   it has a building area not more than the value in Table 3.2.2.30.

Table 3.2.2.30.

Maximum Building Area, Group A, Division 3, up to 2 Storeys

Forming Part of Sentence 3.2.2.30.(1)

| No. of Storeys | Maximum Area, m2 |  |  |
| --- | --- | --- | --- |
|  | Facing 1 Street | Facing 2 Streets | Facing 3 Streets |
| 1 | 4 000 | 5 000 | 6 000 |
| 2 | 2 000 | 2 500 | 3 000 |

2)   Except as permitted by Clauses (c) and (d), the building referred to in Sentence (1) shall be of noncombustible construction, and

a)   floor assemblies shall be fire separations with a fire-resistance rating not less than 1 h,

b)   except as permitted by Article 3.2.2.17., mezzanines shall have a fire-resistance rating not less than 1 h,

c)   except as permitted by Article 3.2.2.17., roof assemblies shall

i)   have a fire-resistance rating not less than 45 min, or

ii)   be of heavy timber construction, and

d)   loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly, except that arches and structural members within the storey immediately below a roof assembly are permitted to be of heavy timber construction.

3)   If intended for occasional use for trade shows and similar exhibition purposes, a building referred to in Sentence (1) that is more than 1 500 m2 in building area shall be sprinklered throughout.

3.2.2.31. Group A, Division 3, up to 2 Storeys, Sprinklered

1)   A building classified as Group A, Division 3 is permitted to conform to Sentence (2) provided

a)   except as permitted by Sentences 3.2.2.7.(1) and 3.2.2.18.(2), the building is sprinklered throughout,

b)   it is not more than 2 storeys in building height, and

c)   it has a building area not more than

i)   12 000 m2 if 1 storey in building height, or

ii)   6 000 m2 if 2 storeys in building height.

2)   Except as permitted by Clause (c) and Article 3.2.2.16., the building referred to in Sentence (1) shall be of noncombustible construction, and

a)   floor assemblies shall be fire separations with a fire-resistance rating not less than 1 h,

b)   mezzanines shall have a fire-resistance rating not less than 1 h, and

c)   loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly, except that arches are permitted to be of heavy timber construction.

3.2.2.32. Group A, Division 3, One Storey, Increased Area

1)   A building classified as Group A, Division 3 is permitted to conform to Sentence (2) provided

a)   it is not more than 1 storey in building height, and

b)   it has a building area not more than

i)   2 400 m2 if facing one street,

ii)   3 000 m2 if facing 2 streets, or

iii)   3 600 m2 if facing 3 streets.

2)   The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and

a)   except as permitted by Article 3.2.2.17., mezzanines shall have, if of combustible construction, a fire-resistance rating not less than 45 min,

b)   except as permitted by Article 3.2.2.17., roof assemblies shall have, if of combustible construction, a fire-resistance rating not less than 45 min, except that the fire-resistance rating is permitted to be waived provided the roof assembly is constructed as a fire-retardant-treated wood roof system conforming to Article 3.1.14.1., and the building area is not more than

i)   1 200 m2 if facing one street,

ii)   1 500 m2 if facing 2 streets, or

iii)   1 800 m2 if facing 3 streets, and

c)   loadbearing walls, columns and arches supporting an assembly required to have a fire-resistance rating shall

i)   have a fire-resistance rating not less than 45 min, or

ii)   be of noncombustible construction.

3)   If intended for occasional use for trade shows and similar exhibition purposes, a building referred to in Sentence (1) that is more than 1 500 m2 in building area shall be sprinklered throughout.

3.2.2.33. Group A, Division 3, One Storey, Sprinklered

1)   A building classified as Group A, Division 3 is permitted to be of combustible construction or noncombustible construction used singly or in combination provided

a)   except as permitted by Sentences 3.2.2.7.(1) and 3.2.2.18.(2), the building is sprinklered throughout,

b)   it is not more than 1 storey in building height, and

c)   it has a building area not more than 7 200 m2.

3.2.2.34. Group A, Division 3, One Storey

1)   A building classified as Group A, Division 3 is permitted to be of combustible construction or noncombustible construction used singly or in combination provided

a)   it is not more than 1 storey in building height, and

b)   it has a building area not more than

i)   1 000 m2 if facing one street,

ii)   1 250 m2 if facing 2 streets, or

iii)   1 500 m2 if facing 3 streets.

3.2.2.35. Group A, Division 4

1)   Except as permitted by Sentences (2) and (3), a building classified as Group A, Division 4 shall be of noncombustible construction.

2)   Roof assemblies and supporting arches and columns are permitted to be of heavy timber construction.

3)   A building classified as Group A, Division 4 is permitted to be of combustible construction provided

a)   the occupant load is less than 1 500, and

b)   the building has a limiting distance not less than 6 m.

4)   Sprinklers shall be installed in all spaces below tiers of seats in a building classified as Group A, Division 4 if those spaces are used for occupancy. (See Note A-3.2.2.35.(4).)

3.2.2.36. Group B, Division 1, Any Height, Any Area, Sprinklered

1)   Except as permitted by Article 3.2.2.37., a building classified as Group B, Division 1 shall conform to Sentence (2).

2)   Except as permitted by Article 3.2.2.16., the building referred to in Sentence (1) shall be of noncombustible construction, and

a)   except as permitted by Sentences 3.2.2.7.(1) and 3.2.2.18.(2), the building shall be sprinklered throughout,

b)   floor assemblies shall be fire separations with a fire-resistance rating not less than 2 h,

c)   mezzanines shall have a fire-resistance rating not less than 1 h, and

d)   loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

3.2.2.37. Group B, Division 1, up to 3 Storeys, Sprinklered

1)    A building classified as Group B, Division 1 is permitted to conform to Sentence (2) provided

a)   except as permitted by Sentences 3.2.2.7.(1) and 3.2.2.18.(2), the building is sprinklered throughout,

b)   it is not more than 3 storeys in building height, and

c)   it has a building area

i)   that is not limited if the building is not more than 1 storey in building height,

ii)   not more than 12 000 m2 if 2 storeys in building height, or

iii)   not more than 8 000 m2 if 3 storeys in building height.

2)   Except as permitted by Article 3.2.2.16., the building referred to in Sentence (1) shall be of noncombustible construction, and

a)   floor assemblies shall be fire separations with a fire-resistance rating not less than 1 h,

b)   mezzanines shall have a fire-resistance rating not less than 1 h, and

c)   loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

3.2.2.38. Group B, Division 2, Any Height, Any Area, Sprinklered

1)   Except as permitted by Articles 3.2.2.39. to 3.2.2.41., a building classified as Group B, Division 2 shall conform to Sentence (2).

2)   Except as permitted by Article 3.2.2.16., the building referred to in Sentence (1) shall be of noncombustible construction, and

a)   except as permitted by Sentences 3.2.2.7.(1) and 3.2.2.18.(2), the building shall be sprinklered throughout,

b)   floor assemblies shall be fire separations with a fire-resistance rating not less than 2 h,

c)   mezzanines shall have a fire-resistance rating not less than 1 h, and

d)   loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

3.2.2.39. Group B, Division 2, up to 3 Storeys, Sprinklered

1)   A building classified as Group B, Division 2 is permitted to conform to Sentence (2) provided

a)   except as permitted by Sentences 3.2.2.7.(1) and 3.2.2.18.(2), the building is sprinklered throughout,

b)   it is not more than 3 storeys in building height, and

c)   it has a building area

i)   that is not limited if the building is not more than 1 storey in building height,

ii)   not more than 12 000 m2 if 2 storeys in building height, or

iii)   not more than 8 000 m2 if 3 storeys in building height.

2)   Except as permitted by Article 3.2.2.16., the building referred to in Sentence (1) shall be of noncombustible construction, and

a)   floor assemblies shall be fire separations with a fire-resistance rating not less than 1 h,

b)   mezzanines shall have a fire-resistance rating not less than 1 h, and

c)   loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

3.2.2.40. Group B, Division 2, up to 2 Storeys, Sprinklered

1)   A building classified as Group B, Division 2 is permitted to conform to Sentence (2) provided

a)   except as permitted by Sentences 3.2.2.7.(1) and 3.2.2.18.(2), the building is sprinklered throughout,

b)   it is not more than 2 storeys in building height, and

c)   it has a building area not more than

i)   2 400 m2 if 1 storey in building height, or

ii)   1 600 m2 if 2 storeys in building height.

2)   The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and

a)   floor assemblies shall be fire separations with a fire-resistance rating not less than 45 min,

b)   mezzanines shall have, if of combustible construction, a fire-resistance rating not less than 45 min, and

c)   loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

3.2.2.41. Group B, Division 2, One Storey, Sprinklered

1)   A building classified as Group B, Division 2 is permitted to be of combustible construction or noncombustible construction, used singly or in combination, provided

a)   except as permitted by Sentences 3.2.2.7.(1) and 3.2.2.18.(2), the building is sprinklered throughout,

b)   it is not more than 1 storey in building height, and

c)   it has a building area not more than 500 m2.

3.2.2.42. Group B, Division 3, Any Height, Any Area, Sprinklered

1)   Except as permitted by Articles 3.2.2.43. to 3.2.2.46., a building classified as Group B, Division 3 shall conform to Sentence (2).

2)   Except as permitted by Article 3.2.2.16., the building referred to in Sentence (1) shall be of noncombustible construction, and

a)   except as permitted by Sentences 3.2.2.7.(1) and 3.2.2.18.(2), the building shall be sprinklered throughout,

b)   floor assemblies shall be fire separations with a fire-resistance rating not less than 2 h,

c)   mezzanines shall have a fire-resistance rating not less than 1 h, and

d)   loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

3.2.2.43. Group B, Division 3, up to 3 Storeys (Noncombustible), Sprinklered

1)   A building classified as Group B, Division 3 is permitted to conform to Sentence (2) provided

a)   except as permitted by Sentences 3.2.2.7.(1) and 3.2.2.18.(2), the building is sprinklered throughout,

b)   it is not more than 3 storeys in building height, and

c)   it has a building area

i)   that is not limited if the building is not more than 1 storey in building height,

ii)   not more than 12 000 m2 if 2 storeys in building height, or

iii)   not more than 8 000 m2 if 3 storeys in building height.

2)   Except as permitted by Article 3.2.2.16., the building referred to in Sentence (1) shall be of noncombustible construction, and

a)   floor assemblies shall be fire separations with a fire-resistance rating not less than 1 h,

b)   mezzanines shall have a fire-resistance rating not less than 1 h, and

c)   loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

3.2.2.44. Group B, Division 3, up to 3 Storeys, Sprinklered

1)   A building classified as Group B, Division 3 is permitted to conform to Sentence (2) provided

a)   except as permitted by Sentences 3.2.2.7.(1) and 3.2.2.18.(2), the building is sprinklered throughout,

b)   it is not more than 3 storeys in building height, and

c)   it has a building area not more than

i)   5 400 m2 if 1 storey in building height,

ii)   2 700 m2 if 2 storeys in building height, or

iii)   1 800 m2 if 3 storeys in building height.

2)   The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction, used singly or in combination, and

a)   floor assemblies shall be fire separations with a fire-resistance rating not less than 1 h,

b)   mezzanines shall have a fire-resistance rating not less than 1 h, and

c)   loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

3.2.2.45. Group B, Division 3, up to 2 Storeys, Sprinklered

1)   A building classified as Group B, Division 3 is permitted to conform to Sentence (2) provided

a)   except as permitted by Sentences 3.2.2.7.(1) and 3.2.2.18.(2), the building is sprinklered throughout,

b)   it is not more than 2 storeys in building height, and

c)   it has a building area not more than

i)   2 400 m2 if 1 storey in building height, or

ii)   1 600 m2 if 2 storeys in building height.

2)   The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction, used singly or in combination, and

a)   floor assemblies shall be fire separations with a fire-resistance rating not less than 45 min,

b)   mezzanines shall have, if of combustible construction, a fire-resistance rating not less than 45 min, and

c)   loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

3.2.2.46. Group B, Division 3, One Storey, Sprinklered

1)   A building classified as Group B, Division 3 is permitted to be of combustible construction or noncombustible construction, used singly or in combination, provided

a)   except as permitted by Sentences 3.2.2.7.(1) and 3.2.2.18.(2), the building is sprinklered throughout,

b)   it is not more than 1 storey in building height, and

c)   it has a building area not more than 600 m2.

3.2.2.47. Group C, Any Height, Any Area, Sprinklered

1)   Except as permitted by Articles 3.2.2.48. to 3.2.2.55., a building classified as Group C shall conform to Sentence (2).

2)   Except as permitted by Article 3.2.2.16., the building referred to in Sentence (1) shall be of noncombustible construction, and

a)   except as permitted by Sentences 3.2.2.7.(1) and 3.2.2.18.(2), the building shall be sprinklered throughout,

b)   except as permitted by Sentence (3), floor assemblies shall be fire separations with a fire-resistance rating not less than 2 h,

c)   mezzanines shall have a fire-resistance rating not less than 1 h, and

d)   loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

3)   In a building that contains dwelling units that have more than one storey, subject to the requirements of Sentence 3.3.4.2.(3), the floor assemblies, including floors over basements, which are entirely contained within these dwelling units, shall have a fire-resistance rating not less than 1 h but need not be constructed as fire separations.

3.2.2.48. Group C, up to 12 Storeys, Sprinklered

1)   A building classified as Group C is permitted to conform to Sentence (2), provided

a)   it is sprinklered throughout,

b)   it is not more than 12 storeys in building height,

c)   it has a height not more than 50 m measured between the floor of the first storey and the uppermost floor level that does not serve a rooftop enclosure for elevator machinery, a stairway or a service room used only for service to the building, and

d)   it has a building area not more than 6 000 m2.

2)   Except as provided in Article 3.2.2.16., the building referred to in Sentence (1) is permitted to be of encapsulated mass timber construction or noncombustible construction, used singly or in combination, and

a)   except as provided in Sentence (3), floor assemblies shall be fire separations with a fire-resistance rating not less than 2 h,

b)   mezzanines shall have a fire-resistance rating not less than 1 h, and

c)   loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

3)   In a building that contains dwelling units that have more than one storey, subject to the requirements of Sentence 3.3.4.2.(3), the floor assemblies, including floors over basements, that are entirely contained within these dwelling units shall have a fire-resistance rating not less than 1 h, but need not be constructed as fire separations.

4)   Group A, Division 2 major occupancies, Group E major occupancies and storage garages located in a building or part of a building within the scope of this Article are permitted to be constructed in accordance with this Article, provided

a)   the Group A, Division 2 major occupancy is located below the fourth storey,

b)   the Group E major occupancy is located below the third storey, and

c)   the storage garage is located below the fifth storey (see also Article 4.4.2.1.).

(See Note A-3.2.2.48.(4) and 3.2.2.57.(3).)

3.2.2.49. Group C, up to 6 Storeys, Sprinklered, Noncombustible Construction

1)   A building classified as Group C is permitted to conform to Sentence (2) provided

a)   except as permitted by Sentences 3.2.2.7.(1) and 3.2.2.18.(2), the building is sprinklered throughout,

b)   it is not more than 6 storeys in building height, and

c)   it has a building area

i)   that is not limited if the building is not more than 2 storeys in building height,

ii)   not more than 12 000 m2 if 3 storeys in building height,

iii)   not more than 9 000 m2 if 4 storeys in building height,

iv)   not more than 7 200 m2 if 5 storeys in building height, or

v)   not more than 6 000 m2 if 6 storeys in building height.

2)   Except as permitted by Article 3.2.2.16., the building referred to in Sentence (1) shall be of noncombustible construction, and

a)   except as permitted by Sentence (3), floor assemblies shall be fire separations with a fire-resistance rating not less than 1 h,

b)   mezzanines shall have a fire-resistance rating not less than 1 h, and

c)   loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

3)   In a building that contains dwelling units that have more than one storey, subject to the requirements of Sentence 3.3.4.2.(3), the floor assemblies, including floors over basements, which are entirely contained within these dwelling units, shall have a fire-resistance rating not less than 1 h but need not be constructed as fire separations.

3.2.2.50. Group C, up to 3 Storeys, Noncombustible Construction

1)   A building classified as Group C is permitted to conform to Sentence (2) provided

a)   it is not more than 3 storeys in building height, and

b)   it has a building area not more than the value in Table 3.2.2.50.

Table 3.2.2.50.

Maximum Building Area, Group C, up to 3 Storeys

Forming Part of Sentence 3.2.2.50.(1)

| No. of Storeys | Maximum Area, m2 |  |  |
| --- | --- | --- | --- |
|  | Facing 1 Street | Facing 2 Streets | Facing 3 Streets |
| 1 | not limited | not limited | not limited |
| 2 | 6 000 | not limited | not limited |
| 3 | 4 000 | 5 000 | 6 000 |

2)   The building referred to in Sentence (1) shall be of noncombustible construction, and

a)   except as permitted by Sentence (3), floor assemblies shall be fire separations with a fire-resistance rating not less than 1 h,

b)   mezzanines shall have a fire-resistance rating not less than 1 h,

c)   roof assemblies shall have a fire-resistance rating not less than 1 h, and

d)   loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

3)   In a building that contains dwelling units that have more than one storey, subject to the requirements of Sentence 3.3.4.2.(3), the floor assemblies, including floors over basements, which are entirely contained within these dwelling units, shall have a fire-resistance rating not less than 1 h but need not be constructed as fire separations.

3.2.2.51. Group C, up to 6 Storeys, Sprinklered

1)   A building classified as Group C is permitted to conform to Sentence (2), provided

a)   it is sprinklered throughout,

b)   it is not more than 6 storeys in building height,

c)   it has a height not more than 18 m measured between the floor of the first storey and the uppermost floor level, excluding any floor level within a rooftop enclosure that is not considered as a storey in calculating building height in accordance with Sentence 3.2.1.1.(1), and

d)   it has a building area not more than

i)   9 000 m2 if 1 storey in building height,

ii)   4 500 m2 if 2 storeys in building height,

iii)   3 000 m2 if 3 storeys in building height,

iv)   2 250 m2 if 4 storeys in building height,

v)   1 800 m2 if 5 storeys in building height, or

vi)   1 500 m2 if 6 storeys in building height.

2)   Buildings referred to in Sentence (1) are permitted to be of combustible construction or noncombustible construction, used singly or in combination, and

a)   except as provided in Sentence (3), floor assemblies shall be fire separations with a fire-resistance rating not less than 1 h,

b)   roof assemblies shall have a fire-resistance rating not less than 1 h,

c)   except as provided in Sentence (4), where the roof assembly has a height greater than 25 m measured from the floor of the first storey to the highest point of the roof assembly, the roof assembly shall be constructed of noncombustible construction or fire-retardant-treated wood conforming to Article 3.1.4.5.,

d)   mezzanines shall have a fire-resistance rating not less than 1 h, and

e)   loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

3)   In a building that contains dwelling units that have more than one storey, subject to the requirements of Sentence 3.3.4.2.(3), the floor assemblies, including those over basements, that are entirely contained within these dwelling units shall have a fire-resistance rating not less than 1 h but need not be constructed as fire separations.

4)   Where buildings conforming to Sentence (2) include non-contiguous roof assemblies at different elevations, the roof assemblies are permitted to be evaluated separately to determine which ones are required to be constructed in accordance with Clause (2)(c).

5)   Group A, Division 2 major occupancies, Group E major occupancies, and storage garages located in a building or part thereof within the scope of this Article are permitted to be constructed in accordance with this Article, provided

a)   the Group A, Division 2 major occupancy and Group E major occupancy are located below the third storey, and

b)   the storage garage is located below the fourth storey (see also Article 4.4.2.1.).

(See Note A-3.2.2.51.(5) and 3.2.2.60.(4).)

3.2.2.52. Group C, up to 4 Storeys, Sprinklered

1)   A building classified as Group C is permitted to conform to Sentence (2) provided

a)   except as permitted by Sentences 3.2.2.7.(1) and 3.2.2.18.(2), the building is sprinklered throughout,

b)   it is not more than 4 storeys in building height, and

c)   it has a building area not more than

i)   7 200 m2 if 1 storey in building height,

ii)   3 600 m2 if 2 storeys in building height,

iii)   2 400 m2 if 3 storeys in building height, or

iv)   1 800 m2 if 4 storeys in building height.

2)   The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and

a)   except as permitted by Sentences (3) and (4), floor assemblies shall be fire separations with a fire-resistance rating not less than 1 h,

b)   mezzanines shall have a fire-resistance rating not less than 1 h, and

c)   loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

3)   In a building that contains dwelling units that have more than one storey, subject to the requirements of Sentence 3.3.4.2.(3), the floor assemblies, including floors over basements, which are entirely contained within these dwelling units, shall have a fire-resistance rating not less than 1 h but need not be constructed as fire separations.

4)   In a building in which there is no dwelling unit above another dwelling unit, the fire-resistance rating for floor assemblies entirely within the dwelling unit is waived.

3.2.2.53. Group C, up to 3 Storeys, Increased Area

1)   A building classified as Group C is permitted to conform to Sentence (2) provided

a)   it is not more than 3 storeys in building height, and

b)   it has a building area not more than the value in Table 3.2.2.53.

Table 3.2.2.53.

Maximum Building Area, Group C, up to 3 Storeys, Increased Area

Forming Part of Sentence 3.2.2.53.(1)

| No. of Storeys | Maximum Area, m2 |  |  |
| --- | --- | --- | --- |
|  | Facing 1 Street | Facing 2 Streets | Facing 3 Streets |
| 1 | 2 400 | 3 000 | 3 600 |
| 2 | 1 200 | 1 500 | 1 800 |
| 3 | 800 | 1 000 | 1 200 |

2)   The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and

a)   except as permitted by Sentences (3) and (4), floor assemblies shall be fire separations with a fire-resistance rating not less than 1 h,

b)   mezzanines shall have a fire-resistance rating not less than 1 h,

c)   roof assemblies shall have a fire-resistance rating not less than 1 h, and

d)   loadbearing walls, columns, and arches shall have a fire-resistance rating not less than that required for the supported assembly.

3)   In a building that contains dwelling units that have more than one storey, subject to the requirements of Sentence 3.3.4.2.(3), the floor assemblies, including floors over basements, which are entirely contained within these dwelling units, shall have a fire-resistance rating not less than 1 h but need not be constructed as fire separations.

4)   In a building in which there is no dwelling unit above another dwelling unit, the fire-resistance rating for floor assemblies entirely within the dwelling unit is waived.

3.2.2.54. Group C, up to 3 Storeys

1)   A building classified as Group C is permitted to conform to Sentence (2) provided

a)   it is not more than 3 storeys in building height, and

b)   it has a building area not more than the value in Table 3.2.2.54.

Table 3.2.2.54.

Maximum Building Area, Group C, up to 3 Storeys

Forming Part of Sentence 3.2.2.54.(1)

| No. of Storeys | Maximum Area, m2 |  |  |
| --- | --- | --- | --- |
|  | Facing 1 Street | Facing 2 Streets | Facing 3 Streets |
| 1 | 1 800 | 2 250 | 2 700 |
| 2 | 900 | 1 125 | 1 350 |
| 3 | 600 | 750 | 900 |

2)   The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and

a)   except as permitted by Sentences (3) and (4), floor assemblies shall be fire separations with a fire-resistance rating not less than 45 min,

b)   mezzanines shall have, if of combustible construction, a fire-resistance rating not less than 45 min, and

c)   loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

3)   In a building that contains dwelling units that have more than one storey, subject to the requirements of Sentence 3.3.4.2.(3), the floor assemblies, including floors over basements, which are entirely contained within these dwelling units, shall have a fire-resistance rating not less than 45 min but need not be constructed as fire separations.

4)   In a building in which there is no dwelling unit above another dwelling unit, the fire-resistance rating for floor assemblies entirely within the dwelling unit is waived.

3.2.2.55. Group C, up to 3 Storeys, Sprinklered

1)   A building classified as Group C is permitted to conform to Sentence (2) provided

a)   except as permitted by Sentences 3.2.2.7.(1) and 3.2.2.18.(2), the building is sprinklered throughout,

b)   it is not more than 3 storeys in building height, and

c)   it has a building area not more than

i)   5 400 m2 if 1 storey in building height,

ii)   2 700 m2 if 2 storeys in building height, or

iii)   1 800 m2 if 3 storeys in building height.

2)   The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and

a)   except as permitted by Sentences (3) and (4), floor assemblies shall be fire separations with a fire-resistance rating not less than 45 min,

b)   mezzanines shall have, if of combustible construction, a fire-resistance rating not less than 45 min, and

c)   loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

3)   In a building that contains dwelling units that have more than one storey, subject to the requirements of Sentence 3.3.4.2.(3), the floor assemblies, including floors over basements, which are entirely contained within these dwelling units, shall have a fire-resistance rating not less than 45 min but need not be constructed as fire separations.

4)   In a building in which there is no dwelling unit above another dwelling unit, the fire-resistance rating for floor assemblies entirely within the dwelling unit is waived.

3.2.2.56. Group D, Any Height, Any Area, Sprinklered

1)   Except as permitted by Articles 3.2.2.57. to 3.2.2.65., a building classified as Group D shall conform to Sentence (2).

2)   Except as permitted by Article 3.2.2.16., the building referred to in Sentence (1) shall be of noncombustible construction, and

a)   except as permitted by Sentences 3.2.2.7.(1) and 3.2.2.18.(2), the building shall be sprinklered throughout,

b)   floor assemblies shall be fire separations with a fire-resistance rating not less than 2  h,

c)   mezzanines shall have a fire-resistance rating not less than 1 h, and

d)   loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

3.2.2.57. Group D, up to 12 storeys, Sprinklered

1)   A building classified as Group D is permitted to conform to Sentence (2), provided

a)   it is sprinklered throughout,

b)   it is not more than 12 storeys in building height,

c)   it has a height not more than 50 m measured between the floor of the first storey and the uppermost floor level that does not serve a rooftop enclosure for elevator machinery, a stairway or a service room used only for service to the building, and

d)   it has a building area not more than 7 200 m2.

2)   Except as provided in Article 3.2.2.16., the building referred to in Sentence (1) is permitted to be of encapsulated mass timber construction or noncombustible construction, used singly or in combination, and

a)   floor assemblies shall be fire separations with a fire-resistance rating not less than 2 h,

b)   mezzanines shall have a fire-resistance rating not less than 1 h, and

c)   loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

3)   Group A, Division 2 major occupancies, Group E major occupancies, Group F, Division 2 and 3 major occupancies, and storage garages located in a building or part of a building within the scope of this Article are permitted to be constructed in accordance with this Article, provided

a)   the Group A, Division 2 major occupancy is located below the fourth storey,

b)   the Group E major occupancy and Group F, Division 2 or 3 major occupancy are located below the third storey, and

c)   the storage garage is located below the fifth storey (see also Article 4.4.2.1.).

(See Note A-3.2.2.48.(4) and 3.2.2.57.(3).)

3.2.2.58. Group D, up to 6 Storeys

1)   A building classified as Group D is permitted to conform to Sentence (2) provided

a)   it is not more than 6 storeys in building height, and

b)   it has a building area not more than the value in Table 3.2.2.58.

Table 3.2.2.58.

Maximum Building Area, Group D, up to 6 Storeys

Forming Part of Sentence 3.2.2.58.(1)

| No. of Storeys | Maximum Area, m2 |  |  |
| --- | --- | --- | --- |
|  | Facing 1 Street | Facing 2 Streets | Facing 3 Streets |
| 1 | not limited | not limited | not limited |
| 2 | 7 200 | not limited | not limited |
| 3 | 4 800 | 6 000 | 7 200 |
| 4 | 3 600 | 4 500 | 5 400 |
| 5 | 2 880 | 3 600 | 4 320 |
| 6 | 2 400 | 3 000 | 3 600 |

2)   The building referred to in Sentence (1) shall be of noncombustible construction, and

a)   floor assemblies shall be fire separations with a fire-resistance rating not less than 1 h,

b)   mezzanines shall have a fire-resistance rating not less than 1 h,

c)   roof assemblies shall have a fire-resistance rating not less than 1 h, except that in a building not more than 1 storey in building height this requirement is waived, and

d)   loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

3.2.2.59. Group D, up to 6 Storeys, Sprinklered, Noncombustible Construction

1)   A building classified as Group D is permitted to conform to Sentence (2) provided

a)   except as permitted by Sentences 3.2.2.7.(1) and 3.2.2.18.(2), the building is sprinklered throughout,

b)   it is not more than 6 storeys in building height, and

c)   it has a building area

i)   that is not limited if the building is not more than 2 storeys in building height,

ii)   not more than 14 400 m2 if 3 storeys in building height,

iii)   not more than 10 800 m2 if 4 storeys in building height,

iv)   not more than 8 640 m2 if 5 storeys in building height, or

v)   not more than 7 200 m2 if 6 storeys in building height.

2)   Except as permitted by Article 3.2.2.16., the building referred to in Sentence (1) shall be of noncombustible construction, and

a)   floor assemblies shall be fire separations with a fire-resistance rating not less than 1 h,

b)   mezzanines shall have a fire-resistance rating not less than 1 h, and

c)   loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

3.2.2.60. Group D, up to 6 Storeys, Sprinklered

1)   A building classified as Group D is permitted to conform to Sentence (2), provided

a)   it is sprinklered throughout,

b)   it is not more than 6 storeys in building height,

c)   it has a height not more than 18 m measured between the floor of the first storey and the uppermost floor level, excluding any floor level within a rooftop enclosure that is not considered as a storey in calculating building height in accordance with Sentence 3.2.1.1.(1), and

d)   it has a building area not more than

i)   18 000 m2 if 1 storey in building height,

ii)   9 000 m2 if 2 storeys in building height,

iii)   6 000 m2 if 3 storeys in building height,

iv)   4 500 m2 if 4 storeys in building height,

v)   3 600 m2 if 5 storeys in building height, or

vi)   3 000 m2 if 6 storeys in building height.

2)   The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction, used singly or in combination, and

a)   floor assemblies shall be fire separations with a fire-resistance rating not less than 1 h,

b)   roof assemblies shall have a fire-resistance rating not less than 1 h,

c)   except as provided in Sentence (3), where the roof assembly has a height greater than 25 m measured from the floor of the first storey to the highest point of the roof assembly, the roof assembly shall be constructed of noncombustible construction or fire-retardant-treated wood conforming to Article 3.1.4.5.,

d)   mezzanines shall have a fire-resistance rating not less than 1 h, and

e)   loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

3)   Where buildings conforming to Sentence (2) include non-contiguous roof assemblies at different elevations, the roof assemblies are permitted to be evaluated separately to determine which ones are required to be constructed in accordance with Clause (2)(c).

4)   Group A, Division 2 major occupancies, Group E major occupancies, Group F, Division 2 and 3 major occupancies, and storage garages located in a building or part thereof within the scope of this Article are permitted to be constructed in accordance with this Article, provided

a)   the Group A, Division 2 major occupancy, Group E major occupancy, and Group F, Division 2 or 3 major occupancy are located below the third storey, and

b)   the storage garage is located below the fourth storey (see also Article 4.4.2.1.).

(See Note A-3.2.2.51.(5) and 3.2.2.60.(4).)

3.2.2.61. Group D, up to 4 Storeys, Sprinklered

1)   A building classified as Group D is permitted to conform to Sentence (2) provided

a)   except as permitted by Sentences 3.2.2.7.(1) and 3.2.2.18.(2), the building is sprinklered throughout,

b)   it is not more than 4 storeys in building height, and

c)   it has a building area not more than 3 600 m2.

2)   The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and

a)   floor assemblies shall be fire separations with a fire-resistance rating not less than 1 h,

b)   mezzanines shall have a fire-resistance rating not less than 1 h, and

c)   loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

3.2.2.62. Group D, up to 3 Storeys

1)   A building classified as Group D is permitted to conform to Sentence (2) provided

a)   it is not more than 3 storeys in building height, and

b)   it has a building area not more than the value in Table 3.2.2.62.

Table 3.2.2.62.

Maximum Building Area, Group D, up to 3 Storeys

Forming Part of Sentence 3.2.2.62.(1)

| No. of Storeys | Maximum Area, m2 |  |  |
| --- | --- | --- | --- |
|  | Facing 1 Street | Facing 2 Streets | Facing 3 Streets |
| 1 | 4 800 | 6 000 | 7 200 |
| 2 | 2 400 | 3 000 | 3 600 |
| 3 | 1 600 | 2 000 | 2 400 |

2)   The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and

a)   floor assemblies shall be fire separations and, if of combustible construction, shall have a fire-resistance rating not less than 45 min,

b)   mezzanines shall have, if of combustible construction, a fire-resistance rating not less than 45 min,

c)   roof assemblies shall have, if of combustible construction, a fire-resistance rating not less than 45 min, except that in a building not more than 1 storey in building height, the fire-resistance rating is permitted to be waived provided the roof assembly is constructed as a fire-retardant-treated wood roof system conforming to Article 3.1.14.1. and the building area is not more than

i)   2 400 m2 if facing one street,

ii)   3 000 m2 if facing 2 streets, or

iii)   3 600 m2 if facing 3 streets, and

d)   loadbearing walls, columns and arches supporting an assembly required to have a fire-resistance rating shall

i)   have a fire-resistance rating not less than 45 min, or

ii)   be of noncombustible construction.

3.2.2.63. Group D, up to 3 Storeys, Sprinklered

1)   A building classified as Group D is permitted to conform to Sentence (2) provided

a)   except as permitted by Sentences 3.2.2.7.(1) and 3.2.2.18.(2), the building is sprinklered throughout,

b)   it is not more than 3 storeys in building height, and

c)   it has a building area not more than

i)   14 400 m2 if 1 storey in building height,

ii)   7 200 m2 if 2 storeys in building height, or

iii)   4 800 m2 if 3 storeys in building height.

2)   The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and

a)   floor assemblies shall be fire separations and, if of combustible construction, shall have a fire-resistance rating not less than 45 min,

b)   mezzanines shall have, if of combustible construction, a fire-resistance rating not less than 45 min, and

c)   loadbearing walls, columns and arches supporting an assembly required to have a fire-resistance rating shall

i)   have a fire-resistance rating not less than 45 min, or

ii)   be of noncombustible construction.

3.2.2.64. Group D, up to 2 Storeys

1)   A building classified as Group D is permitted to conform to Sentence (2) provided

a)   it is not more than 2 storeys in building height, and

b)   it has a building area not more than the value in Table 3.2.2.64.

Table 3.2.2.64.

Maximum Building Area, Group D, up to 2 Storeys

Forming Part of Sentence 3.2.2.64.(1)

| No. of Storeys | Maximum Area, m2 |  |  |
| --- | --- | --- | --- |
|  | Facing 1 Street | Facing 2 Streets | Facing 3 Streets |
| 1 | 1 000 | 1 250 | 1 500 |
| 2 | 800 | 1 000 | 1 200 |

2)   The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and

a)   floor assemblies shall be fire separations and, if of combustible construction, shall have a fire-resistance rating not less than 45 min, and

b)   loadbearing walls, columns and arches supporting an assembly required to have a fire-resistance rating shall

i)   have a fire-resistance rating not less than 45 min, or

ii)   be of noncombustible construction.

3.2.2.65. Group D, up to 2 Storeys, Sprinklered

1)   A building classified as Group D is permitted to conform to Sentence (2) provided

a)   except as permitted by Sentences 3.2.2.7.(1) and 3.2.2.18.(2), the building is sprinklered throughout,

b)   it is not more than 2 storeys in building height, and

c)   it has a building area not more than

i)   3 000 m2 if 1 storey in building height, or

ii)   2 400 m2 if 2 storeys in building height.

2)   The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and

a)   floor assemblies shall be fire separations and, if of combustible construction, shall have a fire-resistance rating not less than 45 min, and

b)   loadbearing walls, columns and arches supporting an assembly required to have a fire-resistance rating shall

i)   have a fire-resistance rating not less than 45 min, or

ii)   be of noncombustible construction.

3.2.2.66. Group E, Any Height, Any Area, Sprinklered

1)   Except as permitted by Articles 3.2.2.67. to 3.2.2.71., a building classified as Group E shall conform to Sentence (2).

2)   Except as permitted by Article 3.2.2.16., the building referred to in Sentence (1) shall be of noncombustible construction, and

a)   except as permitted by Sentences 3.2.2.7.(1) and 3.2.2.18.(2), the building shall be sprinklered throughout,

b)   floor assemblies shall be fire separations with a fire-resistance rating not less than 2 h,

c)   mezzanines shall have a fire-resistance rating not less than 1 h, and

d)   loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

3.2.2.67. Group E, up to 4 Storeys, Sprinklered

1)   A building classified as Group E is permitted to conform to Sentence (2) provided

a)   except as permitted by Sentences 3.2.2.7.(1) and 3.2.2.18.(2), the building is sprinklered throughout,

b)   it is not more than 4 storeys in building height, and

c)   it has a building area not more than 1 800 m2.

2)   The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and

a)   floor assemblies shall be fire separations with a fire-resistance rating not less than 1 h,

b)   mezzanines shall have a fire-resistance rating not less than 1 h, and

c)   loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

3.2.2.68. Group E, up to 3 Storeys

1)   A building classified as Group E is permitted to conform to Sentence (2) provided

a)   it is not more than 3 storeys in building height, and

b)   it has a building area not more than the value in Table 3.2.2.68.

Table 3.2.2.68.

Maximum Building Area, Group E, up to 3 Storeys

Forming Part of Sentence 3.2.2.68.(1)

| No. of Storeys | Maximum Area, m2 |  |  |
| --- | --- | --- | --- |
|  | Facing 1 Street | Facing 2 Streets | Facing 3 Streets |
| 1 | 1 500 | 1 500 | 1 500 |
| 2 | 1 200 | 1 500 | 1 500 |
| 3 | 800 | 1 000 | 1 500 |

2)   The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and

a)   floor assemblies shall be fire separations with a fire-resistance rating not less than 45 min,

b)   mezzanines shall have, if of combustible construction, a fire-resistance rating not less than 45 min,

c)   roof assemblies shall have a fire-resistance rating not less than 45 min, except that in a building not more than 1 storey in building height, the fire-resistance rating is permitted to be waived provided the roof assembly is of noncombustible construction or is constructed as a fire-retardant-treated wood roof system conforming to Article 3.1.14.1.,

d)   loadbearing walls, columns and arches supporting an assembly required to have a fire-resistance rating shall

i)   have a fire-resistance rating not less than 45 min, or

ii)   be of noncombustible construction, and

e)   loadbearing walls, columns and arches supporting a fire separation shall have a fire-resistance rating not less than that required for the fire separation.

3.2.2.69. Group E, up to 3 Storeys, Sprinklered

1)   A building classified as Group E is permitted to conform to Sentence (2) provided

a)   except as permitted by Sentences 3.2.2.7.(1) and 3.2.2.18.(2), the building is sprinklered throughout,

b)   it is not more than 3 storeys in building height, and

c)   it has a building area not more than

i)   7 200 m2 if 1 storey in building height,

ii)   3 600 m2 if 2 storeys in building height, or

iii)   2 400 m2 if 3 storeys in building height.

2)   The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and

a)   floor assemblies shall be fire separations with a fire-resistance rating not less than 45 min,

b)   mezzanines shall have, if of combustible construction, a fire-resistance rating not less than 45 min,

c)   loadbearing walls, columns and arches supporting an assembly required to have a fire-resistance rating shall

i)   have a fire-resistance rating not less than 45 min, or

ii)   be of noncombustible construction, and

d)   loadbearing walls, columns and arches supporting a fire separation shall have a fire-resistance rating not less than that required for the fire separation.

3.2.2.70. Group E, up to 2 Storeys

1)   A building classified as Group E is permitted to conform to Sentence (2) provided

a)   it is not more than 2 storeys in building height, and

b)   it has a building area not more than the value in Table 3.2.2.70.

Table 3.2.2.70.

Maximum Building Area, Group E, up to 2 Storeys

Forming Part of Sentence 3.2.2.70.(1)

| No. of Storeys | Maximum Area, m2 |  |  |
| --- | --- | --- | --- |
|  | Facing 1 Street | Facing 2 Streets | Facing 3 Streets |
| 1 | 1 000 | 1 250 | 1 500 |
| 2 | 600 | 750 | 900 |

2)   The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and

a)   floor assemblies shall be fire separations with a fire-resistance rating not less than 45 min, and

b)   loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

3.2.2.71. Group E, up to 2 Storeys, Sprinklered

1)   A building classified as Group E is permitted to conform to Sentence (2) provided

a)   except as permitted by Sentences 3.2.2.7.(1) and 3.2.2.18.(2), the building is sprinklered throughout,

b)   it is not more than 2 storeys in building height, and

c)   it has a building area not more than

i)   3 000 m2 if 1 storey in building height, or

ii)   1 800 m2 if 2 storeys in building height.

2)   The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and

a)   floor assemblies shall be fire separations with a fire-resistance rating not less than 45 min, and

b)   loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

3.2.2.72. Group F, Division 1, up to 4 Storeys, Sprinklered

1)   Except as permitted by Articles 3.2.2.73. to 3.2.2.75., a building classified as Group F, Division 1 shall conform to Sentence (2) provided

a)   it is not more than 4 storeys in building height, and

b)   it has a building area not more than

i)   9 000 m2 if 1 storey in building height,

ii)   4 500 m2 if 2 storeys in building height,

iii)   3 000 m2 if 3 storeys in building height, or

iv)   2 250 m2 if 4 storeys in building height.

2)   Except as permitted by Article 3.2.2.16., the building referred to in Sentence (1) shall be of noncombustible construction, and

a)   except as permitted by Sentences 3.2.2.7.(1) and 3.2.2.18.(2), the building shall be sprinklered throughout,

b)   floor assemblies shall be fire separations with a fire-resistance rating not less than 2 h,

c)   mezzanines shall have a fire-resistance rating not less than 1 h, and

d)   loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

3.2.2.73. Group F, Division 1, up to 3 Storeys, Sprinklered

1)   A building classified as Group F, Division 1 is permitted to conform to Sentence (2) provided

a)   except as permitted by Sentences 3.2.2.7.(1) and 3.2.2.18.(2), the building is sprinklered throughout,

b)   it is not more than 3 storeys in building height, and

c)   it has a building area not more than

i)   3 600 m2 if 1 storey in building height,

ii)   1 800 m2 if 2 storeys in building height, or

iii)   1 200 m2 if 3 storeys in building height.

2)   The building referred to in Sentence (1) is permitted to be of heavy timber construction or noncombustible construction used singly or in combination, and

a)   floor assemblies shall be fire separations with a fire-resistance rating not less than 45 min, and

b)   loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

3.2.2.74. Group F, Division 1, up to 2 Storeys, Sprinklered

1)   A building classified as Group F, Division 1 is permitted to conform to Sentence (2) provided

a)   except as permitted by Sentences 3.2.2.7.(1) and 3.2.2.18.(2), the building is sprinklered throughout,

b)   it is not more than 2 storeys in building height, and

c)   it has a building area not more than

i)   2 400 m2 if 1 storey in building height, or

ii)   1 200 m2 if 2 storeys in building height.

2)   The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and

a)   floor assemblies shall be fire separations and, if of combustible construction, shall have a fire-resistance rating not less than 45 min, and

b)   loadbearing walls, columns and arches supporting an assembly required to have a fire-resistance rating shall

i)   have a fire-resistance rating not less than 45 min, or

ii)   be of noncombustible construction.

3.2.2.75. Group F, Division 1, One Storey

1)   A building classified as Group F, Division 1 is permitted to be of combustible construction or noncombustible construction used singly or in combination provided

a)   it is not more than 1 storey in building height, and

b)   it has a building area not more than 800 m2.

3.2.2.76. Group F, Division 2, Any Height, Any Area, Sprinklered

1)   Except as permitted by Articles 3.2.2.77. to 3.2.2.81., a building classified as Group F, Division 2 shall conform to Sentence (2).

2)   Except as permitted by Article 3.2.2.16., the building referred to in Sentence (1) shall be of noncombustible construction, and

a)   except as permitted by Sentences 3.2.2.7.(1) and 3.2.2.18.(2), the building shall be sprinklered throughout,

b)   floor assemblies shall be fire separations with a fire-resistance rating not less than 2 h,

c)   mezzanines shall have a fire-resistance rating not less than 1 h, and

d)   loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

3.2.2.77. Group F, Division 2, up to 4 Storeys, Increased Area, Sprinklered

1)   A building classified as Group F, Division 2 is permitted to conform to Sentence (2) provided

a)   except as permitted by Sentences 3.2.2.7.(1) and 3.2.2.18.(2), the building is sprinklered throughout,

b)   it is not more than 4 storeys in building height, and

c)   it has a building area not more than

i)   18 000 m2 if 1 storey in building height,

ii)   9 000 m2 if 2 storeys in building height,

iii)   6 000 m2 if 3 storeys in building height, or

iv)   4 500 m2 if 4 storeys in building height.

2)   Except as permitted by Article 3.2.2.16., the building referred to in Sentence (1) shall be of noncombustible construction, and

a)   floor assemblies shall be fire separations with a fire-resistance rating not less than 1 h,

b)   mezzanines shall have a fire-resistance rating not less than 1 h, and

c)   loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

3.2.2.78. Group F, Division 2, up to 3 Storeys

1)   A building classified as Group F, Division 2 is permitted to conform to Sentence (2) provided

a)   it is not more than 3 storeys in building height, and

b)   it has a building area not more than the value in Table 3.2.2.78.

Table 3.2.2.78.

Maximum Building Area, Group F, Division 2, up to 3 Storeys

Forming Part of Sentence 3.2.2.78.(1)

| No. of Storeys | Maximum Area, m2 |  |  |
| --- | --- | --- | --- |
|  | Facing 1 Street | Facing 2 Streets | Facing 3 Streets |
| 1 | 1 500 | 1 500 | 1 500 |
| 2 | 1 500 | 1 500 | 1 500 |
| 3 | 1 070 | 1 340 | 1 500 |

2)   The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and

a)   floor assemblies shall be fire separations with a fire-resistance rating not less than 45 min,

b)   mezzanines shall have, if of combustible construction, a fire-resistance rating not less than 45 min,

c)   roof assemblies shall have, if of combustible construction, a fire-resistance rating not less than 45 min, except that in a building not more than 1 storey in building height, the fire-resistance rating is permitted to be waived provided that the roof assembly is constructed as a fire-retardant-treated wood roof system conforming to Article 3.1.14.1.,

d)   loadbearing walls, columns and arches supporting an assembly required to have a fire-resistance rating shall

i)   have a fire-resistance rating not less than 45 min, or

ii)   be of noncombustible construction, and

e)   loadbearing walls, columns and arches supporting a fire separation shall have a fire-resistance rating not less than that required for the fire separation.

3.2.2.79. Group F, Division 2, up to 4 Storeys, Sprinklered

1)   A building classified as Group F, Division 2 is permitted to conform to Sentence (2) provided

a)   except as permitted by Sentences 3.2.2.7.(1) and 3.2.2.18.(2), the building is sprinklered throughout,

b)   it is not more than 4 storeys in building height, and

c)   it has a building area not more than

i)   9 600 m2 if 1 storey in building height,

ii)   4 800 m2 if 2 storeys in building height,

iii)   3 200 m2 if 3 storeys in building height, or

iv)   2 400 m2 if 4 storeys in building height.

2)   The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and

a)   floor assemblies shall be fire separations with a fire-resistance rating not less than 45 min,

b)   mezzanines shall have, if of combustible construction, a fire-resistance rating not less than 45 min,

c)   loadbearing walls, columns and arches supporting an assembly required to have a fire-resistance rating shall

i)   have a fire-resistance rating not less than 45 min, or

ii)   be of noncombustible construction, and

d)   loadbearing walls, columns and arches supporting a fire separation shall have a fire-resistance rating not less than that required for the fire separation.

3.2.2.80. Group F, Division 2, up to 2 Storeys

1)   A building classified as Group F, Division 2 is permitted to conform to Sentence (2) provided

a)   it is not more than 2 storeys in building height, and

b)   it has a building area not more than the value in Table 3.2.2.80.

Table 3.2.2.80.

Maximum Building Area, Group F, Division 2, up to 2 Storeys

Forming Part of Sentence 3.2.2.80.(1)

| No. of Storeys | Maximum Area, m2 |  |  |
| --- | --- | --- | --- |
|  | Facing 1 Street | Facing 2 Streets | Facing 3 Streets |
| 1 | 1 000 | 1 250 | 1 500 |
| 2 | 600 | 750 | 900 |

2)   The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and

a)   floor assemblies shall be fire separations and, if of combustible construction, shall have a fire-resistance rating not less than 45 min, and

b)   loadbearing walls, columns and arches supporting an assembly required to have a fire-resistance rating shall

i)   have a fire-resistance rating not less than 45 min, or

ii)   be of noncombustible construction.

3.2.2.81. Group F, Division 2, up to 2 Storeys, Sprinklered

1)   A building classified as Group F, Division 2 is permitted to conform to Sentence (2) provided

a)   except as permitted by Sentences 3.2.2.7.(1) and 3.2.2.18.(2), the building is sprinklered throughout,

b)   it is not more than 2 storeys in building height, and

c)   it has a building area not more than

i)   4 500 m2 if 1 storey in building height, or

ii)   1 800 m2 if 2 storeys in building height.

2)   The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and

a)   floor assemblies shall be fire separations and, if of combustible construction, shall have a fire-resistance rating not less than 45 min, and

b)   loadbearing walls, columns and arches supporting an assembly required to have a fire-resistance rating shall

i)   have a fire-resistance rating not less than 45 min, or

ii)   be of noncombustible construction.

3.2.2.82. Group F, Division 3, Any Height, Any Area, Sprinklered

1)   Except as permitted by Articles 3.2.2.83. to 3.2.2.92., a building classified as Group F, Division 3 shall conform to Sentence (2).

2)   Except as permitted by Article 3.2.2.16., the building referred to in Sentence (1) shall be of noncombustible construction, and

a)   except as permitted by Sentences 3.2.2.7.(1) and 3.2.2.18.(2), the building shall be sprinklered throughout,

b)   floor assemblies shall be fire separations with a fire-resistance rating not less than 2 h, except that floor assemblies are permitted to be fire separations with a fire-resistance rating not less than 1 h in a storage garage with all storeys constructed as open-air storeys,

c)   mezzanines shall have a fire-resistance rating not less than 1 h, and

d)   loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

3.2.2.83. Group F, Division 3, up to 6 Storeys

1)   A building classified as Group F, Division 3 is permitted to conform to Sentence (2), provided

a)   it is not more than 6 storeys in building height, and

b)   it has a building area not more than the value in Table 3.2.2.83.

Table 3.2.2.83.

Maximum Building Area, Group F, Division 3, up to 6 Storeys

Forming Part of Sentence 3.2.2.83.(1)

| No. of Storeys | Maximum Area, m2 |  |  |
| --- | --- | --- | --- |
|  | Facing 1 Street | Facing 2 Streets | Facing 3 Streets |
| 1 | not limited | not limited | not limited |
| 2 | 7 200 | 9 000 | 10 800 |
| 3 | 4 800 | 6 000 | 7 200 |
| 4 | 3 600 | 4 500 | 5 400 |
| 5 | 2 880 | 3 600 | 4 320 |
| 6 | 2 400 | 3 000 | 3 600 |

2)   The building referred to in Sentence (1) shall be of noncombustible construction, and

a)   floor assemblies shall be fire separations with a fire-resistance rating not less than 1 h,

b)   mezzanines shall have a fire-resistance rating not less than 1 h,

c)   roof assemblies shall have a fire-resistance rating not less than 1 h, and

d)   loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

3.2.2.84. Group F, Division 3, up to 6 Storeys, Sprinklered

1)   A building classified as Group F, Division 3 is permitted to conform to Sentence (2), provided

a)   except as permitted by Sentences 3.2.2.7.(1) and 3.2.2.18.(2), the building is sprinklered throughout,

b)   it is not more than 6 storeys in building height, and

c)   it has a building area

i)   that is not limited if the building is not more than 1 storey in building height,

ii)   not more than 21 600 m2 if 2 storeys in building height,

iii)   not more than 14 400 m2 if 3 storeys in building height,

iv)   not more than 10 800 m2 if 4 storeys in building height,

v)   not more than 8 640 m2 if 5 storeys in building height, or

vi)   not more than 7 200 m2 if 6 storeys in building height.

2)   Except as permitted by Article 3.2.2.16., the building referred to in Sentence (1) shall be of noncombustible construction, and

a)   floor assemblies shall be fire separations with a fire-resistance rating not less than 1 h,

b)   mezzanines shall have a fire-resistance rating not less than 1 h, and

c)   loadbearing walls, columns and arches shall have a fire-resistance rating not less than that required for the supported assembly.

3.2.2.85. Group F, Division 3, up to 4 Storeys

1)   A building classified as Group F, Division 3 is permitted to conform to Sentence (2) provided

a)   it is not more than 4 storeys in building height, and

b)   it has a building area not more than the value in Table 3.2.2.85.

Table 3.2.2.85.

Maximum Building Area, Group F, Division 3, up to 4 Storeys

Forming Part of Sentence 3.2.2.85.(1)

| No. of Storeys | Maximum Area, m2 |  |  |
| --- | --- | --- | --- |
|  | Facing 1 Street | Facing 2 Streets | Facing 3 Streets |
| 1 | 4 800 | 6 000 | 7 200 |
| 2 | 2 400 | 3 000 | 3 600 |
| 3 | 1 600 | 2 000 | 2 400 |
| 4 | 1 200 | 1 500 | 1 800 |

2)   The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and

a)   floor assemblies shall be fire separations and, if of combustible construction, shall have a fire-resistance rating not less than 45 min,

b)   mezzanines shall have, if of combustible construction, a fire-resistance rating not less than 45 min,

c)   roof assemblies shall have, if of combustible construction, a fire-resistance rating not less than 45 min, except that in a building not more than 1 storey in building height, the fire-resistance rating is permitted to be waived provided the roof assembly is constructed as a fire-retardant-treated wood roof system conforming to Article 3.1.14.1., and the building area is not more than

i)   2 400 m2 if facing one street,

ii)   3 000 m2 if facing 2 streets, or

iii)   3 600 m2 if facing 3 streets, and

d)   loadbearing walls, columns and arches supporting an assembly required to have a fire-resistance rating shall

i)   have a fire-resistance rating not less than 45 min, or

ii)   be of noncombustible construction.

3.2.2.86. Group F, Division 3, up to 4 Storeys, Sprinklered

1)   A building classified as Group F, Division 3 is permitted to conform to Sentence (2) provided

a)   except as permitted by Sentences 3.2.2.7.(1) and 3.2.2.18.(2), the building is sprinklered throughout,

b)   it is not more than 4 storeys in building height, and

c)   it has a building area not more than

i)   14 400 m2 if 1 storey in building height,

ii)   7 200 m2 if 2 storeys in building height,

iii)   4 800 m2 if 3 storeys in building height, or

iv)   3 600 m2 if 4 storeys in building height.

2)   The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and

a)   floor assemblies shall be fire separations and, if of combustible construction, shall have a fire-resistance rating not less than 45 min,

b)   mezzanines shall have, if of combustible construction, a fire-resistance rating not less than 45 min, and

c)   loadbearing walls, columns and arches supporting an assembly required to have a fire-resistance rating shall

i)   have a fire-resistance rating not less than 45 min, or

ii)   be of noncombustible construction.

3.2.2.87. Group F, Division 3, up to 2 Storeys

1)   A building classified as Group F, Division 3 is permitted to conform to Sentence (2) provided

a)   it is not more than 2 storeys in building height, and

b)   it has a building area not more than the value in Table 3.2.2.87.

Table 3.2.2.87.

Maximum Building Area, Group F, Division 3, up to 2 Storeys

Forming Part of Sentence 3.2.2.87.(1)

| No. of Storeys | Maximum Area, m2 |  |  |
| --- | --- | --- | --- |
|  | Facing 1 Street | Facing 2 Streets | Facing 3 Streets |
| 1 | 1 600 | 2 000 | 2 400 |
| 2 | 800 | 1 000 | 1 200 |

2)   The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and

a)   floor assemblies shall be fire separations and, if of combustible construction, shall have a fire-resistance rating not less than 45 min, and

b)   loadbearing walls, columns and arches supporting an assembly required to have a fire-resistance rating shall

i)   have a fire-resistance rating not less than 45 min, or

ii)   be of noncombustible construction.

3.2.2.88. Group F, Division 3, up to 2 Storeys, Sprinklered

1)   A building classified as Group F, Division 3 is permitted to conform to Sentence (2) provided

a)   except as permitted by Sentences 3.2.2.7.(1) and 3.2.2.18.(2), the building is sprinklered throughout,

b)   it is not more than 2 storeys in building height, and

c)   it has a building area not more than

i)   7 200 m2 if 1 storey in building height, or

ii)   2 400 m2 if 2 storeys in building height.

2)   The building referred to in Sentence (1) is permitted to be of combustible construction or noncombustible construction used singly or in combination, and

a)   floor assemblies shall be fire separations and, if of combustible construction, shall have a fire-resistance rating not less than 45 min, and

b)   loadbearing walls, columns and arches supporting an assembly required to have a fire-resistance rating shall

i)   have a fire-resistance rating not less than 45 min, or

ii)   be of noncombustible construction.

3.2.2.89. Group F, Division 3, One Storey

1)   A building classified as Group F, Division 3 is permitted to be of heavy timber construction or noncombustible construction used singly or in combination provided

a)   it is not more than 1 storey in building height, and

b)   it has a building area not more than

i)   5 600 m2 if facing one street,

ii)   7 000 m2 if facing 2 streets, or

iii)   8 400 m2 if facing 3 streets.

3.2.2.90. Group F, Division 3, One Storey, Sprinklered

1)   A building classified as Group F, Division 3 is permitted to be of heavy timber construction or noncombustible construction used singly or in combination provided

a)   except as permitted by Sentences 3.2.2.7.(1) and 3.2.2.18.(2), the building is sprinklered throughout,

b)   it is not more than 1 storey in building height, and

c)   it has a building area not more than 16 800 m2.

3.2.2.91. Group F, Division 3, One Storey, Any Area, Low Fire Load Occupancy

1)   A building classified as Group F, Division 3 is permitted to conform to Sentence (2) provided it is

a)   not more than 1 storey in building height,

b)   used solely for low fire load occupancies such as

i)   power generating plants, or

ii)   plants for the manufacture or storage of noncombustible materials, and

c)   not limited in building area.

2)   The building referred to in Sentence (1) shall be of noncombustible construction.

3.2.2.92. Group F, Division 3, Storage Garages up to 22 m High

1)   A building used as a storage garage with all storeys constructed as open-air storeys and having no other occupancy above it is permitted to have its floor, wall, ceiling and roof assemblies constructed without a fire-resistance rating provided it is

a)   of noncombustible construction,

b)   not more than 22 m high, measured between grade and the ceiling level of the top storey,

c)   not more than 10 000 m2 in building area, and

d)   designed so that every portion of each floor area is within 60 m of an exterior wall opening.

3.2.3. Spatial Separation and Exposure Protection

(See Note A-3.2.3.)

3.2.3.1. Limiting Distance and Area of Unprotected Openings

1)   Except as permitted by Articles 3.2.3.10. to 3.2.3.12., the area of unprotected openings in an exposing building face for the applicable limiting distance shall be not more than the value determined in accordance with

a)   Table 3.2.3.1.-B or 3.2.3.1.-C for an exposing building face conforming to Article 3.2.3.2. of a building or fire compartment which is not sprinklered, or

b)   Table 3.2.3.1.-D or 3.2.3.1.-E for an exposing building face conforming to Article 3.2.3.2. of a sprinklered fire compartment that is part of a building which is sprinklered in conformance with Section 3.2.

(See Note A-3.)

(See also Article 3.1.18.3.)

2)   The area of the unprotected openings in an exposing building face shall be the aggregate area of unprotected openings expressed as a percentage of the area of the exposing building face in Table 3.2.3.1.-B, 3.2.3.1.-C, 3.2.3.1.-D or 3.2.3.1.-E. (See Sentence 3.2.3.2.(1).)

3)   For the purpose of determining the type of construction and cladding and the fire-resistance rating of an exterior wall,

a)   the exposing building face shall be taken as the projection of the exterior wall onto a vertical plane located so that no portion of the exterior wall of the building or of a fire compartment, if the fire compartment complies with the requirements of Article 3.2.3.2., is between the vertical plane and the line to which the limiting distance is measured, and

b)   the area of unprotected openings shall be determined from Table 3.2.3.1.-B, 3.2.3.1.-C, 3.2.3.1.-D or 3.2.3.1.-E.

4)   For the purpose of determining the actual percentage of unprotected openings permitted in an exterior wall, the location of the exposing building face is permitted to be taken at a vertical plane located so that there are no unprotected openings between the vertical plane and the line to which the limiting distance is measured. (See Note A-3.2.3.1.(4).)

5)   Except for buildings that are sprinklered, where the limiting distance is 2 m or less, individual unprotected openings in an exposing building face shall be no greater than

a)   the area stated in Table 3.2.3.1.-A, or

b)   where the limiting distance is equal to or greater than 1.2 m, the area calculated by

where

Area   = area of the unprotected opening, and

LD   = limiting distance.

Table 3.2.3.1.-A

Maximum Concentrated Area of Unprotected Openings

Forming Part of Sentence 3.2.3.1.(5)

| Limiting Distance, m | Maximum Area of Individual Unprotected Openings, m2 |
| --- | --- |
| 1.2 | 0.35 |
| 1.5 | 0.78 |
| 2.0 | 1.88 |

6)   The spacing between individual unprotected openings described in Sentence (5) that serve a single room or space described in Sentence (7) shall not be less than

a)   2 m horizontally of another unprotected opening that is on the same exposing building face and serves the single room or space, or

b)   2 m vertically of another unprotected opening that serves the single room or space, or another room or space on the same storey.

7)   For the purpose of Sentence (6), “single room or space” shall mean

a)   two or more adjacent spaces having a full-height separating wall extending less than 1.5 m from the interior face of the exterior wall, or

b)   two or more stacked spaces that are on the same storey.

8)   A limiting distance equal to half the actual limiting distance shall be used as input to Tables 3.2.3.1.-B and 3.2.3.1.-C, where

a)   the time from receipt of notification of a fire by the fire department until the arrival of the first fire department vehicle at the building exceeds 10 min in 10% or more of all fire department calls to the building, and

b)   any storey in the building is not sprinklered.

(See Notes A-3.2.3.1.(8) and A-3.2.3.)

9)   If the surface temperature on the unexposed surface of a wall assembly exceeds the temperature limit of a standard fire test as permitted by Article 3.1.7.2., an allowance shall be made for the radiation from the hot unexposed wall surface by adding an equivalent area of unprotected opening to the area of actual openings as follows:

where

AC   = corrected area of unprotected openings including actual and equivalent openings,

A   = actual area of unprotected openings,

AF   = area of exterior surface of the exposing building face, exclusive of openings, on which the temperature limit of the standard test is exceeded, and

FEO   = an equivalent opening factor derived from the following expression:

Tu   = average temperature in degrees Celsius of the unexposed wall surface at the time the required fire-resistance rating is reached under test conditions,

Te   = 892°C for a fire-resistance rating not less than 45 min, 927°C for a fire-resistance rating not less than 1 h, and 1 010°C for a fire-resistance rating not less than 2 h.

10)   Unless a closure used to protect an opening in an exposing building face has a protective performance equivalent to that required for the wall assembly in which it is located, an equivalent area of unprotected opening, determined in accordance with the procedures of Sentence (9) shall be added to the greater of

a)   the actual area of unprotected openings, or

b)   the corrected area of unprotected openings.

Table 3.2.3.1.-B

Unprotected Opening Limits for a Building or Fire Compartment that is not Sprinklered Throughout

Forming Part of Article 3.2.3.1.

| Exposing Building Face |  | Area of Unprotected Opening for Groups A, C, D, and F, Division 3 Occupancies, % |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Max. Area, m2 | Ratio (L/H or H/L)(1) | Limiting Distance, m |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | 0 | 1.2 | 1.5 | 2.0 | 2.5 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 16 | 18 | 20 | 25 | 30 | 35 | 40 | 45 | 50 |
|  | Less than 3 : 1 | 0 | 8 | 10 | 18 | 29 | 46 | 91 | 100 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 10 | 3 : 1 to 10 : 1 | 0 | 8 | 12 | 21 | 33 | 50 | 96 | 100 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | over 10 : 1 | 0 | 11 | 18 | 32 | 48 | 68 | 100 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Less than 3 : 1 | 0 | 7 | 9 | 14 | 22 | 33 | 63 | 100 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 15 | 3 : 1 to 10 : 1 | 0 | 8 | 10 | 17 | 25 | 37 | 67 | 100 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | over 10 : 1 | 0 | 10 | 15 | 26 | 39 | 53 | 87 | 100 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Less than 3 : 1 | 0 | 7 | 9 | 12 | 18 | 26 | 49 | 81 | 100 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 20 | 3 : 1 to 10 : 1 | 0 | 8 | 10 | 15 | 21 | 30 | 53 | 85 | 100 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | over 10 : 1 | 0 | 9 | 14 | 23 | 33 | 45 | 72 | 100 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Less than 3 : 1 | 0 | 7 | 8 | 11 | 16 | 23 | 41 | 66 | 98 | 100 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 25 | 3 : 1 to 10 : 1 | 0 | 8 | 9 | 13 | 19 | 26 | 45 | 70 | 100 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | over 10 : 1 | 0 | 9 | 13 | 21 | 30 | 39 | 62 | 90 | 100 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Less than 3 : 1 | 0 | 7 | 8 | 11 | 15 | 20 | 35 | 56 | 83 | 100 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 30 | 3 : 1 to 10 : 1 | 0 | 7 | 9 | 12 | 17 | 23 | 39 | 61 | 88 | 100 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | over 10 : 1 | 0 | 8 | 12 | 19 | 27 | 36 | 56 | 79 | 100 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Less than 3 : 1 | 0 | 7 | 8 | 10 | 13 | 17 | 28 | 44 | 64 | 89 | 100 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 40 | 3 : 1 to 10 : 1 | 0 | 7 | 8 | 11 | 15 | 20 | 32 | 48 | 69 | 93 | 100 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | over 10 : 1 | 0 | 8 | 11 | 17 | 24 | 31 | 47 | 66 | 88 | 100 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Less than 3 : 1 | 0 | 7 | 8 | 9 | 12 | 15 | 24 | 37 | 53 | 72 | 96 | 100 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 50 | 3 : 1 to 10 : 1 | 0 | 7 | 8 | 10 | 14 | 18 | 28 | 41 | 57 | 77 | 100 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | over 10 : 1 | 0 | 8 | 10 | 15 | 21 | 28 | 41 | 57 | 76 | 97 | 100 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Less than 3 : 1 | 0 | 7 | 8 | 9 | 11 | 14 | 21 | 32 | 45 | 62 | 81 | 100 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 60 | 3 : 1 to 10 : 1 | 0 | 7 | 8 | 10 | 13 | 16 | 25 | 36 | 49 | 66 | 85 | 100 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | over 10 : 1 | 0 | 8 | 10 | 14 | 20 | 25 | 38 | 51 | 67 | 85 | 100 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Less than 3 : 1 | 0 | 7 | 7 | 8 | 10 | 12 | 18 | 26 | 36 | 48 | 62 | 79 | 98 | 100 |  |  |  |  |  |  |  |  |  |  |  |  |
| 80 | 3 : 1 to 10 : 1 | 0 | 7 | 8 | 9 | 11 | 14 | 21 | 29 | 40 | 52 | 67 | 84 | 100 |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | over 10 : 1 | 0 | 8 | 9 | 13 | 17 | 22 | 32 | 44 | 56 | 70 | 86 | 100 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Less than 3 : 1 | 0 | 7 | 7 | 8 | 9 | 11 | 16 | 22 | 30 | 40 | 51 | 65 | 80 | 97 | 100 |  |  |  |  |  |  |  |  |  |  |  |
| 100 | 3 : 1 to 10 : 1 | 0 | 7 | 8 | 9 | 11 | 13 | 18 | 25 | 34 | 44 | 56 | 69 | 84 | 100 |  |  |  |  |  |  |  |  |  |  |  |  |
|  | over 10 : 1 | 0 | 7 | 9 | 12 | 16 | 20 | 29 | 39 | 49 | 61 | 74 | 89 | 100 |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Less than 3 : 1 | 0 | 7 | 7 | 8 | 9 | 10 | 13 | 17 | 22 | 29 | 37 | 46 | 56 | 67 | 79 | 93 | 100 |  |  |  |  |  |  |  |  |  |
| 150 | 3 : 1 to 10 : 1 | 0 | 7 | 7 | 8 | 10 | 11 | 15 | 20 | 26 | 33 | 41 | 50 | 60 | 71 | 84 | 97 | 100 |  |  |  |  |  |  |  |  |  |
|  | over 10 : 1 | 0 | 7 | 8 | 11 | 13 | 17 | 24 | 31 | 39 | 48 | 57 | 68 | 79 | 91 | 100 |  |  |  |  |  |  |  |  |  |  |  |
|  | Less than 3 : 1 | 0 | 7 | 7 | 7 | 8 | 9 | 10 | 13 | 16 | 20 | 25 | 30 | 36 | 43 | 51 | 59 | 68 | 87 | 100 |  |  |  |  |  |  |  |
| 250 | 3 : 1 to 10 : 1 | 0 | 7 | 7 | 8 | 9 | 10 | 12 | 15 | 19 | 24 | 28 | 34 | 40 | 47 | 55 | 63 | 72 | 92 | 100 |  |  |  |  |  |  |  |
|  | over 10 : 1 | 0 | 7 | 8 | 9 | 11 | 14 | 19 | 24 | 30 | 36 | 43 | 50 | 57 | 65 | 73 | 82 | 92 | 100 |  |  |  |  |  |  |  |  |
|  | Less than 3 : 1 | 0 | 7 | 7 | 7 | 8 | 8 | 9 | 11 | 14 | 16 | 20 | 24 | 28 | 33 | 38 | 44 | 50 | 64 | 81 | 99 | 100 |  |  |  |  |  |
| 350 | 3 : 1 to 10 : 1 | 0 | 7 | 7 | 8 | 8 | 9 | 11 | 13 | 16 | 19 | 23 | 27 | 32 | 37 | 42 | 48 | 55 | 69 | 85 | 100 |  |  |  |  |  |  |
|  | over 10 : 1 | 0 | 7 | 8 | 9 | 10 | 12 | 16 | 21 | 25 | 30 | 36 | 41 | 47 | 53 | 59 | 66 | 73 | 88 | 100 |  |  |  |  |  |  |  |
|  | Less than 3 : 1 | 0 | 7 | 7 | 7 | 7 | 8 | 9 | 10 | 12 | 14 | 16 | 19 | 22 | 25 | 29 | 33 | 37 | 47 | 59 | 71 | 100 |  |  |  |  |  |
| 500 | 3 : 1 to 10 : 1 | 0 | 7 | 7 | 7 | 8 | 8 | 10 | 12 | 14 | 16 | 19 | 22 | 25 | 29 | 33 | 37 | 41 | 52 | 63 | 76 | 100 |  |  |  |  |  |
|  | over 10 : 1 | 0 | 7 | 7 | 8 | 9 | 11 | 14 | 18 | 22 | 25 | 30 | 34 | 38 | 43 | 48 | 53 | 58 | 70 | 82 | 96 | 100 |  |  |  |  |  |
|  | Less than 3 : 1 | 0 | 7 | 7 | 7 | 7 | 7 | 8 | 9 | 9 | 10 | 12 | 13 | 14 | 16 | 18 | 20 | 22 | 27 | 33 | 39 | 58 | 82 | 100 |  |  |  |
| 1 000 | 3 : 1 to 10 : 1 | 0 | 7 | 7 | 7 | 7 | 8 | 9 | 10 | 11 | 12 | 14 | 15 | 17 | 19 | 21 | 23 | 26 | 31 | 37 | 43 | 63 | 86 | 100 |  |  |  |
|  | over 10 : 1 | 0 | 7 | 7 | 8 | 8 | 9 | 11 | 13 | 16 | 19 | 21 | 24 | 27 | 30 | 33 | 36 | 39 | 46 | 53 | 60 | 82 | 100 |  |  |  |  |
|  | Less than 3 : 1 | 0 | 7 | 7 | 7 | 7 | 7 | 7 | 8 | 8 | 9 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 17 | 20 | 23 | 33 | 44 | 58 | 74 | 93 | 100 |
| 2 000 | 3 : 1 to 10 : 1 | 0 | 7 | 7 | 7 | 7 | 7 | 8 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 20 | 23 | 27 | 37 | 49 | 63 | 79 | 97 | 100 |
|  | over 10 : 1 | 0 | 7 | 7 | 7 | 8 | 8 | 9 | 11 | 12 | 14 | 16 | 18 | 19 | 21 | 23 | 25 | 27 | 32 | 36 | 40 | 53 | 66 | 82 | 99 | 100 |  |

Notes to Table 3.2.3.1.-B:

(1) Apply whichever ratio is greater.

L   = Length of exposing building face

H   = Height of exposing building face

Table 3.2.3.1.-C

Unprotected Opening Limits for a Building or Fire Compartment that is not Sprinklered Throughout

Forming Part of Article 3.2.3.1.

| Exposing Building Face |  | Area of Unprotected Openings for Groups E and F, Division 1 and 2 Occupancies, % |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Max. Area, m 2 | Ratio (L/H or H/L)(1) | Limiting Distance, m |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | 0 | 1.2 | 1.5 | 2.0 | 2.5 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 16 | 18 | 20 | 25 | 30 | 35 | 40 | 45 | 50 | 55 | 60 | 65 | 70 |
|  | Less than 3 : 1 | 0 | 4 | 5 | 9 | 15 | 23 | 46 | 77 | 100 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 10 | 3 : 1 to 10 : 1 | 0 | 4 | 6 | 10 | 17 | 25 | 48 | 79 | 100 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | over 10 : 1 | 0 | 5 | 9 | 16 | 24 | 34 | 58 | 91 | 100 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Less than 3 : 1 | 0 | 4 | 5 | 7 | 11 | 16 | 32 | 53 | 79 | 100 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 15 | 3 : 1 to 10 : 1 | 0 | 4 | 5 | 8 | 13 | 18 | 34 | 55 | 82 | 100 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | over 10 : 1 | 0 | 5 | 8 | 13 | 19 | 26 | 43 | 66 | 93 | 100 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Less than 3 : 1 | 0 | 4 | 4 | 6 | 9 | 13 | 25 | 40 | 61 | 85 | 100 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 20 | 3 : 1 to 10 : 1 | 0 | 4 | 5 | 7 | 11 | 15 | 27 | 43 | 63 | 87 | 100 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | over 10 : 1 | 0 | 5 | 7 | 11 | 17 | 22 | 36 | 53 | 74 | 99 | 100 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Less than 3 : 1 | 0 | 4 | 4 | 6 | 8 | 11 | 20 | 33 | 49 | 69 | 92 | 100 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 25 | 3 : 1 to 10 : 1 | 0 | 4 | 5 | 7 | 9 | 13 | 22 | 35 | 51 | 71 | 94 | 100 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | over 10 : 1 | 0 | 4 | 6 | 10 | 15 | 20 | 31 | 45 | 62 | 82 | 100 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Less than 3 : 1 | 0 | 4 | 4 | 5 | 7 | 10 | 18 | 28 | 42 | 58 | 77 | 100 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 30 | 3 : 1 to 10 : 1 | 0 | 4 | 4 | 6 | 9 | 12 | 20 | 30 | 44 | 60 | 80 | 100 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | over 10 : 1 | 0 | 4 | 6 | 10 | 14 | 18 | 28 | 40 | 54 | 71 | 91 | 100 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Less than 3 : 1 | 0 | 4 | 4 | 5 | 6 | 8 | 14 | 22 | 32 | 44 | 59 | 76 | 94 | 100 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 40 | 3 : 1 to 10 : 1 | 0 | 4 | 4 | 6 | 8 | 10 | 16 | 24 | 34 | 47 | 61 | 78 | 97 | 100 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | over 10 : 1 | 0 | 4 | 5 | 8 | 12 | 15 | 23 | 33 | 44 | 57 | 72 | 89 | 100 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Less than 3 : 1 | 0 | 4 | 4 | 5 | 6 | 7 | 12 | 18 | 26 | 36 | 48 | 61 | 76 | 93 | 100 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 50 | 3 : 1 to 10 : 1 | 0 | 4 | 4 | 5 | 7 | 9 | 14 | 20 | 29 | 38 | 50 | 63 | 79 | 95 | 100 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | over 10 : 1 | 0 | 4 | 5 | 8 | 11 | 14 | 21 | 29 | 38 | 48 | 61 | 74 | 90 | 100 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Less than 3 : 1 | 0 | 4 | 4 | 4 | 5 | 7 | 11 | 16 | 23 | 31 | 40 | 52 | 64 | 78 | 94 | 100 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 60 | 3 : 1 to 10 : 1 | 0 | 4 | 4 | 5 | 6 | 8 | 12 | 18 | 25 | 33 | 43 | 54 | 66 | 81 | 96 | 100 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | over 10 : 1 | 0 | 4 | 5 | 7 | 10 | 13 | 19 | 26 | 34 | 43 | 53 | 64 | 77 | 92 | 100 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Less than 3 : 1 | 0 | 4 | 4 | 4 | 5 | 6 | 9 | 13 | 18 | 24 | 31 | 40 | 49 | 60 | 71 | 84 | 98 | 100 |  |  |  |  |  |  |  |  |  |  |  |  |
| 80 | 3 : 1 to 10 : 1 | 0 | 4 | 4 | 5 | 6 | 7 | 10 | 15 | 20 | 26 | 33 | 42 | 51 | 62 | 74 | 86 | 100 |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | over 10 : 1 | 0 | 4 | 5 | 6 | 9 | 11 | 16 | 22 | 28 | 35 | 43 | 52 | 62 | 73 | 85 | 98 | 100 |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Less than 3 : 1 | 0 | 4 | 4 | 4 | 5 | 5 | 8 | 11 | 15 | 20 | 26 | 32 | 40 | 48 | 58 | 68 | 79 | 100 |  |  |  |  |  |  |  |  |  |  |  |  |
| 100 | 3 : 1 to 10 : 1 | 0 | 4 | 4 | 4 | 5 | 6 | 9 | 13 | 17 | 22 | 28 | 35 | 42 | 51 | 60 | 70 | 81 | 100 |  |  |  |  |  |  |  |  |  |  |  |  |
|  | over 10 : 1 | 0 | 4 | 4 | 6 | 8 | 10 | 14 | 19 | 25 | 31 | 37 | 44 | 52 | 61 | 71 | 81 | 92 | 100 |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Less than 3 : 1 | 0 | 4 | 4 | 4 | 4 | 5 | 6 | 8 | 11 | 14 | 18 | 23 | 28 | 33 | 40 | 46 | 54 | 70 | 89 | 100 |  |  |  |  |  |  |  |  |  |  |
| 150 | 3 : 1 to 10 : 1 | 0 | 4 | 4 | 4 | 5 | 6 | 8 | 10 | 13 | 16 | 20 | 25 | 30 | 36 | 42 | 49 | 56 | 73 | 92 | 100 |  |  |  |  |  |  |  |  |  |  |
|  | over 10 : 1 | 0 | 4 | 4 | 5 | 7 | 8 | 12 | 16 | 20 | 24 | 29 | 34 | 39 | 46 | 52 | 59 | 67 | 84 | 100 |  |  |  |  |  |  |  |  |  |  |  |
|  | Less than 3 : 1 | 0 | 4 | 4 | 4 | 4 | 4 | 5 | 7 | 8 | 10 | 12 | 15 | 18 | 22 | 25 | 29 | 34 | 44 | 55 | 68 | 100 |  |  |  |  |  |  |  |  |  |
| 250 | 3 : 1 to 10 : 1 | 0 | 4 | 4 | 4 | 4 | 5 | 6 | 8 | 10 | 12 | 14 | 17 | 20 | 24 | 27 | 32 | 36 | 46 | 57 | 70 | 100 |  |  |  |  |  |  |  |  |  |
|  | over 10 : 1 | 0 | 4 | 4 | 5 | 6 | 7 | 9 | 12 | 15 | 18 | 21 | 25 | 28 | 32 | 37 | 41 | 46 | 56 | 68 | 81 | 100 |  |  |  |  |  |  |  |  |  |
|  | Less than 3 : 1 | 0 | 4 | 4 | 4 | 4 | 4 | 5 | 6 | 7 | 8 | 10 | 12 | 14 | 16 | 19 | 22 | 25 | 32 | 40 | 49 | 77 | 100 |  |  |  |  |  |  |  |  |
| 350 | 3 : 1 to 10 : 1 | 0 | 4 | 4 | 4 | 4 | 4 | 5 | 7 | 8 | 10 | 12 | 14 | 16 | 18 | 21 | 24 | 27 | 34 | 43 | 52 | 79 | 100 |  |  |  |  |  |  |  |  |
|  | over 10 : 1 | 0 | 4 | 4 | 4 | 5 | 6 | 8 | 10 | 13 | 15 | 18 | 21 | 23 | 26 | 30 | 33 | 36 | 44 | 53 | 62 | 90 | 100 |  |  |  |  |  |  |  |  |
|  | Less than 3 : 1 | 0 | 4 | 4 | 4 | 4 | 4 | 4 | 5 | 6 | 7 | 8 | 9 | 11 | 13 | 14 | 16 | 19 | 24 | 29 | 36 | 55 | 78 | 100 |  |  |  |  |  |  |  |
| 500 | 3 : 1 to 10 : 1 | 0 | 4 | 4 | 4 | 4 | 4 | 5 | 6 | 7 | 8 | 9 | 11 | 13 | 14 | 16 | 18 | 21 | 26 | 31 | 38 | 57 | 80 | 100 |  |  |  |  |  |  |  |
|  | over 10 : 1 | 0 | 4 | 4 | 4 | 5 | 5 | 7 | 9 | 11 | 13 | 15 | 17 | 19 | 21 | 24 | 26 | 29 | 35 | 41 | 48 | 68 | 92 | 100 |  |  |  |  |  |  |  |
|  | Less than 3 : 1 | 0 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 5 | 5 | 6 | 6 | 7 | 8 | 9 | 10 | 11 | 14 | 16 | 20 | 29 | 41 | 55 | 71 | 89 | 100 |  |  |  |  |
| 1 000 | 3 : 1 to 10 : 1 | 0 | 4 | 4 | 4 | 4 | 4 | 4 | 5 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 15 | 18 | 22 | 31 | 43 | 57 | 73 | 91 | 100 |  |  |  |  |
|  | over 10 : 1 | 0 | 4 | 4 | 4 | 4 | 5 | 6 | 7 | 8 | 9 | 11 | 12 | 13 | 15 | 16 | 18 | 20 | 23 | 26 | 30 | 41 | 53 | 68 | 84 | 100 |  |  |  |  |  |
|  | Less than 3 : 1 | 0 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 5 | 5 | 5 | 6 | 6 | 7 | 7 | 9 | 10 | 12 | 16 | 22 | 29 | 37 | 46 | 56 | 68 | 80 | 94 | 100 |
| 2 000 | 3 : 1 to 10 : 1 | 0 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 5 | 5 | 5 | 6 | 6 | 7 | 7 | 8 | 9 | 10 | 12 | 13 | 18 | 24 | 31 | 39 | 49 | 59 | 70 | 83 | 96 | 100 |
|  | over 10 : 1 | 0 | 4 | 4 | 4 | 4 | 4 | 5 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 16 | 18 | 20 | 26 | 33 | 41 | 50 | 59 | 70 | 81 | 94 | 100 |  |

Notes to Table 3.2.3.1.-C:

(1) Apply whichever ratio is greater.

L   = Length of exposing building face

H   = Height of exposing building face

Table 3.2.3.1.-D

Unprotected Opening Limits for a Building or Fire Compartment that is Sprinklered Throughout

Forming Part of Sentence 3.1.6.9.(5) and Article 3.2.3.1.

| Exposing Building Face | Area of Unprotected Opening for Groups A, B, C, D and F, Division 3 Occupancies, % |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Max. Area, m2 | Limiting Distance, m |  |  |  |  |  |  |  |  |  |  |  |
|  | 0 | 1.2 | 1.5 | 2.0 | 2.5 | 3 | 4 | 5 | 6 | 7 | 8 | 9 |
| 10 | 0 | 16 | 24 | 42 | 66 | 100 |  |  |  |  |  |  |
| 15 | 0 | 16 | 20 | 34 | 50 | 74 | 100 |  |  |  |  |  |
| 20 | 0 | 16 | 20 | 30 | 42 | 60 | 100 |  |  |  |  |  |
| 25 | 0 | 16 | 18 | 26 | 38 | 52 | 90 | 100 |  |  |  |  |
| 30 | 0 | 14 | 18 | 24 | 34 | 46 | 78 | 100 |  |  |  |  |
| 40 | 0 | 14 | 16 | 22 | 30 | 40 | 64 | 96 | 100 |  |  |  |
| 50 | 0 | 14 | 16 | 20 | 28 | 36 | 56 | 82 | 100 |  |  |  |
| 60 | 0 | 14 | 16 | 20 | 26 | 32 | 50 | 72 | 98 | 100 |  |  |
| 80 | 0 | 14 | 16 | 18 | 22 | 28 | 42 | 58 | 80 | 100 |  |  |
| 100 | 0 | 14 | 16 | 18 | 22 | 26 | 36 | 50 | 68 | 88 | 100 |  |
| 150 or more | 0 | 14 | 14 | 16 | 20 | 22 | 30 | 40 | 52 | 66 | 82 | 100 |

Table 3.2.3.1.-E

Unprotected Opening Limits for a Building or Fire Compartment that is Sprinklered Throughout

Forming Part of Sentence 3.1.6.9.(5) and Article 3.2.3.1.

| Exposing Building Face | Area of Unprotected Opening for Groups E and F, Division 1 and 2 Occupancies, % |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Max. Area, m2 | Limiting Distance, m |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | 0 | 1.2 | 1.5 | 2.0 | 2.5 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 |
| 10 | 0 | 8 | 12 | 20 | 34 | 50 | 96 | 100 |  |  |  |  |  |  |  |  |  |  |
| 15 | 0 | 8 | 10 | 16 | 26 | 36 | 68 | 100 |  |  |  |  |  |  |  |  |  |  |
| 20 | 0 | 8 | 10 | 14 | 22 | 30 | 54 | 86 | 100 |  |  |  |  |  |  |  |  |  |
| 25 | 0 | 8 | 10 | 14 | 18 | 26 | 44 | 70 | 100 |  |  |  |  |  |  |  |  |  |
| 30 | 0 | 8 | 8 | 12 | 18 | 24 | 40 | 60 | 88 | 100 |  |  |  |  |  |  |  |  |
| 40 | 0 | 8 | 8 | 12 | 16 | 20 | 32 | 48 | 68 | 94 | 100 |  |  |  |  |  |  |  |
| 50 | 0 | 8 | 8 | 10 | 14 | 18 | 28 | 40 | 58 | 76 | 100 |  |  |  |  |  |  |  |
| 60 | 0 | 8 | 8 | 10 | 12 | 16 | 24 | 36 | 50 | 66 | 86 | 100 |  |  |  |  |  |  |
| 80 | 0 | 8 | 8 | 10 | 12 | 14 | 20 | 30 | 40 | 52 | 66 | 84 | 100 |  |  |  |  |  |
| 100 | 0 | 8 | 8 | 8 | 10 | 12 | 18 | 26 | 34 | 44 | 56 | 70 | 84 | 100 |  |  |  |  |
| 150 | 0 | 8 | 8 | 8 | 10 | 12 | 16 | 20 | 26 | 32 | 40 | 50 | 60 | 72 | 84 | 98 | 100 |  |
| 200 or more | 0 | 8 | 8 | 8 | 8 | 10 | 14 | 18 | 22 | 28 | 34 | 42 | 50 | 60 | 68 | 80 | 92 | 100 |

3.2.3.2. Area of Exposing Building Face

1)   Except as permitted by Sentences (2) and (3), the area of an exposing building face shall be calculated as the total area of an exterior wall facing in one direction on any side of a building measured from the finished ground level to the uppermost ceiling.

2)   If a building is divided by fire separations into fire compartments, the area of exposing building face is permitted to be calculated for each fire compartment provided the fire separations have a fire-resistance rating not less than 45 min.

3)   In a building that is sprinklered throughout and contains an interconnected floor space, the area of the exposing building face for the interconnected floor space is permitted to be determined by considering each storey as a separate fire compartment notwithstanding openings through the floor assemblies.

3.2.3.3. Wall Enclosing Attic or Roof Space

1)   An exterior wall enclosing an attic or roof space and located above an exposing building face, shall be constructed in conformance with the requirements for the exposing building face.

3.2.3.4. Party Wall

1)   A party wall shall be constructed as a firewall. (See Note A-3.2.3.4.(1).)

3.2.3.5. Wall with Limiting Distance Less Than 1.2 m

1)   Openings in a wall that has a limiting distance less than 1.2 m shall be protected by closures whose fire-protection rating is in conformance with the fire-resistance rating required for the wall.

2)   Wired glass or glass block shall not be used for a closure referred to in Sentence (1).

3.2.3.6. Combustible Projections

1)   Except for a building containing one or two dwelling units only, combustible projections on the exterior of a wall that could expose an adjacent building to fire spread and are more than 1 m above ground level, including balconies, platforms, canopies and stairs, shall not be permitted within

a)   1.2 m of a property line or the centre line of a public way, or

b)   2.4 m of a combustible projection on another building on the same property.

2)   Except as provided in Sentence (4), where the exposing building face has a limiting distance of not more than 0.45 m, projecting roof soffits shall not be constructed above the exposing building face. (See Note A-3.2.3.6.(2).)

3)   Except as provided in Sentence (4), where the exposing building face has a limiting distance of more than 0.45 m, the face of roof soffits shall not project to less than 0.45 m from the property line. (See Note A-3.2.3.6.(2).)

4)   The face of a roof soffit is permitted to project to the property line, where it faces a public way. (See Note A-9.10.14.5.(11) and 9.10.15.5.(10).)

5)   Where roof soffits project to less than 1.2 m from the centre line of a public way, or from an imaginary line between two buildings or fire compartments on the same property, they shall

a)   have no openings, and

b)   be protected by

i)   not less than 0.38 mm thick sheet steel,

ii)   unvented aluminum conforming to CAN/CGSB-93.2-M, “Prefinished Aluminum Siding, Soffits, and Fascia, for Residential Use,”

iii)   not less than 12.7 mm thick gypsum soffit board or gypsum ceiling board installed according to CSA A82.31-M, “Gypsum Board Application,”

iv)   not less than 11 mm thick plywood,

v)   not less than 12.5 mm thick OSB or waferboard, or

vi)   not less than 11 mm thick lumber.

6)   For buildings of combustible construction, materials installed to provide the required protection of soffits may be covered with a combustible or noncombustible finish material.

3.2.3.7. Construction of Exposing Building Face

1)   Except as provided in Sentences (3) and (4), and Articles 3.2.3.10. and 3.2.3.11., the fire-resistance rating, construction and cladding for exposing building faces of buildings or fire compartments of Group A, B, C, D or Group F, Division 3 occupancy classification shall comply with Table 3.2.3.7.

2)   Except as provided in Sentences (3) and (4) and Article 3.2.3.10., the fire-resistance rating, construction and cladding for exposing building faces of buildings or fire compartments of Group E or Group F, Division 1 or 2 occupancy classification shall comply with Table 3.2.3.7.

Table 3.2.3.7.

Minimum Construction Requirements for Exposing Building Faces

Forming Part of Sentences 3.1.6.9.(5) and 3.2.3.7.(1) to (4)

| Occupancy Classification of Building or Fire Compartment | Maximum Area of Unprotected Openings Permitted, % of Exposing Building Face Area | Minimum Required Fire-Resistance Rating | Type of Construction Required | Type of Cladding Required |
| --- | --- | --- | --- | --- |
| Group A, B, C, D, or Group F, Division 3 | 0 to 10 | 1 h | Noncombustible | Noncombustible |
|  | > 10 to 25 | 1 h | Combustible, Encapsulated mass timber, or Noncombustible | Noncombustible |
|  | > 25 to 50 | 45 min | Combustible, Encapsulated mass timber, or Noncombustible | Noncombustible |
|  | > 50 to < 100 | 45 min | Combustible, Encapsulated mass timber, or Noncombustible | Combustible or Noncombustible(1)(2) |
| Group E, or Group F, Division 1 or 2 | 0 to 10 | 2 h | Noncombustible | Noncombustible |
|  | > 10 to 25 | 2 h | Combustible, Encapsulated mass timber, or Noncombustible | Noncombustible |
|  | > 25 to 50 | 1 h | Combustible, Encapsulated mass timber, or Noncombustible | Noncombustible |
|  | > 50 to < 100 | 1 h | Combustible, Encapsulated mass timber, or Noncombustible | Combustible or Noncombustible(3) |

Notes to Table 3.2.3.7.:

(1) The cladding on Group C buildings conforming to Article 3.2.2.51. and on Group D buildings conforming to Article 3.2.2.60. shall be noncombustible or consist of a wall that satisfies the requirements of Article 3.1.4.8.

(2) The cladding on Group C buildings or parts thereof conforming to Article 3.2.2.48. and on Group D buildings or parts thereof conforming to Article 3.2.2.57. shall conform to Sentence 3.1.6.9.(2) or be noncombustible.

(3) See also Article 3.1.4.8. for additional requirements for exterior cladding on buildings or parts thereof conforming to Articles 3.2.2.51. and 3.2.2.60.

3)   Except as provided in Articles 3.1.4.8. and 3.1.6.9., the requirement in Table 3.2.3.7. for noncombustible cladding for buildings or fire compartments where the maximum permitted area of unprotected openings is more than 10% of the exposing building face is permitted to be waived for exterior wall assemblies that comply with Article 3.1.5.5. or 3.1.5.6.

4)   Except as provided in Articles 3.1.4.8. and 3.1.6.9., the requirement in Table 3.2.3.7. for noncombustible cladding for buildings or fire compartments where the maximum permitted area of unprotected openings is more than 25% but not more than 50% of the exposing building face is permitted to be waived where

a)   the limiting distance is greater than 5 m,

b)   the building or fire compartment and all combustible attic and roof spaces are sprinklered throughout,

c)   the cladding

i)   conforms to Subsections 9.27.6., 9.27.7., 9.27.8., 9.27.9. or 9.27.10.,

ii)   is installed without furring members, or on furring not more than 25 mm thick, over gypsum sheathing at least 12.7 mm thick or over masonry, and

iii)   after conditioning in conformance with ASTM D2898, “Standard Practice for Accelerated Weathering of Fire-Retardant-Treated Wood for Fire Testing,” has a flame-spread rating not greater than 25 on the exterior face when tested in accordance with Sentence 3.1.12.1.(1),

d)   the cladding

i)   conforms to Subsection 9.27.12.,

ii)   is installed with or without furring members over gypsum sheathing at least 12.7 mm thick or over masonry,

iii)   has a flame-spread rating not greater than 25 when tested in accordance with Sentence 3.1.12.1.(2), and

iv)   does not exceed 2 mm in thickness, exclusive of fasteners, joints and local reinforcements (see Note A-3.2.3.7.(4)(d)(iv)), or

e)   the exterior wall assembly complies with Article 3.1.5.5. or 3.1.5.6.

5)   The construction requirements for the exposing building face stated in Sentences (1) and (2) shall be satisfied before increasing the unprotected opening area as permitted by Sentence 3.2.3.12.(1).

3.2.3.8. Protection of Exterior Building Face

1)   Except as permitted by Sentence (3) and in addition to the requirements of Sentences 3.2.3.7.(1) and (2) and where the maximum permitted area of unprotected openings is greater than 10% of the exposing building face, foamed plastic insulation used in an exterior wall of a building more than 3 storeys in building height shall be protected on its exterior surface by

a)   concrete or masonry not less than 25 mm thick, or

b)   noncombustible material that complies with the criteria for testing and the conditions of acceptance stated in Sentence (2) when tested in conformance with CAN/ULC-S101, “Standard Method of Fire Endurance Tests of Building Construction and Materials.”

2)   The criteria for testing and the conditions of acceptance for a wall assembly to satisfy the requirements of Clause (1)(b) are that

a)   the fire exposed area of the wall assembly shall be not less than 9.3 m2 and have no dimension less than 2.75 m,

b)   the exposed surface shall include typical vertical and horizontal joints,

c)   the test shall be continued for not less than 15 min and the standard time/temperature curve of the referenced standard shall be followed,

d)   the noncombustible protective material must remain in place and no through openings should develop that are visible when viewed normal to the face of the material, and

e)   the noncombustible protective material should not disintegrate in a manner that would permit fire to propagate along the surface of the test assembly.

3)   The requirements of Sentence (1) are waived for wall assemblies that comply with the requirements of Article 3.1.5.5. (See Note A-3.1.4.1.(1).)

3.2.3.9. Protection of Structural Members

1)   Structural members, including beams, columns and arches, that are placed wholly or partly outside the exterior face of a building and are less than 3 m from the property line or the centre line of a public thoroughfare shall be protected from exterior fire exposure by fire protection having a fire-resistance rating not less than that required for their protection from interior fire exposure, as stated in Articles 3.2.2.20. to 3.2.2.92., but not less than 1 h.

2)   Structural members of heavy timber construction, including beams, columns and arches, that are placed wholly or partly outside the exterior face of a building and are 3 m or more from the property line or the centre line of a public thoroughfare need not be covered with noncombustible cladding.

3.2.3.10. Unlimited Unprotected Openings

1)   An exposing building face in a storage garage with all storeys constructed as open-air storeys is permitted to have unlimited unprotected openings provided it has a limiting distance not less than 3 m.

2)   The exposing building face of a storey that faces a street and is at the same level as the street is permitted to have unlimited unprotected openings if the limiting distance is not less than 9 m.

3.2.3.11. Low Fire Load, One Storey Building

1)   An exposing building face of a building of low-hazard industrial occupancy conforming to Article 3.2.2.91. is permitted to be of noncombustible construction without a fire-resistance rating provided

a)   it is not a loadbearing wall, and

b)   the limiting distance is not less than 3 m.

3.2.3.12. Area Increase for Unprotected Openings

1)   Except as required by Sentence 3.2.3.7.(5), the maximum area of unprotected openings in any exposing building face of a building that is not sprinklered is permitted to be doubled if the openings are glazed with

a)   glass block conforming to the requirements of Article 3.1.8.16., or

b)   wired glass assemblies conforming to Article D-2.3.15. of Appendix D.

3.2.3.13. Protection of Exit Facilities

1)   Except as required by Sentence (3) and as permitted by Sentence 3.4.4.3.(1), if the plane of an exterior wall of an exit enclosure forms an angle less than 135° with the plane of an exterior wall of the building it serves, and an opening in the exterior wall of the exit enclosure could be exposed to fire from an opening in the exterior wall of the building, the opening in either the exterior wall of the exit or the exterior wall of the building shall be protected in conformance with the requirements of Sentence (4) where the opening in the exterior wall of the building is within 3 m horizontally and

a)   less than 10 m below an opening in the exterior wall of the exit, or

b)   less than 2 m above an opening in the exterior wall of the exit.

(See Note A-3.2.3.14.(1).)

2)   If an unenclosed exterior exit stair or ramp could be exposed to fire from an opening in the exterior wall of the building it serves, the opening in the exterior wall of the building shall be protected in conformance with the requirements of Sentence (4) where the opening in the exterior wall of the building is within 3 m horizontally and

a)   less than 10 m below the exit stair or ramp, or

b)   less than 5 m above the exit stair or ramp.

3)   Except as permitted by Sentence 3.4.4.3.(1), if an exterior exit door in one fire compartment is within 3 m horizontally of an opening in another fire compartment and the exterior walls of these fire compartments intersect at an exterior angle of less than 135°, the opening shall be protected in conformance with the requirements of Sentence (4).

4)   The opening protection referred to in Sentences (1) to (3) shall consist of

a)   glass block conforming to the requirements of Article 3.1.8.16.,

b)   a wired glass assembly conforming to Article D-2.3.15. of Appendix D, or

c)   a closure conforming to the requirements of Subsection 3.1.8. and Articles 3.2.3.1. and 3.2.3.14.

3.2.3.14. Wall Exposed to Another Wall

1)   Except as required by Sentences (3) and 3.2.3.13.(1) or as permitted by Sentence 3.2.3.19.(5), if an unprotected opening in an exterior wall of a fire compartment is exposed to an unprotected opening in the exterior wall of another fire compartment, and the planes of the 2 walls are parallel or at an angle less than 135°, measured from the exterior of the building, the unprotected openings in the 2 fire compartments shall be separated by a distance not less than Do where

but in no case less than 1 m, and

D   = the greater required limiting distance for the exposing building faces of the 2 fire compartments, and

θ   = the angle made by the intersecting planes of the exposing building faces of the 2 fire compartments (in the case where the exterior walls are parallel and face each other, θ = 0°).

(See Note A-3.2.3.14.(1).)

2)   The exterior wall of each fire compartment referred to in Sentence (1) within the distance, Do, shall have a fire-resistance rating not less than that required for the interior vertical fire separation between the fire compartment and the remainder of the building.

3)   Sentence (1) does not apply to unprotected openings of fire compartments within a building that is sprinklered throughout, but shall apply to

a)   unprotected openings of fire compartments on opposite sides of a firewall, and

b)   exposure from unprotected openings of a fire compartment that is not protected by an automatic sprinkler system.

3.2.3.15. Wall Exposed to Adjoining Roof

1)   Except as permitted by Sentence 3.2.3.19.(5), if a wall in a building is exposed to a fire hazard from an adjoining roof of a separate fire compartment that is not sprinklered in the same building, and the exposed wall contains windows within 3 storeys vertically and 5 m horizontally of the roof, the roof shall contain no skylights within 5 m of the exposed wall.

3.2.3.16. Protection of Soffits

1)   Except as permitted by Sentences (3) and (4), where there is a common attic or roof space above more than 2 suites of residential occupancy or above more than 2 patients' sleeping rooms, and the common attic or roof space projects beyond the exterior wall of the building, the soffit, and any opening in the soffit or other surface of the projection located within 2 500 mm of a window or door opening, shall be protected by

a)   noncombustible material

i)   not less than 0.38 mm thick, and

ii)   having a melting point not below 650°C,

b)   plywood not less than 11 mm thick,

c)   strandboard or waferboard not less than 12.5 mm thick, or

d)   lumber not less than 11 mm thick.

2)   The soffit protection required by Sentence (1) shall extend the full width of the opening and to not less than 1 200 mm on either side of it, and shall apply to all openings through the soffit within this limit.

3)   If an eave overhang is completely separated from the remainder of the attic or roof space by the use of fire blocks, the requirements of Sentence (1) do not apply.

4)    The protection required by Sentence (1) for projections is permitted to be omitted if

a)   the fire compartments behind the window and door openings are sprinklered in accordance with Article 3.2.5.12., and

b)   all rooms, including closets and bathrooms, having openings in the wall beneath the soffit are sprinklered, notwithstanding exceptions permitted in the standards referenced in Article 3.2.5.12. for the installation of automatic sprinkler systems.

3.2.3.17. Canopy Protection for Vertically Separated Openings

1)   Except as permitted by Sentences (2) and (3), if a storey classified as a Group E or Group F, Division 1 or 2 major occupancy is required to be separated from the storey above by a fire separation,

a)   every opening in the exterior wall of the lower storey that is located vertically below an opening in the storey above shall be separated from the storey above by a canopy projecting not less than 1 m from the face of the building at the intervening floor level, and

b)   the canopy required by Clause (a) shall have a fire-resistance rating not less than that required for the floor assembly but need not be more than 1 h, except as required elsewhere in this Subsection.

2)   Except as permitted by Sentence (3), the canopy required by Sentence (1) is permitted to be omitted if the exterior wall of the upper storey is recessed not less than 1 m behind the exterior wall containing the opening in the lower storey.

3)    The requirements of Sentences (1) and (2) are permitted to be waived if the building is sprinklered throughout.

3.2.3.18. Covered Vehicular Passageway

1)   A covered vehicular passageway designed as a receiving or shipping area shall be separated from every building or part of a building adjoining it by a fire separation having a fire-resistance rating not less than 1.5 h.

2)   A covered vehicular passageway constructed below grade shall be of noncombustible construction.

3.2.3.19. Walkway between Buildings

1)   Except as required by Sentence 3.2.3.20.(2), if buildings are connected by a walkway, each building shall be separated from the walkway by a fire separation with a fire-resistance rating not less than 45 min.

2)   Except as permitted by Sentence (4), a walkway connected to a building required to be of noncombustible construction shall also be of noncombustible construction.

3)   Except as provided in Sentence (4), a walkway connected to a building or part of a building permitted to be of encapsulated mass timber construction shall be of noncombustible construction or encapsulated mass timber construction.

4)   A walkway connected to a building required to be of noncombustible construction or to a building or part of a building permitted to be of encapsulated mass timber construction is permitted to be of heavy timber construction, provided

a)   not less than 50% of the area of any enclosing perimeter walls is open to the outdoors, and

b)   the walkway is at ground level.

5)   A walkway of noncombustible construction used only as a pedestrian thoroughfare need not conform to the requirements of Articles 3.2.3.14. and 3.2.3.15.

6)   A walkway between buildings shall be not more than 9 m wide.

3.2.3.20. Underground Walkway

1)   An underground walkway shall not be designed or used for any purpose other than pedestrian travel unless

a)   the purpose is acceptable to the authority having jurisdiction, and

b)   sprinklers are installed in any space in the walkway containing an occupancy.

2)   Buildings connected by an underground walkway shall be separated from the walkway by a fire separation with a fire-resistance rating not less than 1 h.

3)   An underground walkway shall be of noncombustible construction suitable for an underground location.

4)   In an underground walkway

a)   smoke barrier doors shall be installed at intervals of not more than 100 m, or

b)   the travel distance from the door of an adjacent room or space to the nearest exit shall be not more than one and a half times the least allowable travel distance to an exit for any of the adjacent occupancies as permitted by Sentence 3.4.2.5.(1).

5)   An underground walkway between buildings shall be not more than 9 m wide.

3.2.3.21. Storage and Process Equipment Located Outdoors

1)   Location of outdoor storage and outdoor process equipment in relation to buildings shall conform to Parts 3 and 4 of Division B of the British Columbia Fire Code.

3.2.3.22. Installation of Service Lines Under Buildings

1)   When a building is erected over existing buried flammable gas mains, such service lines shall be encased in gas-tight conduits in conformance with CAN/CSA-Z662, “Oil and gas pipeline systems.”

3.2.4. Fire Alarm and Detection Systems

(See Note A-3.2.4.)

3.2.4.1. Determination of Requirement for a Fire Alarm System

1)   Except as permitted in Sentences (2) and (3), a fire alarm system shall be installed in buildings in which an automatic sprinkler system is required by this Part.

2)   Buildings in which a sprinkler system is installed in accordance with NFPA 13D, “Standard for the Installation of Sprinkler Systems in One- and Two-Family Dwellings and Manufactured Homes,” need not comply with Sentence (1).

3)   Buildings that contain fewer than 9 sprinklers conforming to Sentence 3.2.5.12.(4) need not comply with Sentence (1).

4)   Except as permitted by Sentences (5), (6) and 3.2.4.2.(4), a fire alarm system shall be installed in a building that is not sprinklered throughout and that contains

a)   a contained use area,

b)   an impeded egress zone,

c)   more than 3 storeys, including the storeys below the first storey,

d)   a total occupant load more than 300, other than in open air seating areas,

e)   an occupant load more than 150 above or below the first storey, other than in open air seating areas,

f)   a school, college, or child care facility, including a daycare facility for children, with an occupant load more than 40,

g)   a licensed beverage establishment or a licensed restaurant, with an occupant load more than 150,

h)   a low-hazard industrial occupancy with an occupant load more than 75 above or below the first storey,

i)   a medium-hazard industrial occupancy with an occupant load more than 75 above or below the first storey,

j)   a residential occupancy with sleeping accommodation for more than 10 persons,

k)   a high-hazard industrial occupancy with an occupant load more than 25, or

l)   an occupant load more than 300 below an open air seating area.

5)   A fire alarm system is not required in a residential occupancy that is not sprinklered, where

a)   not more than 4 suites share a common means of egress, or

b)   each suite has direct access to an exterior exit facility leading to ground level.

6)   A fire alarm system is not required in a storage garage conforming to Article 3.2.2.92. that is contained in a building that is not sprinklered provided there are no other occupancies in the building.

3.2.4.2. Continuity of Fire Alarm System

1)   Except as permitted by Sentence (6), if there are openings through a firewall, other than those for piping, tubing, wiring and totally enclosed noncombustible raceways, the requirements in this Subsection shall apply to the floor areas on both sides of the firewall as if they were in the same building.

2)   Except as permitted by Sentence (4), if a building contains more than one major occupancy and a fire alarm system is required, a single system shall serve all occupancies.

3)   Except as permitted by Sentence (4), if a fire alarm system is required in any portion of a building, it shall be installed throughout the building.

4)   Except as required by Sentence (5), the requirements in this Subsection are permitted to be applied to each portion of a building not more than 3 storeys in building height, in which a vertical fire separation having a fire-resistance rating not less than 1 h separates the portion from the remainder of the building as if it were a separate building, provided there are no openings through the fire separation, other than those for piping, tubing, wiring and totally enclosed noncombustible raceways.

5)   The permission in Sentence (4) to consider separated portions of a building as separate buildings does not apply to service rooms and storage rooms.

6)   Buildings interconnected by walkways permitted in Articles 3.2.3.19. and 3.2.3.20. or by vestibules provided in conformance with Article 3.2.6.3. shall be treated as separate buildings for the purpose of fire alarm installation required by this Subsection.

3.2.4.3. Types of Fire Alarm Systems

1)   A fire alarm system shall be

a)   a single-stage system in a Group F, Division 1 occupancy,

b)   except as permitted in Clause (c), a 2-stage system in a Group B occupancy,

c)   a single- or 2-stage system in a Group B, Division 3 occupancy where the building is 3 storeys or less in building height, and

d)   a single- or 2-stage system in all other cases.

3.2.4.4. Description of Fire Alarm Systems

1)   A single stage fire alarm system shall, upon the operation of any manual station, waterflow detecting device, or fire detector, cause an alarm signal to sound on all audible signal devices in the system. (See Note A-3.2.4.4.(1).)

2)   A 2-stage fire alarm system shall

a)   cause an alert signal to sound upon the operation of any manual station, waterflow detecting device, or fire detector,

b)   automatically cause an alarm signal to sound if the alert signal is not acknowledged within 5 min of its initiation, and

c)   have manual stations, each of which is equipped so that the use of a key or other similar device causes an alarm signal to sound that continues to sound upon removal of the key or similar device from the manual station (see Note A-3.2.4.4.(2)(c)).

(See Note A-3.2.4.4.(2).)

3)   A 2-stage fire alarm system is permitted to be zone coded so that, upon the operation of any manual station, waterflow detecting device, or fire detector,

a)   a coded alert signal is sounded indicating the zone of alarm initiation,

b)   the coded alert signal is repeated in its entirety not less than 4 times, and

c)   a continuous alert signal is sounded upon completion of the coded signals referred to in Clause (b) and Sentence (4).

4)   If a second manual station, waterflow detecting device, or fire detector is operated in a fire alarm system with zone coding as permitted by Sentence (3), in a zone other than that for which the first alert signal was sounded, the coded alert signal for the first zone shall be completed before the coded alert signal for the second zone is repeated not less than 4 times.

3.2.4.5. Installation and Verification of Fire Alarm Systems

1)   Fire alarm systems, including the voice communication capability where provided, shall be installed in conformance with CAN/ULC-S524, “Standard for Installation of Fire Alarm Systems.”

2)   Fire alarm systems shall be verified in conformance with CAN/ULC-S537, “Standard for Verification of Fire Alarm Systems,” to ensure they are operating satisfactorily.

3.2.4.6. Silencing of Alarm Signals

1)   A fire alarm system shall be designed so that when an alarm signal is actuated, it cannot be silenced automatically before a period of time has elapsed that is not less than

a)   5 min for a building not required to be equipped with an annunciator, and

b)   20 min for any other building.

2)   Except as permitted by Sentence 3.2.4.18.(8) and Sentences 3.2.4.22.(2) and (3), a fire alarm system shall not incorporate manual silencing switches other than those installed inside the fire alarm control unit. (See Note A-3.2.4.6.(2).)

3.2.4.7. Signals to Fire Department

1)   A single stage fire alarm system installed in a building of assembly occupancy that has an occupant load more than 300 shall be designed to notify the fire department, in conformance with Sentence (4), that an alarm signal has been initiated.

2)   A fire alarm system that includes waterflow-indicating devices shall be designed to notify the fire department in conformance with Sentence (4) when an alarm is initiated.

3)   A 2-stage fire alarm system shall be designed to notify the fire department, in conformance with Sentence (4), that an alert signal has been initiated.

4)   Notification of the fire department, as required by Sentences (1) to (3), shall be provided in conformance with CAN/ULC-S561, “Standard for Installation and Services for Fire Signal Receiving Centres and Systems.” (See Note A-3.2.4.7.(4).)

5)   Where a single stage fire alarm system is installed in a building that is not sprinklered throughout and Sentence (1) does not apply, a legible notice that is not easily removed shall be affixed to the wall near each manual station stating

a)   that the fire department is to be notified in the event of a fire emergency, and

b)   the emergency telephone number for the municipality or for the fire department (see Note A-3.2.4.7.(5)(b)).

6)   Helicopter landing areas on roofs shall be provided with telephone extensions or means to notify the fire department.

3.2.4.8. Annunciator and Zone Indication

1)   Except as permitted by Sentences (3) to (5), an annunciator shall be installed in close proximity to a building entrance that faces a street or an access route for fire department vehicles that complies with Sentence 3.2.5.5.(1).

2)   Except as permitted by Sentence (6), the annunciator required by Sentence (1) shall have separate zone indication of the actuation of the alarm initiating devices in each

a)   floor area so that the area of coverage for each zone in a building that is not sprinklered is not more than 2 000 m2,

b)   floor area so that the area of coverage for each zone is neither

i)   more than one storey, nor

ii)   more than the system area limits specified in NFPA 13, “Standard for the Installation of Sprinkler Systems,”

c)   shaft required to be equipped with smoke detectors,

d)   air-handling system required to be equipped with smoke detectors,

e)   fire extinguishing system required by NFPA 96, “Standard for Ventilation Control and Fire Protection of Commercial Cooking Operations,”

f)   contained use area,

g)   impeded egress zone, and

h)   fire compartment required by Sentence 3.3.3.5.(2).

(See Note A-3.2.4.8.(2).)

3)   An annunciator need not be provided for a fire alarm system if not more than one zone indicator is required by Sentence (2).

4)   If an annunciator is not installed as part of a fire alarm system in conformance with Sentence (1), a visible and audible trouble signal device shall be provided inside the main entrance of the building.

5)   The requirements of Sentence (1) are waived in a building

a)   in which an automatic sprinkler system is not installed,

b)   that has an aggregate area for all storeys of not more than 2 000 m2, and

c)   that is not more than 3 storeys in building height.

6)   The area limits of Clause (2)(a) are waived for an interior undivided open space used as an arena, a rink, or a swimming pool provided that other spaces in the building that are separated from the open space are individually zoned in accordance with the requirements of Sentence (2).

7)   A fire alarm control unit installed in close proximity to a building entrance that faces a street or an access route for fire department vehicles that complies with Sentence 3.2.5.5.(1) is deemed to satisfy the requirement for an annunciator, provided all indicators required for an annunciator or trouble signal device are included on the control unit.

3.2.4.9. Electrical Supervision

1)   Electrical supervision shall be provided for a fire alarm system.

2)   If a fire alarm system in a building is required to have an annunciator by Sentence 3.2.4.8.(1), except for hose valves, all valves controlling water supplies in a standpipe system shall be equipped with an electrically supervised switch for transmitting a trouble signal to the annunciator in the event of movement of the valve handle.

3)   An automatic sprinkler system shall be electrically supervised to indicate a supervisory signal on the building fire alarm system annunciator for each of the following:

a)   movement of a valve handle that controls the supply of water to sprinklers,

b)   loss of excess water pressure required to prevent false alarms in a wet pipe system,

c)   loss of air pressure in a dry pipe system,

d)   loss of air pressure in a pressure tank,

e)   a significant change in water level in any water storage container used for firefighting purposes,

f)   loss of power to any automatically starting fire pump (see Note A-3.2.4.9.(3)(f)), and

g)   a temperature approaching the freezing point in any dry pipe valve enclosure or water storage container used for firefighting purposes.

4)   A fire pump shall be electrically supervised as stipulated in NFPA 20, “Standard for the Installation of Stationary Pumps for Fire Protection.”

5)   Heat-tracing cables installed on standpipe risers and sprinkler lines shall be electrically supervised by the fire alarm system for loss of power.

6)   Indication of a supervisory signal in accordance with Sentences (3) and (5) shall be transmitted to the fire department in conformance with Sentence 3.2.4.7.(4).

3.2.4.10. Fire Detectors

1)   Fire detectors required by this Code shall be connected to the fire alarm system.

2)   Except as permitted by Sentence (3), if a fire alarm system is required in a building that is not sprinklered, fire detectors shall be installed in the following spaces:

a)   storage rooms not within dwelling units,

b)   service rooms not within dwelling units,

c)   janitors' rooms,

d)   rooms in which hazardous substances are to be used or stored (see Note A-3.3.1.2.(1)),

e)   elevator hoistways and dumbwaiter shafts, and

f)   laundry rooms in buildings of residential occupancy, but not those within dwelling units.

3)   Fire detectors required by Sentence (2) need not be provided within floor areas that are sprinklered.

4)   Fire detectors required by Sentence (2) shall be installed in elevator hoistways and dumbwaiter shafts where a sprinkler system is not installed within the hoistway or shaft.

3.2.4.11. Smoke Detectors

1)   If a fire alarm system is installed, smoke detectors shall be installed in

a)   except as permitted in Sentence (2), each sleeping room and each corridor serving as part of a means of egress from sleeping rooms in portions of a building classified as a Group B major occupancy,

b)   each room in a contained use area and corridors serving those rooms,

c)   each corridor in portions of a building classified as a Group A, Division 1 major occupancy,

d)   each public corridor in portions of a building classified as a Group C major occupancy,

e)   each exit stair shaft other than those serving only a Group A, Division 4 major occupancy or an open storage garage,

f)   the vicinity of draft stops required by Article 3.2.8.6., and

g)   elevator machine rooms.

(See Note A-3.2.4.11.(1).)

2)   Smoke detectors need not be installed in sleeping rooms and in corridors serving the sleeping rooms within a suite of care occupancy where smoke alarms are installed in accordance with Article 3.2.4.20.

3)   Smoke detectors required in the sleeping rooms of a care, treatment or detention occupancy shall, upon actuation, provide an audible and visible signal to staff serving those rooms so that the room or location containing the actuated smoke detector can be easily identified. (See Note A-3.2.4.11.(3).)

4)   Smoke detectors required in Clause (1)(g) shall, upon actuation, recall the elevators served by the elevator machine room in which the smoke detector is installed.

5)   Except as permitted in Sentences (6) and (7), smoke detectors installed in buildings required to be equipped with a fire alarm system shall be located near the entrance to walkways described in Articles 3.2.3.19. and 3.2.3.20. or vestibules provided in conformance with Article 3.2.6.3.

6)   Smoke detectors installed at the entrance to the walkways in conformance with Article 3.1.8.14. shall be deemed to meet the requirements of Sentence (5).

7)   Smoke detectors required by Sentence (5) may be replaced with fire detectors in Group F occupancies where the smoke detectors may be subjected to false alarms due to the activities within the building.

3.2.4.12. Prevention of Smoke Circulation

1)   If a fire alarm system is installed, an air-handling system shall be designed to prevent the circulation of smoke upon a signal from a duct-type smoke detector if the air-handling system

a)   serves more than one storey,

b)   serves more than one suite in a storey, or

c)   serves more than one fire compartment required by Sentence 3.3.3.5.(2).

3.2.4.13. Vacuum Cleaning System Shutdown

1)   A central vacuum cleaning system in a building equipped with a fire alarm system shall be designed to shut down upon actuation of the fire alarm system.

3.2.4.14. Elevator Emergency Return

1)   Except as permitted by Sentence (3), in a building having elevators that serve storeys above the first storey and that are equipped with an automatic emergency recall feature, smoke detectors shall be installed in the elevator lobbies on the recall level so that when these smoke detectors are actuated, the elevators will automatically return directly to an alternate floor level.

2)   Smoke detectors required by Sentence (1) shall be designed as part of the building fire alarm system.

3)   The alternate floor recall feature required by Sentence (1) is not required if the floor area containing the recall level is sprinklered throughout.

3.2.4.15. System Monitoring

1)   An automatic sprinkler system shall be equipped with waterflow detecting devices and, if an annunciator is required by Article 3.2.4.8., shall be installed so that each device serves

a)   not more than one storey, and

b)   except as required by Sentence 3.2.4.8.(2), an area on each storey that is not more than the system area limits as specified in NFPA 13, “Standard for the Installation of Sprinkler Systems.”

2)   Waterflow-detecting devices required by Sentence (1) shall be connected to the fire alarm system so that, upon its actuation, an alert signal or an alarm signal is initiated.

3)   The actuation of each waterflow detecting device required by Sentence (1) shall be indicated separately on the fire alarm system annunciator.

3.2.4.16. Manual Stations

1)   Except as permitted by Sentences (2) and (3), where a fire alarm system is installed, a manual station shall be installed in every floor area near

a)   every principal entrance to the building, and

b)   every required exit, and

c)  every other egress facility that has been designed and identified as an exit and has all the features of a required exit.

(See Note A-3.2.4.16.(1).)

2)   In a building that is sprinklered throughout, a manual station is not required at an exterior egress doorway from a suite that does not lead to an interior shared means of egress in a hotel or motel not more than 3 storeys in building height, provided each suite is served by an exterior exit facility leading directly to ground level.

3)   In a building that is sprinklered throughout, a manual station is not required at an exterior egress doorway from a dwelling unit that does not lead to an interior shared means of egress in a building not more than 3 storeys in building height containing only dwelling units, provided each dwelling unit is served by an exterior exit facility leading directly to ground level.

4)   In a building referred to in Sentence (2) or (3), manual stations shall be installed near doorways leading from shared interior corridors to the exterior.

5)   Where a fire alarm system is installed, a manually operated fire alarm station shall be installed on the roof at each exit from a helicopter landing area.

3.2.4.17. Alert and Alarm Signals

1)   In a 2-stage fire alarm system described in Sentence 3.2.4.4.(2), the same audible signal devices are permitted to be used to sound the alert signals and the alarm signals.

2)   If audible signal devices with voice reproduction capabilities are intended for paging and similar voice message use, other than during a fire emergency, they shall be installed so that alert signals and alarm signals take priority over all other signals.

3)   Audible signal devices forming part of a fire alarm or voice communication system shall not be used for playing music or background noise.

3.2.4.18. Audibility of Alarm Systems

(See Note A-3.2.4.18.)

1)   Audible signal devices forming part of a fire alarm system shall be installed in a building so that

a)   alarm signals are clearly audible throughout the floor area and throughout any occupancy on a roof, and

b)   alert signals are clearly audible in continuously staffed locations, and where there are no continuously staffed locations, throughout the floor area and throughout any occupancy on a roof.

(See Note A-3.2.4.18.(1).)

2)   The sound pattern of an alarm signal shall conform to the temporal pattern defined in Clause 4.2 of ISO 8201, “Acoustics – Audible emergency evacuation signal.” (See Note A-3.2.4.18.(2).)

3)   The sound patterns of alert signals shall be significantly different from the temporal patterns of alarm signals. (See Note A-3.2.4.18.(3).)

4)   The fire alarm signal sound pressure level shall be not more than 110 dBA in any normally occupied area. (See Note A-3.2.4.18.(4).)

5)   The sound pressure level in a sleeping room from a fire alarm audible signal device shall be not less than 75 dBA in a building of residential or care occupancy when any intervening doors between the device and the sleeping room are closed. (See Note A-3.2.4.18.(5).)

6)   Audible signal devices in sleeping rooms in a building of residential or care occupancy shall emit a low frequency signal. (See Note A-3.2.4.18.(6).)

7)   Except as required by Sentence (5), the sound pressure level from a fire alarm system's audible signal device within a floor area shall be not less than 10 dBA above the ambient noise level and not less than 65 dBA when any intervening doors between the device and the rest of the floor area are closed.

8)   Except as permitted by Sentence (12), audible signal devices located within a dwelling unit shall include a means for them to be manually silenced for a period of not more than 10 min, after which time the devices shall restore themselves to normal operation. (See Note A-3.2.4.18.(8).)

9)   Audible signal devices within a dwelling unit or a suite of residential or care occupancy shall be connected to the fire alarm system

a)   in a manner such that a single open circuit at one device will not impair the operation of other audible signal devices on that same circuit that serve the other dwelling units or suites of residential or care occupancy, or

b)   on separate signal circuits that are not connected to the devices in any other dwelling unit, public corridor or suite of residential or care occupancy.

(See Note A-3.2.4.18.(9) and (10).)

10)   In a building or part thereof classified as a residential or care occupancy,

a)   separate circuits shall be provided for audible signal devices on each floor area, and

b)   audible signal devices within dwelling units or suites of residential or care occupancy shall be wired on separate signal circuits from those not within dwelling units or suites of residential or care occupancy.

(See Note A-3.2.4.18.(9) and (10).)

11)   Audible signal devices shall be installed in a service space referred to in Sentence 3.2.1.1.(8) and shall be connected to the fire alarm system.

12)   Audible signal devices within dwelling units that are wired on separate signal circuits in accordance with Clause (9)(b) need not include a means for manual signal silencing as required by Sentence (8), provided the fire alarm system includes a provision for an automatic signal silence within dwelling units, where

a)   the automatic signal silence cannot occur within the first 60 s of operation or within the zone of initiation,

b)   a subsequent alarm elsewhere in the building will reactuate the silenced audible signal devices within dwelling units,

c)   after a period of not more than 10 min, the silenced audible signal devices will be restored to continuous audible signal if the alarm is not acknowledged, and

d)   the voice communication systems referred to in Articles 3.2.4.22. and 3.2.4.23. have a provision to override the automatic signal silence to allow the transmission of voice messages through silenced audible signal device circuits that serve the dwelling units.

(See Note A-3.2.4.18.(8).)

13)   If a 2-stage fire alarm system has been installed with an automatic signal silence as described in Sentence (12), the system shall be designed so that any silenced audible signal devices serving dwelling units are reactuated whenever an alarm signal is required to be transmitted as part of the second stage. (See Note A-3.2.4.18.(8).)

3.2.4.19. Visible Signals

1)   Where a fire alarm system is installed, visible signal devices shall be provided in addition to alarm signal devices

a)   in buildings or portions thereof intended for use primarily by persons who are deaf or hard of hearing,

b)   in assembly occupancies in which music and other sounds associated with performances could exceed 100 dBA,

c)   in any floor area in which the ambient noise level is more than 87 dBA,

d)   in any floor area in which the occupants

i)   use ear protection devices,

ii)   are located in an audiometric booth, or

iii)   are located in sound-insulating enclosures,

e)   in public corridors serving a Group B, C, D or E major occupancy,

f)   in corridors used by the public serving a Group A major occupancy,

g)   in not less than 10% of the suites of residential occupancy in a hotel or motel (see Note A-3.2.4.19.(1)(g)), and

h)   in washrooms, except those located within

i)   suites of residential occupancy,

ii)   suites of care occupancy, or

iii)   patients' sleeping rooms.

2)   Visible signal devices are permitted to be installed in lieu of audible signal devices in the compartments referred to in Article 3.3.3.6.

3)   Visible signal devices required by Sentence (1) shall be installed so that the signal from at least one device is visible throughout the floor area or portion thereof in which they are installed. (See Note A-3.2.4.19.(3).)

4)   Visible signal devices shall be installed in the rooms and spaces required by Article 3.2.4.20. and Section 3.8. and shall

a)   conform to Sentence (5) where a fire alarm system is provided,

b)   conform to Sentence (6) where a fire alarm system is not provided,

c)   have a luminous intensity of not less than

i)   75 candela, if the strobe light is located in a sleeping room or bed space, and

ii)   15 candela, if the strobe light is not located in a sleeping room or bed space,

d)   produce between 1 and 3 flashes per second, with the flashes synchronized when more than one strobe light is visible from a single location, and

e)   be installed in each

i)   sleeping room or bed space,

ii)   room closed off from the living area by a door, including bathrooms, and

iii)   living area and any hallway serving the living area.

5)   The visible signal devices required by Sentence (4) shall

a)   consist of strobe lights conforming to CAN/ULC-S526, “Visible Signaling Devices for Fire Alarm and Signaling Systems, Including Accessories,” that are designed to operate as part of the fire alarm system, and

b)   be located in conformance with the installation requirements for visible signal devices in CAN/ULC-S524, “Standard for Installation of Fire Alarm Systems.”

6)   Where a fire alarm system is not provided, the visible signal devices required by Sentence (4) shall

a)   consist of strobe lights conforming to CAN/ULC-S526, “Visible Signaling Devices for Fire Alarm and Signaling Systems, Including Accessories,”

b)   be connected to, and activated by,

i)   the smoke alarms required by Article 3.2.4.20. and 9.10.19.1., or

ii)   the smoke detectors permitted by Articles 3.2.4.20., 3.2.4.21. or 9.10.19.8., and

c)   be located not less than 2 100 mm above the floor on a wall or ceiling in a location that will maximize effectiveness.

7)   Each adaptable dwelling unit shall be provided with special outlet boxes and cover plates that

a)   are designed, located and wired specifically to allow strobe lights to operate in conformance with

i)   Sentence (5) where a fire alarm system is provided, or

ii)   Sentence (6) where a fire alarm system is not provided,

b)   are permanently identified as “FIRE – Strobe Light Connection Only,”

c)   are installed in the locations described in Clause (4)(e), and

d)   for the purposes of providing power to the strobe lights that may be connected to the outlet boxes, are assumed that the total special outlets for at least 20 percent of the adaptable dwelling units in the building are in use.

3.2.4.20. Smoke Alarms

1)   Except as provided in Article 3.2.4.21., smoke alarms shall be installed in accordance with this Article.

2)   Except as required by Sentence (5) and permitted by Sentence (10), smoke alarms conforming to CAN/ULC-S531, “Standard for Smoke Alarms,” shall be installed in each dwelling unit and, except for care, treatment or detention occupancies required to have a fire alarm system, in each sleeping room not within a dwelling unit or suite of care occupancy.

3)   At least one smoke alarm shall be installed on each storey of a dwelling unit or suite of care occupancy.

4)   On any storey of a dwelling unit containing sleeping rooms, a smoke alarm shall be installed

a)   in each sleeping room, and

b)   in a location between the sleeping rooms and the remainder of the storey, and if the sleeping rooms are served by a hallway, the smoke alarm shall be located in the hallway.

5)   Where a care occupancy has individual suites for residents, a smoke alarm shall be installed

a)   in each sleeping room, and

b)   in a location between the sleeping rooms and the remainder of the suite, and if the sleeping rooms are served by a corridor within the suite, the smoke alarm shall be located in the corridor.

6)   A smoke alarm shall be installed on or near the ceiling.

7)   In hotels and motels with a fire alarm system, smoke alarms installed in rooms required to have a visible signal device connected to the fire alarm system as specified in Clause 3.2.4.19.(1)(g) shall have a visible signal component installed in accordance with CAN/ULC-S524, “Standard for Installation of Fire Alarm Systems.”

8)   In hotels and motels without a fire alarm system, smoke alarms installed in sleeping rooms of not less than 10% of the suites of residential occupancy shall have a visible signal component installed in accordance with CAN/ULC-S524, “Standard for Installation of Fire Alarm Systems.” (See also Note A-3.2.4.19.(1)(g).)

9)   Except as permitted in Sentence (10), smoke alarms referred in Sentence (2) shall

a)   be installed with permanent connections to an electrical circuit (see Note A-3.2.4.20.(9)(a)),

b)   have no disconnect switch between the overcurrent device and the smoke alarm, and

c)   except for the visible signal component required in Sentences (7) and (8), in case the regular power supply to the smoke alarm is interrupted, be provided with a battery as an alternative power source that can continue to provide power to the smoke alarm for a period of no less than 7 days in the normal condition, followed by 4 minutes of alarm.

10)   Suites of residential occupancy are permitted to be equipped with smoke detectors in lieu of smoke alarms, provided the smoke detectors

a)   are capable of independently sounding audible signals with a sound pressure level between 75 dBA and 110 dBA within the individual suites (see also Note A-3.2.4.18.(4)),

b)   except as permitted in Sentence (11), are installed in conformance with CAN/ULC-S524, “Standard for Installation of Fire Alarm Systems,” and

c)   form part of the fire alarm system.

(See Note A-3.2.4.20.(10).)

11)   Smoke detectors permitted to be installed in lieu of smoke alarms as stated in Sentence (10) are permitted to sound localized alarms within individual suites, and need not sound an alarm throughout the rest of the building.

12)   If more than one smoke alarm is required in a dwelling unit, the smoke alarms shall be interconnected so that the actuation of one smoke alarm will cause all smoke alarms within the dwelling unit to sound.

13)   A smoke alarm required by Sentence (2) shall be installed in conformance with CAN/ULC-S553, “Standard for the Installation of Smoke Alarms.”

14)   Except as permitted in Sentence (15), a manually operated silencing device shall be incorporated within the circuitry of a smoke alarm installed in a dwelling unit so that it will silence the signal emitted by the smoke alarm for a period of not more than 10 min, after which the smoke alarm will reset and again sound the alarm if the level of smoke in the vicinity is sufficient to reactuate the smoke alarm.

15)   Suites of residential occupancy equipped with smoke detectors installed to CAN/ULC-S524, “Standard for Installation of Fire Alarm Systems,” as part of the fire alarm system in lieu of smoke alarms as permitted by Sentence (10), need not incorporate the manually operated device required in Sentence (14). (See Note A-3.2.4.20.(10).)

16)   The sound patterns of smoke alarms shall

a)   meet the temporal patterns of alarm signals (see Note A-3.2.4.18.(2)), or

b)   be a combination temporal pattern and voice relay.

17)   Sleeping rooms and bed spaces provided in care occupancies in a building that is not equipped with a 2-stage fire alarm system shall be equipped with visible signal devices conforming to this Article. (See also Clause 3.2.4.3.(1)(c).)

3.2.4.21. Residential Fire Warning Systems

1)   Except where a fire alarm system is installed or required in a building, smoke detectors forming part of a residential fire warning system installed in conformance with CAN/ULC-S540, “Standard for Residential Fire and Life Safety Warning Systems: Installation, Inspection, Testing and Maintenance,” are permitted to be installed in lieu of all smoke alarms required by Article 3.2.4.20., provided the system

a)   is capable of sounding audible signals in accordance with Articles 9.10.19.2. and 9.10.19.5.,

b)   is powered in accordance with Article 9.10.19.4., and

c)   is provided with a silencing device in accordance with Article 9.10.19.6.

3.2.4.22. Voice Communication Systems for High Buildings

1)   A voice communication system required by Subsection 3.2.6. shall

a)   consist of a two-way means of communication with the central alarm and control facility and to the mechanical control centre from each floor area, and

b)   be capable of broadcasting prerecorded, synthesized, or live messages from the central alarm and control facility that are audible and intelligible in all parts of the building, except that this requirement does not apply to elevator cars (see Note A-3.2.4.22.(1)(b)).

2)   The voice communication system referred to in Sentence (1) shall include a means to silence the alarm signal in a single stage fire alarm system while voice instructions are being transmitted, but only after the alarm signal has initially sounded for not less than 30 s.

3)   The voice communication system referred to in Sentence (1) shall include a means to silence the alert signal and the alarm signal in a 2-stage fire alarm system while voice instructions are being transmitted, but only after the alert signal has initially sounded for not less than

a)   10 s in hospitals that have supervisory personnel on duty for twenty-four hours each day, or

b)   30 s for all other occupancies.

4)   The voice communication system referred to in Clause (1)(b) shall be designed so that the alarm signal in a 2-stage fire alarm system can be selectively transmitted to any zone or zones while maintaining an alert signal or selectively transmitting voice instructions to any other zone or zones in the building.

5)   The 2-way communication system referred to in Clause (1)(a) shall be installed so that emergency telephones are located in each floor area near exit stair shafts.

6)   Visible signal devices required by Sentence 3.2.4.19.(1), Article 3.2.4.20. and Section 3.8. shall continue to emit a visible signal while voice instructions are being transmitted.

7)   Where the facility is not equipped with staff trained to provide instructions over the loudspeakers, a pre-recorded message shall be provided.

3.2.4.23. One-Way Voice Communication Systems

1)   Except for Group B, Division 1 and Group F, Division 1 major occupancies, where a fire alarm system is required under Subsection 3.2.4., a one-way voice communication system shall be installed in buildings where a 2-stage fire alarm system is installed and whose occupant load exceeds 1 000.

2)   The one-way voice communication system required by Sentence (1) shall consist of loudspeakers that are

a)   operated from the central alarm and control facility or, in the absence of such a facility, from a designated area, and

b)   except in elevator cars, designed and located so that transmitted messages are audible and intelligible in all parts of the building.

(See Note A-3.2.4.22.(1)(b).)

3)   Where the facility is not equipped with staff trained to provide instructions over the loudspeakers, a pre-recorded message shall be provided.

4)   The one-way voice communication system required by Sentence (1) shall meet the silencing and transmission requirements of Sentences 3.2.4.22.(2) to (4) and (6).

3.2.5. Provisions for Firefighting

(See Note A-3.)

3.2.5.1. Access to Above-Grade Storeys

1)   Except for storeys below the first storey, direct access for firefighting shall be provided from the outdoors to every storey that is not sprinklered throughout and whose floor level is less than 25 m above grade, by at least one unobstructed window or access panel for each 15 m of wall in each wall required to face a street by Subsection 3.2.2.

2)   An opening for access required by Sentence (1) shall

a)   have a sill no higher than 900 mm above the inside floor, and

b)   be not less than 1 100 mm high by not less than

i)   550 mm wide for a building not designed for the storage or use of dangerous goods, or

ii)   750 mm wide for a building designed for the storage or use of dangerous goods.

3)   Access panels above the first storey shall be readily openable from both inside and outside, or the opening shall be glazed with plain glass.

3.2.5.2. Access to Basements

1)   Direct access from at least one street shall be provided from the outdoors in a building that is not sprinklered to each basement having a horizontal dimension more than 25 m.

2)   The access required by Sentence (1) is permitted to be provided by

a)   doors, windows or other means that provide an opening not less than 1 100 mm high and 550 mm wide, with a sill no higher than 900 mm above the inside floor, or

b)   an interior stairway immediately accessible from the outdoors.

3.2.5.3. Roof Access

1)   On a building more than 3 storeys in building height where the slope of the roof is less than 1 in 4, all main roof areas shall be provided with direct access from the floor areas immediately below, either by

a)   a stairway, or

b)   a hatch not less than 550 mm by 900 mm with a fixed ladder.

3.2.5.4. Access Routes

1)   A building which is more than 3 storeys in building height or more than 600 m2 in building area shall be provided with access routes for fire department vehicles

a)   to the building face having a principal entrance, and

b)   to each building face having access openings for firefighting as required by Articles 3.2.5.1. and 3.2.5.2.

(See Note A-3.2.5.4.(1).)

3.2.5.5. Location of Access Routes

1)   Access routes required by Article 3.2.5.4. shall be located so that the principal entrance and every access opening required by Articles 3.2.5.1. and 3.2.5.2. are located not less than 3 m and not more than 15 m from the closest portion of the access route required for fire department use, measured horizontally from the face of the building.

2)   Access routes shall be provided to a building so that

a)   for a building provided with a fire department connection, a fire department pumper vehicle can be located adjacent to the hydrants referred to in Article 3.2.5.15.,

b)   for a building not provided with a fire department connection, a fire department pumper vehicle can be located so that the length of the access route from a hydrant to the vehicle plus the unobstructed path of travel for the firefighter from the vehicle to the building is not more than 90 m, and

c)   the unobstructed path of travel for the firefighter from the vehicle to the building is not more than 45 m.

3)   The unobstructed path of travel for the firefighter required by Sentence (2) from the vehicle to the building shall be measured from the vehicle to the fire department connection provided for the building, except that if no fire department connection is provided, the path of travel shall be measured to the principal entrance of the building.

4)   If a portion of a building is completely cut off from the remainder of the building so that there is no access to the remainder of the building, the access routes required by Sentence (2) shall be located so that the unobstructed path of travel from the vehicle to one entrance of each portion of the building is not more than 45 m.

3.2.5.6. Access Route Design

1)   A portion of a roadway or yard provided as a required access route for fire department use shall

a)   have a clear width not less than 6 m, unless it can be shown that lesser widths are satisfactory,

b)   have a centre-line radius not less than 12 m,

c)   have an overhead clearance not less than 5 m,

d)   have a change of gradient not more than 1 in 12.5 over a minimum distance of 15 m,

e)   be designed to support the expected loads imposed by firefighting equipment and be surfaced with concrete, asphalt or other material designed to permit accessibility under all climatic conditions,

f)   have turnaround facilities for any dead-end portion of the access route more than 90 m long, and

g)   be connected with a public thoroughfare.

(See Note A-3.2.5.6.(1).)

2)   For buildings conforming to Article 3.2.2.51. or 3.2.2.60., no portion of the access route described in Sentence 3.2.2.10.(3) shall be more than 20 m below the uppermost floor level.

3.2.5.7. Water Supply

1)   Every building shall be provided with an adequate water supply for firefighting. (See Note A-3.2.5.7.(1).)

2)   Buildings that are sprinklered throughout with a sprinkler system conforming to Article 3.2.5.12. or have a standpipe system conforming to Article 3.2.5.8. to 3.2.5.10. are deemed to comply with Sentence (1).

3.2.5.8. Standpipe Systems

1)   Except as permitted by Sentence (2), a standpipe system shall be installed in a building that is

a)   more than 3 storeys in building height,

b)   more than 14 m high measured between grade and the ceiling of the top storey, or

c)   not more than 14 m high measured between grade and the ceiling of the top storey but has a building area exceeding the area shown in Table 3.2.5.8. for the applicable building height unless the building is sprinklered throughout.

2)   A standpipe system need not be installed in a storage garage conforming to Article 3.2.2.92., provided the building is not more than 15 m high.

Table 3.2.5.8.

Building Limits without Standpipe Systems

Forming Part of Sentence 3.2.5.8.(1)

| Occupancy Classification | Building Area, m2 |  |  |
| --- | --- | --- | --- |
|  | 1 storey | 2 storeys | 3 storeys |
| Group A | 2 500 | 2 000 | 1 500 |
| Group C | 2 000 | 1 500 | 1 000 |
| Group D | 4 000 | 3 000 | 2 000 |
| Group F, Division 2 | 1 500 | 1 500 | 1 000 |
| Group F, Division 3 | 3 000 | 2 000 | 1 000 |

3.2.5.9. Standpipe System Design

1)   Except as provided in Sentences (2) to (5), Articles 3.2.5.10. and 3.2.5.11., and Sentence 3.2.4.9.(2), the design, construction, installation and testing of a standpipe system shall conform to NFPA 14, “Standard for the Installation of Standpipe and Hose Systems.”

2)   A dry standpipe that is not connected to a water supply shall not be considered as fulfilling the requirements of this Article.

3)   If more than one standpipe is provided, the total water supply need not be more than 30 L/s.

4)   The residual water pressure at the design flow rate at the topmost hose connection of a standpipe system that is required to be installed in a building is permitted to be less than 690 kPa provided

a)   the building is sprinklered throughout,

b)   the water supply at the base of the sprinkler riser is capable of meeting, without a fire pump, the design flow rate and pressure demand of the sprinkler system, including the inside and outside hose allowance, and

c)   fire protection equipment is available to deliver, by means of the fire department connection, the full demand flow rate at a residual water pressure of 690 kPa at the topmost hose connection of the standpipe system (see Note A-3.2.5.9.(4)(c)).

5)   A fire department connection shall be provided for every standpipe system.

3.2.5.10. Hose Connections

1)   Hose connections shall be located in exits, in accordance with NFPA 14, “Standard for the Installation of Standpipe and Hose Systems.”

2)   Hose connections are not required within a floor area.

3)   Hose connections shall be provided with sufficient clearance to permit the use of a standard fire department hose key.

4)   Except as permitted by Sentence (5), 64 mm diam hose connections shall be installed in a standpipe system.

5)   Hose connections for 64 mm diam hose are not required in a building that is not more than 25 m high, measured between grade and the ceiling level of the top storey and in which an automatic sprinkler system is not installed.

3.2.5.11. Hose Stations

1)   Hose stations for 38 mm diam hose shall be installed for a standpipe system in a building that is not sprinklered throughout.

2)   Hose stations for a 38 mm diam hose shall be installed for a standpipe system within every floor area that is not sprinklered throughout. (See Note A-3.2.5.11.(2).)

3)   Hose stations shall be located in the floor area within 5 m of exits and at other locations to provide coverage of the entire floor area.

4)   A hose station located on one side of a horizontal exit shall be considered to serve only the floor area on that side of the horizontal exit.

5)   A hose cabinet shall be located so that its door, when fully opened, will not obstruct the required width of a means of egress.

6)   Where a building or part thereof is used as a distillery and the building is sprinklered in conformance with Article 3.2.5.12., small hose (38 mm) stations are permitted to be supplied from interior sprinkler piping.

7)   Where a hose station is provided in grain handling and storage facilities in which combustible dusts are produced in quantities or concentrations that create an explosion or fire hazard, fog and fine spray nozzles shall be used instead of nozzles that discharge a solid stream of water to prevent combustible dusts from being raised into suspension.

3.2.5.12. Automatic Sprinkler Systems

1)   Except as permitted by Sentences (2) to (4) and (9), an automatic sprinkler system shall be designed, constructed, installed and tested in conformance with NFPA 13, “Standard for the Installation of Sprinkler Systems.” (See Note A-3.2.5.12.(1).)

2)   Instead of the requirements of Sentence (1), NFPA 13R, “Standard for the Installation of Sprinkler Systems in Low-Rise Residential Occupancies,” is permitted to be used for the design, construction and installation of an automatic sprinkler system installed

a)   in a building of Group C major occupancy containing no other major occupancies that

i)   is not more than 4 storeys in building height and conforms to Article 3.2.2.47., 3.2.2.49., 3.2.2.51., 3.2.2.52. or 3.2.2.55., or

ii)   is not more than 3 storeys in building height and conforms to Article 9.10.1.3., or

b)   in a building of care occupancy with not more than 10 occupants that is not more than 3 storeys in building height and conforms to one of Articles 3.2.2.42. to 3.2.2.46.

(See Note A-3.2.5.12.(2).)

3)   Instead of the requirements of Sentence (1), NFPA 13D, “Standard for the Installation of Sprinkler Systems in One- and Two-Family Dwellings and Manufactured Homes,” is permitted to be used for the design, construction and installation of an automatic sprinkler system installed

a)   in a building of residential occupancy throughout that contains not more than two dwelling units,

b)   in a building of care occupancy, provided

i)   it contains not more than two suites of care occupancy,

ii)   it has not more than five residents throughout, and

iii)   a 30-minute water supply demand can be met, and

c)   in a building of residential occupancy throughout that contains more than two dwelling units, provided

i)   except for a secondary suite, no dwelling unit is located above another dwelling unit,

ii)   all suites are separated by a vertical fire separation having a fire-resistance rating of not less than 1 h that provides continuous protection from the top of the footing to the underside of the roof deck, with any space between the top of the wall and the roof deck tightly filled with mineral wool or noncombustible material,

iii)   each dwelling unit has its own sprinkler water supply provided in accordance with NFPA 13D, “Standard for the Installation of Sprinkler Systems in One- and Two-Family Dwellings and Manufactured Homes,”

iv)   a passive purge sprinkler system design is used as described in NFPA 13D, “Standard for the Installation of Sprinkler Systems in One- and Two-Family Dwellings and Manufactured Homes,” and

v)   where the sprinkler system is taken into consideration for the reduction of limiting distance, all rooms, including closets, bathrooms and attached garages, that adjoin an exposing building face are sprinklered, notwithstanding any exemption stated in NFPA 13D, “Standard for the Installation of Sprinkler Systems in One- and Two-Family Dwellings and Manufactured Homes.”

(See Note A-3.2.5.12.(2).)

4)   If a building contains fewer than 9 sprinklers, the water supply for these sprinklers is permitted to be supplied from the domestic water system for the building provided the required flow for the sprinklers can be met by the domestic system.

5)   If a water supply serves both an automatic sprinkler system and a system serving other equipment, control valves shall be provided so that either system can be shut off independently.

6)   Notwithstanding the requirements of the standards referenced in Sentences (1) and (2) regarding the installation of automatic sprinkler systems, sprinklers shall not be omitted in any room or closet in the storey immediately below a roof assembly. (See Note A-3.2.5.12.(6).)

7)   Notwithstanding the requirements of the standards referenced in Sentences (1) and (2) regarding the installation of automatic sprinkler systems, in buildings conforming to Article 3.2.2.48., 3.2.2.51., 3.2.2.57. or 3.2.2.60., sprinklers shall be provided for balconies and decks exceeding 610 mm in depth measured perpendicular to the exterior wall. (See Note A-3.2.5.12.(7).)

8)   Sprinklers in elevator machine rooms shall have a temperature rating not less than that required for an intermediate temperature classification and shall be protected against physical damage. (See Note A-3.2.5.12.(8).)

9)   Except as provided in Subsection 3.2.8., closely spaced sprinklers and associated draft stops need not be installed around floor openings in conformance with NFPA 13, “Standard for the Installation of Sprinkler Systems.”

10)   Fast response sprinklers shall be installed in residential occupancies, care occupancies, treatment occupancies and detention occupancies. (See Note A-3.2.5.12.(10).)

3.2.5.13. Combustible Sprinkler Piping

1)   Combustible sprinkler piping shall be used only for sprinkler systems in residential occupancies and other light-hazard occupancies. (See Note A-3.2.5.13.(1).)

2)   Combustible sprinkler piping shall meet the requirements of ULC/ORD-C199P, “Combustible Piping for Sprinkler Systems.”

3)   Except as permitted by Sentence (5), combustible sprinkler piping shall be separated from the area served by the sprinkler system, and from any other fire compartment, by ceilings, walls, or soffits consisting of, as a minimum,

a)   lath and plaster,

b)   gypsum board not less than 9.5 mm thick,

c)   plywood not less than 13 mm thick, or

d)   a suspended membrane ceiling with

i)   steel suspension grids, and

ii)   lay-in panels or tiles having a mass not less than 1.7 kg/m2.

4)   Except as permitted by Sentence (5), combustible sprinkler piping may be located above a ceiling provided that the distance between the edge of any ceiling opening that is not protected in conformance with Sentence (3) and the nearest sprinkler is not more than 300 mm.

5)   Where combustible sprinkler piping has been tested in conformance with ULC/ORD-C199P, “Combustible Piping for Sprinkler Systems,” and has been shown to meet the requirements therein without additional protection, conformance to Sentences (3) and (4) is not required.

3.2.5.14. Sprinklered Service Space

1)   An automatic sprinkler system shall be installed in a service space referred to in Sentence 3.2.1.1.(8) if flooring for access within the service space is other than catwalks.

2)   The sprinkler system required by Sentence (1) shall be equipped with waterflow detecting devices, with each device serving not more than one storey.

3)   The waterflow detecting devices required by Sentence (2) shall be connected to the fire alarm system, to

a)   initiate an alert signal in a 2-stage system or an alarm signal in a single stage system, and

b)   indicate separately on the fire alarm system annunciator the actuation of each device.

3.2.5.15. Fire Department Connections

1)   The fire department connection for a standpipe system shall be located so that the distance from the fire department connection to a hydrant is not more than 45 m and is unobstructed.

2)   The fire department connection for an automatic sprinkler system shall be located so that the distance from the fire department connection to a hydrant is not more than 45 m and is unobstructed.

3.2.5.16. Portable Fire Extinguishers

1)   Portable extinguishers shall be provided and installed in accordance with the British Columbia Fire Code.

2)   In a Group B, Division 1 major occupancy, portable fire extinguishers are permitted to be located in secure areas, or in lockable cabinets provided

a)   identical keys for all cabinets are located at all supervisory or security stations, or

b)   electrical remote release devices are provided and are connected to an emergency power supply.

3.2.5.17. Protection from Freezing

1)   Equipment forming part of a fire protection system shall be protected from freezing if

a)   it could be adversely affected by freezing temperatures, and

b)   it is located in an unheated area.

3.2.5.18. Fire Pumps

1)   If a fire pump is installed, it shall be installed in accordance with the requirements of NFPA 20, “Standard for the Installation of Stationary Pumps for Fire Protection.” (See Note A-3.2.5.18.(1).)

3.2.6. Additional Requirements for High Buildings

(See Note A-3.2.6.)

3.2.6.1. Application

1)   Except as provided in Sentence (2), this Subsection applies to a building

a)   of Group A, D, E or F major occupancy classification that is more than

i)   36 m high, measured between grade and the floor level of the top storey, or

ii)   18 m high, measured between grade and the floor level of the top storey, and in which the cumulative or total occupant load on or above any storey above grade, other than the first storey, divided by 1.8 times the width in metres of all exit stairs at that storey, exceeds 300,

b)   containing a Group B major occupancy in which the floor level of the highest storey of that major occupancy is more than 18 m above grade,

c)   containing a floor area or part of a floor area located above the third storey designed or intended as a Group B, Division 2 or 3 occupancy, or

d)   containing a Group C major occupancy whose floor level is more than 18 m above grade.

2)   This Subsection applies to a building or part of a building constructed in conformance with Article 3.2.2.57. in which the floor level of the highest storey is more than 18 m above grade.

3.2.6.2. Limits to Smoke Movement

1)   A building to which this Subsection applies shall be designed in accordance with Sentences (2) to (6) and Article 3.2.6.3. to limit the danger to occupants and firefighters from exposure to smoke in a building fire.

2)   A building referred to in Sentence (1) shall be designed so that, during a period of 2 h after the start of a fire, each exit stair serving storeys below the lowest exit level will not contain more than 1% by volume of contaminated air from the fire floor, assuming an outdoor temperature equal to the January design temperature on a 2.5% basis determined in accordance with Subsection 1.1.3. (See Note A-3.2.6.2.(2).)

3)    Each stairway that serves storeys above the lowest exit level shall have a vent to the outdoors, at or near the bottom of the stair shaft, that

a)   has an openable area of 0.05 m2 for every door between the stair shaft and a floor area, but not less than 1.8 m2,

b)   opens directly to the outdoors or into a vestibule that has a similar opening to the outdoors, and

c)   has a door or closure that

i)   is openable manually, and

ii)   can remain in the open position during a fire emergency.

(See Note A-3.2.6.2.(3).)

4)   Measures shall be taken to limit movement of smoke from a fire in a floor area below the lowest exit storey into upper storeys. (See Note A-3.2.6.2.(4).)

5)   Except for exhaust fans in kitchens, washrooms and bathrooms in dwelling units, and except for fans used for smoke venting as required by Article 3.2.6.6., air moving fans in a system that serves more than 2 storeys shall be designed and installed so that in the event of a fire these fans can be stopped by means of a manually operated switch at the central alarm and control facility.

6)   Except as provided in Article 3.2.4.12. or where there is a conflict with other smoke control measures in the building, air-handling systems used to provide make-up air to public corridors serving suites in a Group C major occupancy shall not shut down automatically upon activation of the fire alarm so as to maintain corridor pressurization.

3.2.6.3. Connected Buildings

1)   If a building described in Article 3.2.6.1. is connected to any other building, measures shall be taken to limit movement of contaminated air from one building into another during a fire. (See Note A-3.2.6.3.(1).)

3.2.6.4. Emergency Operation of Elevators

1)   Manual emergency recall shall be provided for all elevators serving storeys above the first storey.

2)   Key-operated switches for emergency recall required by Sentence (1) shall be provided in a conspicuous location at

a)   each elevator lobby on the recall level, and

b)   the central alarm and control facility required by Article 3.2.6.7.

3)   In-car emergency service switches shall be provided in all elevator cars.

4)   Keys to operate the switches required by Sentences (2) and (3) shall be

a)   provided in a suitably identified box conspicuously located on the outside of an elevator hoistway near the central alarm and control facility required by Article 3.2.6.7., and

b)   kept at the central alarm and control facility.

3.2.6.5. Elevator for Use by Firefighters

1)   At least one elevator shall be provided for use by firefighters in conformance with Sentences (2) to (6).

2)   The elevator referred to in Sentence (1) shall have a useable platform area not less than 2.2 m2 and shall be capable of carrying a load of 900 kg to the top floor that it serves from a landing on the storey containing the entrance for firefighter access referred to in Articles 3.2.5.4. and 3.2.5.5. within 1 min.

3)   Each elevator for use by firefighters shall

a)   be provided with a closure at each shaft opening so that the interlock mechanism remains mechanically engaged and electrical continuity is maintained in the interlock circuits and associated wiring for a period of not less than 1 h when the assembly is subjected to the standard fire exposure described in CAN/ULC-S104, “Standard Method for Fire Tests of Door Assemblies,”

b)   be protected with a vestibule containing no occupancy and separated from the remainder of the floor area by a fire separation having a fire-resistance rating not less than 45 min, or

c)   be protected with a corridor containing no occupancy and separated from the remainder of the building by a fire separation having a fire-resistance rating not less than 1 h.

4)   Except as permitted by Sentence (5), an elevator referred to in Sentence (1) shall be capable of providing transportation from the storey containing the entrance for firefighter access referred to in Articles 3.2.5.4. and 3.2.5.5. to every floor that is above grade in the building and that is normally served by the elevator system.

5)   If it is necessary to change elevators to reach any floor referred to in Sentence (4), the system shall be designed so that not more than one change of elevator is required when travelling to any floor in the building from the storey containing the entrance for firefighter access referred to in Articles 3.2.5.4. and 3.2.5.5.

6)   Electrical conductors for the operation of the elevator referred to in Sentence (1) shall

a)   be installed in service spaces conforming to Section 3.6. that do not contain other combustible material, or

b)   conform to CAN/ULC-S139, “Standard for Fire Test for Circuit Integrity of Fire-Resistive Power, Instrumentation, Control and Data Cables,” including the hose stream application, to provide a circuit integrity rating of not less than 1 h (see Note A-3.2.6.5.(6)(b)).

3.2.6.6. Venting to Aid Firefighting

1)   Means of venting each floor area to the outdoors shall be provided by windows, wall panels, smoke shafts, or the building exhaust system. (See Note A-3.2.6.6.(1).)

2)   Fixed glass windows shall not be used for the venting required by Sentence (1) if the breaking of the windows could endanger pedestrians below.

3)   Openable windows used for the venting required by Sentence (1) shall be permanently marked so that they are easily identifiable.

4)   Elevator hoistways shall not be designed for the venting required by Sentence (1).

3.2.6.7. Central Alarm and Control Facility

1)   A central alarm and control facility shall be provided on the storey containing the entrance for firefighter access referred to in Articles 3.2.5.4. and 3.2.5.5. in a location that

a)   is readily accessible to firefighters entering the building, and

b)   takes into account the effect of background noise likely to occur under fire emergency conditions, so that the facility can properly perform its required function under these conditions.

(See Note A-3.2.6.7.(1).)

2)   The central alarm and control facility required by Sentence (1) shall include

a)   means to control the voice communication system required by Article 3.2.6.8., so that messages can be sent to

i)   all loudspeakers simultaneously,

ii)   individual floor areas, and

iii)   exit stairwells,

b)   means to indicate audibly and visually alert signals and alarm signals and a switch to

i)   silence the audible portion of these signals, and

ii)   indicate visually that the audible portion has been silenced,

c)   means to indicate visually that elevators are on emergency recall,

d)   an annunciator conforming to Article 3.2.4.8.,

e)   means to transmit alert signals and alarm signals to the fire department in conformance with Article 3.2.4.7.,

f)   means to release hold-open devices on doors to vestibules,

g)   means to manually actuate alarm signals in the building selectively to any zone or zones,

h)   means to silence the alarm signals referred to in Clause (g) in conformance with Sentences 3.2.4.22.(2) and 3.2.4.22.(3),

i)   means, as appropriate to the measure for fire safety provided in the building, to

i)   actuate auxiliary equipment identified in Articles 3.2.6.2., 3.2.6.3. and 3.2.6.6., or

ii)   communicate with a continually staffed auxiliary equipment control centre,

j)   means to communicate with telephones in elevator cars, separate from connections to firefighters' telephones, if elevator cars are required by the Safety Standards Act and pursuant regulations to be equipped with a telephone,

k)   means to indicate visually, individual sprinkler system waterflow signals,

l)   means to indicate audibly and visually, sprinkler and standpipe system supervisory signals and trouble signals,

m)   a switch to silence the audible portion of a supervisory signal or a trouble signal, and

n)   visual indication that the audible portion of a supervisory signal or a trouble signal has been silenced.

(See Note A-3.2.6.7.(2).)

3.2.6.8. Voice Communication System

1)   A voice communication system conforming to Article 3.2.4.22. shall be provided in a building if

a)   the floor of the top storey is more than 36 m above grade, or

b)   a floor area or part of a floor area located above the third storey is designed or intended for use as a Group B, Division 2 or 3 occupancy.

3.2.6.9. Testing

1)   The systems for control of smoke movement and mechanical venting required by Articles 3.2.6.2. and 3.2.6.6. shall be tested to ensure satisfactory operation. (See Note A-3.2.6.9.(1).)

3.2.7. Lighting and Emergency Power Systems

3.2.7.1. Minimum Lighting Requirements

1)   An accessible path of travel required by Section 3.8., an exit, a public corridor, or a corridor providing access to exit for the public or serving patients' sleeping rooms or classrooms shall be equipped to provide illumination to an average level not less than 50 lx at floor or tread level and at angles and intersections at changes of level where there are stairs or ramps.

2)   The minimum level of the illumination required by Sentence (1) shall be 10 lx.

3)   Rooms and spaces used by the public shall be equipped to provide illumination as described in Sentences (4) to (7) and Article 9.34.2.7.

4)   The minimum level of illumination over the entire length of escalators and moving walks shall be not less than 100 lx at the level of the treads and walking surfaces.

5)   Except as provided in Sentence (6) and except for light switches and internally illuminated controls, the minimum level of illumination at controls required by Article 3.8.2.6. shall be not less than 100 lx.

6)   Where visual information is provided at controls referred to in Sentence (5), the minimum level of illumination at the controls shall be not less than 200 lx, except where the visual information is internally illuminated.

7)   Except for internally illuminated signs, the minimum level of illumination at signs displaying visual information required by Clauses 3.4.6.10.(5)(b) and 3.4.6.16.(5)(g), Subclause 3.4.6.16.(5)(l)(ii), Clause 3.4.6.16.(6)(d), Sentence 3.4.6.18.(3), Clause 3.4.6.18.(4)(a) and Articles 3.4.6.19. and 3.8.2.10. shall be not less than 200 lx.

8)   Lighting outlets in a building of residential occupancy shall be provided in conformance with Subsection 9.34.2.

3.2.7.2. Recessed Lighting Fixtures

1)   A recessed lighting fixture shall not be located in an insulated ceiling unless the fixture is designed for this type of installation.

3.2.7.3. Emergency Lighting

1)   Emergency lighting shall be provided to an average level of illumination not less than 10 lx at floor or tread level in

a)   exits,

b)   principal routes providing access to exit in open floor areas and in service rooms,

c)   corridors used by the public,

d)   corridors serving sleeping rooms in a treatment occupancy,

e)   corridors serving sleeping rooms in a care occupancy, except corridors serving sleeping rooms within individual suites of care occupancy,

f)   corridors serving classrooms,

g)   underground walkways,

h)   public corridors,

i)   floor areas or parts thereof where the public may congregate

i)   in Group A, Division 1 occupancies, or

ii)   in Group A, Division 2 and 3 occupancies having an occupant load of 60 or more,

j)   floor areas or parts thereof where persons are cared for that are within daycare facilities, including daycare facilities for children,

k)   food preparation areas in commercial kitchens,

l)   public washrooms,

m)   locations where doors are equipped with an electromagnetic lock as described in Clauses 3.4.6.16.(5)(k) and (6)(g), and

n)   universal washrooms, universal shower rooms and accessible change spaces required by Article 3.8.2.8.

2)   Emergency lighting to provide an average level of illumination of not less than 10 lx at floor or catwalk level shall be included in a service space referred to in Sentence 3.2.1.1.(8).

3)   The minimum value of the illumination required by Sentences (1) and (2) shall be not less than 1 lx.

4)   In addition to the requirements of Sentences (1) to (3), the installation of battery-operated emergency lighting in buildings or part thereof where treatment is provided shall conform to the appropriate requirements of CSA Z32, “Electrical safety and essential electrical systems in health care facilities.”

3.2.7.4. Emergency Power for Lighting

1)   An emergency power supply shall be

a)   provided to maintain the emergency lighting required by this Subsection from a power source such as batteries or generators that will continue to supply power in the event that the regular power supply to the building is interrupted, and

b)   so designed and installed that upon failure of the regular power it will assume the electrical load automatically for a period of

i)   2 h for a building within the scope of Subsection 3.2.6.,

ii)   1 h for a building of Group B major occupancy classification that is not within the scope of Subsection 3.2.6.,

iii)   1 h for a building constructed in accordance with Article 3.2.2.51. or 3.2.2.60., and

iv)   30 min for a building of any other occupancy.

(See Note A-3.2.7.4.(1).)

2)   If self-contained emergency lighting units are used, they shall conform to CSA C22.2 No. 141, “Emergency lighting equipment.”

3.2.7.5. Emergency Power Supply Installation

1)   Except as required by Articles 3.2.7.6. and 3.2.7.7., an emergency electrical power supply system shall be installed in conformance with CSA C282, “Emergency electrical power supply for buildings.” (See Sentence 3.2.7.8.(1) for emergency electrical power supply for voice communication systems.)

3.2.7.6. Emergency Power for Treatment Occupancies

1)   Except as required by Article 3.2.7.7., an emergency electrical power supply system for emergency equipment required by this Part for treatment occupancies shall be installed in conformance with CSA Z32, “Electrical safety and essential electrical systems in health care facilities.” (See Note A-3.2.7.6.(1).)

3.2.7.7. Fuel Supply Shut-off Valves

1)   If a liquid or gas fuel-fired engine or turbine for an emergency electric power supply is dependent on a fuel supply from outside the building, the fuel supply shall be provided with a suitably-identified separate shut-off valve outside the building.

3.2.7.8. Emergency Power for Fire Alarm Systems

1)   Fire alarm systems, including those incorporating a voice communication system, shall be provided with an emergency power supply conforming to Sentences (2) to (4).

2)   The emergency power supply required by Sentence (1) shall be supplied from

a)   a generator,

b)   batteries, or

c)   a combination thereof.

3)   The emergency power supply required by Sentence (1) shall be capable of providing

a)   supervisory power for not less than 24 h, and

b)   immediately following that period, emergency power under full load for not less than

i)   2 h for a building within the scope of Subsection 3.2.6.,

ii)   1 h for a building classified as a Group B major occupancy that is not within the scope of Subsection 3.2.6.,

iii)   1 h for a building constructed in accordance with Article 3.2.2.51. or 3.2.2.60.,

iv)   5 min for a building not required to be equipped with an annunciator, and

v)   30 min for any other building.

(See Note A-3.2.7.8.(3).)

4)   The emergency power supply required by Sentence (1) shall be designed so that, in the event of a failure of the normal power source, there is an immediate automatic transfer to emergency power with no loss of information.

3.2.7.9. Emergency Power for Building Services

1)   An emergency power supply capable of operating under a full load for not less than 2 h shall be provided by an emergency generator for

a)   every elevator serving storeys above the first storey in a building that is more than 36 m high measured between grade and the floor level of the top storey and every elevator for firefighters in conformance with Sentence (2),

b)   except as provided in Sentence (4), equipment that supplies water for fire suppression as required by Articles 3.2.5.7. and 3.2.5.8. and Sentences 3.2.5.12.(1) and (2) and 3.2.5.18.(1), if the supply depends solely on electrical power supplied to the building,

c)   fans and other electrical equipment that are installed to maintain the air quality specified in Articles 3.2.6.2. and 3.3.3.6.,

d)   fans required for venting by Article 3.2.6.6., and

e)   fans required by Clause 3.2.8.4.(1)(c) and Article 3.2.8.7. in buildings within the scope of Subsection 3.2.6.

(See Note A-3.2.7.9.(1).)

2)   Except as permitted by Sentence (3), the emergency power supply for elevators required by Clause (1)(a) shall be capable of operating all elevators for firefighters plus one additional elevator simultaneously.

3)   Sentence (2) does not apply if the time to recall all elevators under emergency power supply is not more than 5 min, each from its most remote storey to

a)   the storey containing the entrance for firefighter access referred to in Articles 3.2.5.4. and 3.2.5.5., or

b)   to a transfer lobby.

4)   The emergency power supply required by Clause (1)(b) for the equipment that supplies water for fire suppression need not be provided for sprinkler systems conforming to NFPA 13D, “Standard for the Installation of Sprinkler Systems in One- and Two-Family Dwellings and Manufactured Homes.”

3.2.7.10. Protection of Electrical Conductors

1)   The protection of electrical and emergency conductors referred to in Clauses (a) to (c) shall conform to the requirements stated in Sentences (2) to (11):

a)   electrical conductors located within buildings identified in Article 3.2.6.1. serving

i)   fire alarms,

ii)   emergency lighting, or

iii)   emergency equipment within the scope of Articles 3.2.6.2. to 3.2.6.8.,

b)   emergency conductors serving fire pumps required to be installed under Article 3.2.5.18., and

c)   electrical conductors serving mechanical systems serving

i)   areas of refuge identified in Clause 3.3.3.6.(1)(b), or

ii)   contained use areas identified in Clauses 3.3.3.7.(4)(a) and (b).

2)   Except as otherwise required by Sentence (3) and permitted by this Article, electrical conductors that are used in conjunction with systems identified in Sentence (1) shall

a)   conform to CAN/ULC-S139, “Standard for Fire Test for Circuit Integrity of Fire-Resistive Power, Instrumentation, Control and Data Cables,” including the hose stream application, to provide a circuit integrity rating of not less than 1 h (see Note A-3.2.7.10.(2)(a) and (3)(a)) (see also Clause 3.2.6.5.(6)(b)), or

b)   be located in a service space that is separated from the remainder of the building by a fire separation that has a fire-resistance rating not less than 1 h.

3)   Electrical conductors identified in Clause (1)(c) shall

a)   conform to CAN/ULC-S139, “Standard for Fire Test for Circuit Integrity of Fire-Resistive Power, Instrumentation, Control and Data Cables,” including the hose stream application, to provide a circuit integrity rating of not less than 2 h (see Note A-3.2.7.10.(2)(a) and (3)(a)), or

b)   be located in a service space that is separated from the remainder of the building by a fire separation that has a fire-resistance rating not less than 2 h.

4)   The service spaces referred to in Clauses (2)(b) and (3)(b) shall not contain any combustible materials other than the conductors being protected.

5)   Except as stated in Sentences (7) and (9), the electrical conductors referred to in Sentence (1) are those that extend from the source of emergency power to

a)   the equipment served, or

b)   the distribution equipment supplying power to the equipment served, if both are in the same room (see Note A-3.2.7.10.(5)(b)).

6)   If a fire alarm transponder or annunciator in one fire compartment is connected to a central processing unit or another transponder or annunciator located in a different fire compartment, the electrical conductors connecting them shall be protected in accordance with Sentence (2).

7)   Fire alarm system branch circuits within a storey that connect transponders and individual devices need not conform to Sentence (2). (See Note A-3.2.7.10.(7).)

8)   Except as permitted in Sentence (9), if a distribution panel supplies power to emergency lighting, the power supply conductors leading up to the distribution panel shall be protected in accordance with Sentence (2).

9)   Conductors leading from a distribution panel referred to in Sentence (8) to emergency lighting units in the same storey need not conform to Sentence (2).

10)   Distribution panels serving emergency lighting units located on other storeys shall be installed in a service room separated from the floor area by a fire separation having a fire-resistance rating of at least 1 h.

11)   Conductors leading from a distribution panel to emergency lighting units located on other storeys shall be protected in accordance with Sentence (2) between the distribution panel and the floor area where the emergency lighting units are located.

3.2.8. Mezzanines and Openings through Floor Assemblies

3.2.8.1. Application

1)   Except as permitted by Article 3.2.8.2. and Sentence 3.3.4.2.(3), the portions of a floor area or a mezzanine that do not terminate at an exterior wall, a firewall or a vertical shaft shall

a)   terminate at a vertical fire separation having a fire-resistance rating not less than that required for the floor assembly and extending from the floor assembly to the underside of the floor or roof assembly above, or

b)   be protected in conformance with the requirements of Articles 3.2.8.3. to 3.2.8.8.

2)   The penetration of a floor assembly by an exit or a vertical service space shall conform to the requirements of Sections 3.4., 3.5. and 3.6.

3)   A floor area containing sleeping rooms in a building of Group B, Division 2 major occupancy shall not be constructed as part of an interconnected floor space.

3.2.8.2. Exceptions to Special Protection

1)   A mezzanine need not terminate at a vertical fire separation nor be protected in conformance with the requirements of Articles 3.2.8.3. to 3.2.8.8. provided the mezzanine

a)   serves a Group A, Division 1 major occupancy,

b)   serves a Group A, Division 3 major occupancy in a building not more than 2 storeys in building height, or

c)   serves a Group A, C, D, E or F major occupancy and

i)   is 500 m2 or less in area, and

ii)   conforms to Sentence 3.2.1.1.(3) or (4).

2)   Except for floors referred to in Sentence 3.1.10.3.(1) and Article 3.2.1.2., openings through a horizontal fire separation for vehicular ramps in a storage garage are not required to be protected with closures and need not conform to this Subsection.

3)   If a closure in an opening in a fire separation would disrupt the nature of a manufacturing process, such as a continuous flow of material from storey to storey, the closure for the opening is permitted to be omitted provided precautions are taken to offset the resulting hazard. (See Note A-3.2.8.2.(3).)

4)   An interconnected floor space in a Group B, Division 1 occupancy need not conform to the requirements of Articles 3.2.8.3. to 3.2.8.8. provided the interconnected floor space does not interconnect more than 2 adjacent storeys.

5)   Except as permitted by Sentence (6), openings for escalators and inclined moving walks need not conform to the requirements in Articles 3.2.8.3. to 3.2.8.8. provided

a)   the opening for each escalator or walk does not exceed 10 m2,

b)   the building is sprinklered throughout,

c)   closely spaced sprinklers and associated draft stops are installed around the openings in conformance with NFPA 13, “Standard for the Installation of Sprinkler Systems,” and

d)   the interconnected floor space contains only Group A, Division 1, 2 or 3, Group D or Group E major occupancies (see Note A-3.2.8.2.(6)(c)).

6)   An interconnected floor space need not conform to the requirements of Articles 3.2.8.3. to 3.2.8.8., provided

a)   it consists of the first storey and the storey next above or below it, but not both,

b)   it is sprinklered throughout or, where the building area is not more than one half of the area permitted by Subsection 3.2.2., the openings through the floor are used only for stairways, escalators or moving walks (see Note A-3.2.8.2.(6)(b)), and

c)   it contains only Group A, Division 1, 2 or 3, Group D, Group E, or Group F, Division 2 or 3 major occupancies (see Note A-3.2.8.2.(6)(c)).

3.2.8.3. Sprinklers

1)   A building containing an interconnected floor space shall be sprinklered throughout.

2)   Except for large floor openings as defined in NFPA 13, “Standard for the Installation of Sprinkler Systems,” closely spaced sprinklers and associated draft stops shall be installed around floor openings in conformance with NFPA 13.

3.2.8.4. Vestibules

1)   An exit opening into an interconnected floor space shall be protected at each opening into the interconnected floor space by a vestibule

a)   with doorways that are not less than 1.8 m apart,

b)   that is separated from the remainder of the floor area by a fire separation that is not required to have a fire-resistance rating (see Note A-3.1.8.1.(1)(b)), and

c)   that is designed to limit the passage of smoke so that the exit stair shaft does not contain more than 1% by volume of contaminated air from the fire floor, assuming an outdoor temperature equal to the January design temperature on a 2.5% basis determined in accordance with Subsection 1.1.3. (see Note A-3.2.8.4.(1)(c)).

2)   An exit opening into an interconnected floor space shall conform to Sentence 3.4.3.2.(6).

3)   If an elevator hoistway opens into an interconnected floor space and into storeys above the interconnected floor space, either the elevator doors opening into the interconnected floor space or the elevator doors opening into the storeys above the interconnected floor space shall be protected by vestibules conforming to Sentence (1).

3.2.8.5. Protected Floor Space

1)   A protected floor space used to satisfy the requirements of Clause 3.4.3.2.(6)(b) shall

a)   be separated from the interconnected floor space by a fire separation having a fire-resistance rating not less than that required for the floor assembly of the storey in which it is located,

b)   have all openings in the vertical fire separation between a protected floor space and the adjacent interconnected floor space protected by vestibules conforming to Sentence 3.2.8.4.(1), and

c)   be designed so that it is not necessary to enter the interconnected floor space to reach an exit.

3.2.8.6. Draft Stops

1)   A draft stop shall be provided at each floor level within an interconnected floor space, immediately adjacent to and surrounding the opening, and shall be not less than 500 mm deep measured from ceiling level down to the underside of the draft stop.

3.2.8.7. Mechanical Exhaust System

1)   A mechanical exhaust system shall be provided to remove air from an interconnected floor space at a rate of 4 air changes per hour. (See Note A-3.2.8.7.(1).)

2)   The mechanical exhaust system required by Sentence (1) shall be actuated by a switch located on the storey containing the entrance for firefighter access referred to in Articles 3.2.5.4. and 3.2.5.5. near the annunciator for the fire alarm system.

3.2.8.8. Combustible Content Limits

1)   An interconnected floor space shall be designed so that the combustible contents, excluding interior finishes, in those parts of a floor area in which the ceiling is more than 8 m above the floor, are limited to not more than 16 g of combustible material for each cubic metre of volume of the interconnected floor space.

3.2.9. Integrated Fire Protection and Life Safety Systems

3.2.9.1. Testing

1)   Where fire protection and life safety systems and systems with fire protection and life safety functions are integrated with each other, they shall be tested as a whole in accordance with CAN/ULC-S1001, “Standard for Integrated Systems Testing of Fire Protection and Life Safety Systems,” to verify that they have been properly integrated. (See Note A-3.2.9.1.(1).)

Section  3.3.   Safety within Floor Areas

(See Note A-3.3.)

3.3.1. All Floor Areas

3.3.1.1. Separation of Suites

1)   Except as permitted by Sentences (2) and (3), a suite shall be separated from adjoining suites by a fire separation having a fire-resistance rating not less than 1 h. (See also Subsection 3.3.3. for care, treatment or detention occupancies, Article 3.3.4.2. for residential occupancies, and Article 3.1.8.7. for fire dampers.)

2)   The fire-resistance rating of the fire separation required by Sentence (1) is permitted to be less than 1 h but not less than 45 min provided the fire-resistance rating required by Subsection 3.2.2. is permitted to be less than 1 h for

a)   the floor assembly above the floor area, or

b)   the floor assembly below the floor area, if there is no floor assembly above.

3)   Occupancies that are served by public corridors conforming to Clause 3.3.1.4.(4)(b) in a building that is sprinklered throughout, are not required to be separated from one another by fire separations provided the occupancies are

a)   suites of business and personal services occupancy,

b)   fast food vending operations that do not provide seating for customers,

c)   suites of mercantile occupancy, or

d)   any combination of these occupancies.

4) No fire separation is required between suites of business and personal services occupancy.

3.3.1.2. Hazardous Substances, Equipment and Processes

1)   Except as provided in Subsections 3.3.5. and 3.3.6., the storage, handling and use of hazardous substances shall be in conformance with

a)   provincial or territorial regulations or municipal bylaws, or

b)   in the absence of the regulations or bylaws referred to in Clause (a), the British Columbia Fire Code.

(See Note A-3.3.1.2.(1).)

2)   Systems for the ventilation of cooking equipment that is not within a dwelling unit and is used in processes producing grease-laden vapours shall be designed and installed in conformance with Articles 3.6.3.5., 6.3.1.6. and 6.9.1.3. (See Note A-3.3.1.2.(2).)

3)   A fuel-fired appliance shall not be installed in a corridor serving as an access to exit.

3.3.1.3. Means of Egress

(See Note A-3.3.1.3.)

1)   Access to exit within floor areas shall conform to Subsections 3.3.2. to 3.3.5., in addition to the requirements of this Subsection.

2)   If a podium, terrace, platform or contained open space is provided, egress requirements shall conform to the appropriate requirements of Sentence 3.3.1.5.(1) for rooms and suites.

3)   Means of egress shall be provided from every podium, terrace, platform or contained open space used or intended for occupancy, to exits in conformance with the requirements of Section 3.4.

4)   Means of egress from an occupancy on a roof serving only a single dwelling unit shall be provided in conformance with Article 3.3.4.4.

5)   Except as permitted by Sentence (4) and except as required by Sentence (6), a means of egress at the roof level, designed in conformance with the requirements for exits in Section 3.4., shall be provided from an occupancy on a roof.

6)   At least two separate means of egress at the roof level, designed in conformance with the requirements for exits in Section 3.4., shall be provided from a roof used or intended for an occupant load more than 60.

7)   For the purposes of Sentences (5) and (6), the occupied area of the occupancy on a roof shall be used in place of floor area.

8)   A rooftop enclosure that does not serve as part of a means of egress for an occupancy on a roof in accordance with Sentence (5) or (6) shall be provided with an access to exit that leads to an exit

a)   at the roof level, or

b)   on the storey immediately below the roof.

9)   A rooftop enclosure which is more than 200 m2 in area shall be provided with at least 2 means of egress.

10)   Two points of egress shall be provided for a service space referred to in Sentence 3.2.1.1.(8) if

a)   the area is more than 200 m2, or

b)   the travel distance measured from any point in the service space to a point of egress is more than 25 m.

11)   Except as permitted by Sentences 3.3.4.4.(5) and (6), each suite in a floor area that contains more than one suite shall have

a)   an exterior exit doorway, or

b)   a doorway

i)   into a public corridor, or

ii)   to an exterior passageway.

12)   Except as permitted by this Section and by Sentence 3.4.2.1.(2), at the point where a doorway referred to in Sentence (11) opens onto a public corridor or exterior passageway, it shall be possible to go in opposite directions to each of 2 separate exits.

3.3.1.4. Public Corridor Separations

1)   Except as otherwise required by this Part or as permitted by Sentence (4), a public corridor shall be separated from the remainder of the storey by a fire separation.

2)   Except as permitted by Sentence (3) and Clauses (4)(a) and (b), the fire separation between a public corridor and the remainder of the storey shall have a fire-resistance rating not less than 45 min.

3)   If a storey is sprinklered throughout, no fire-resistance rating is required for a fire separation between a public corridor and the remainder of the storey, provided the corridor does not serve a care, treatment or detention occupancy or a residential occupancy. (See Note A-3.1.8.1.(1)(b).)

4)   No fire separation is required in a sprinklered floor area between a public corridor and

a)   except as required by Sentences 3.3.3.5.(8) and 3.3.4.2.(1), and notwithstanding Sentence 3.4.2.4.(2), the remainder of a storey, provided the travel distance from any part of the floor area to an exit is not more than 45 m,

b)   a room or a suite, provided the public corridor complies with Sentence 3.3.1.9.(4) and Clause 3.4.2.5.(1)(d), or

c)   a space containing plumbing fixtures required by Subsection 3.7.2., provided the space and the public corridor are separated from the remainder of the storey by a fire separation having a fire-resistance rating not less than that required between the public corridor and the remainder of the storey.

3.3.1.5. Egress Doorways

1)   Except for dwelling units, a minimum of 2 egress doorways located so that one doorway could provide egress from the room or suite as required by Article 3.3.1.3. if the other doorway becomes inaccessible to the occupants due to a fire which originates in the room or suite, shall be provided for every room and every suite

a)   that is used for a high-hazard industrial occupancy and whose area is more than 15 m2,

b)   intended for an occupant load more than 60,

c)   in a floor area that is not sprinklered throughout, and

i)   the area of a room or suite is more than the value in Table 3.3.1.5.-A, or

ii)   the travel distance within the room or suite to the nearest egress doorway is more than the value in Table 3.3.1.5.-A, or

d)   in a floor area that is sprinklered throughout and does not contain a high-hazard industrial occupancy and

i)   the travel distance to an egress doorway is more than 25 m, or

ii)   the area of the room or suite is more than the value in Table 3.3.1.5.-B.

2)   Where 2 egress doorways are required by Sentence (1), they shall be placed at a distance from one another equal to or greater than one third of the maximum overall diagonal dimension of the area to be served, measured as the shortest distance that smoke would have to travel between the nearest required egress doors.

Table 3.3.1.5.-A

Egress in Floor Area not Sprinklered Throughout

Forming Part of Sentence 3.3.1.5.(1)

| Occupancy of Room or Suite | Maximum Area of Room or Suite, m2 | Maximum Distance to Egress Doorway, m |
| --- | --- | --- |
| Group A | 150 | 15 |
| Group C | 100(1) | 15(1) |
| Group D | 200 | 25 |
| Group E | 150 | 15 |
| Group F, Division 2 | 150 | 10 |
| Group F, Division 3 | 200 | 15 |

Notes to Table 3.3.1.5.-A:

(1) See Article 3.3.4.4. for dwelling units.

Table 3.3.1.5.-B

Egress in Floor Area Sprinklered Throughout

Forming Part of Sentence 3.3.1.5.(1)

| Occupancy of Room or Suite | Maximum Area of Room or Suite, m2 |
| --- | --- |
| Group A | 200 |
| Group B, Division 1 | 100 |
| Group B, Division 2 |  |
| sleeping rooms | 100 |
| other than sleeping rooms | 200 |
| Group B, Division 3 sleeping rooms not in suites | 100 |
| individual suites | 150 |
| other than sleeping rooms | 200 |
| Group C | 150(1) |
| Group D | 300 |
| Group E | 200 |
| Group F, Division 2 | 200 |
| Group F, Division 3 | 300 |

Notes to Table 3.3.1.5.-B:

(1) See Article 3.3.4.4. for dwelling units.

3.3.1.6. Travel Distance

1)   If more than one egress doorway is required from a room or suite referred to in Article 3.3.1.5., the travel distance within the room or suite to the nearest egress doorway shall not exceed the maximum travel distances specified in Clauses 3.4.2.5.(1)(a), (b), (c) and (f) for exits.

3.3.1.7. Protection on Floor Areas with an Accessible Path of Travel

1)   Every floor area that is not sprinklered throughout and that has an accessible path of travel shall

a)   be served by an elevator

i)   conforming to Sentences 3.2.6.5.(4) to (6),

ii)   protected against fire in conformance with Clause 3.2.6.5.(3)(b) or (c), and

iii)   in a building over 3 storeys in building height, protected against smoke movement so that the hoistway will not contain more than 1% by volume of contaminated air from a fire floor during a period of 2 h after the start of a fire, assuming an outdoor temperature equal to the January design temperature on a 2.5% basis determined in conformance with Subsection 1.1.3.,

b)   be divided into at least 2 zones by fire separations conforming to Sentences (2), (3) and 3.1.8.5.(6) so that (see Note A-3.3.1.7.(1)(b))

i)   persons with disabilities can be accommodated in each zone, and

ii)   the travel distance from any point in one zone to a doorway leading to another zone shall be not more than the value for travel distance permitted by Sentence 3.4.2.5.(1) for the occupancy classification of the zone,

c)   in the case of residential occupancies, be provided with balconies conforming to Sentence (4), except on a storey containing an accessible entrance that complies with Article 3.8.2.2.,

d)   have an accessible exterior exit at ground level, or

e)   have a ramp conforming to Subsection 3.8.3. leading to ground level.

(See Note A-3.3.1.7.(1).)

2)   Except as permitted by Sentence (3), the fire separations referred to in Clause (1)(b) shall have a fire-resistance rating not less than 1 h.

3)   The fire-resistance rating of the fire separations referred to in Clause (1)(b) is permitted to be less than 1 h but not less than 45 min provided the fire-resistance rating required by Subsection 3.2.2. is permitted to be less than 1 h for

a)   the floor assembly above the floor area, or

b)   the floor assembly below the floor area, if there is no floor assembly above.

4)    A balcony required by Clause (1)(c) shall

a)   have direct access from the suite or floor area

b)   be not less than 1 500 mm deep from the outside face of the exterior wall to the inside edge of the balcony with a clear perpendicular dimension of not less than 1 700 mm, and

c)   provide not less than 2 m2 of balcony space for each accessible sleeping room or bed space.

5)   The floor area on either side of a horizontal exit conforming to Article 3.4.6.10. is permitted to be considered as a zone in applying the requirements of Clause (1)(b).

3.3.1.8. Headroom and Protruding Objects

1)   Except within the floor area of a storage garage, the minimum headroom clearance in every access to exit shall conform to the requirements of Article 3.4.3.4. for exits. (See also Sentence 3.3.5.4.(5).)

2)   Except as permitted by Sentence (3) and except for paths of travel in service rooms and dwelling units, protruding building elements located within 1 980 mm of the floor shall not project more than 100 mm horizontally into paths of travel in a manner that would create a hazard. (See Note A-3.3.1.8.(2) and (3).)

3)   The horizontal projection of a protruding building element referred to in Sentence (2) is permitted to be more than 100 mm, provided the clearance between the protruding element and the floor is less than 680 mm. (See Note A-3.3.1.8.(2) and (3).)

3.3.1.9. Corridors

1)   The minimum width of a public corridor shall be 1 100 mm.

2)   Except as required by Sentence 3.3.3.3.(3), the minimum unobstructed width of a corridor used by the public or a corridor serving classrooms or patients' sleeping rooms shall be 1 100 mm.

3)   If a corridor contains an occupancy, the occupancy shall not reduce the unobstructed width of the corridor to less than its required width.

4)   If a public corridor conforming to Clause 3.4.2.5.(1)(d) contains an occupancy,

a)   the occupancy shall be located so that for pedestrian travel there is an unobstructed width not less than 3 m at all times adjacent and parallel to all rooms and suites that front onto the public corridor, and

b)   the combined area of all occupancies in the public corridor shall be not more than 15% of the area of the public corridor.

5)   Except for a dead-end corridor that is entirely within a suite or as permitted by Sentences 3.3.3.3.(1) and 3.3.4.4.(6), a dead-end corridor is permitted provided it is not more than 6 m long.

3.3.1.10. Aisles

1)   Except as otherwise stated in this Section, aisles shall be provided in conformance with the British Columbia Fire Code.

3.3.1.11. Door Swing

1)   Except as permitted by Sentence (5) and Article 3.3.1.12., a door that opens into a corridor or other facility providing access to exit from a suite or room not located within a suite shall swing on a vertical axis.

2)   Except as permitted by Article 3.3.1.12., a door that opens into a corridor or other facility providing access to exit from a room or suite that is used or intended for an occupant load more than 60 or for a high-hazard industrial occupancy shall swing in the direction of travel to the exit.

3)   Every door that divides a corridor that is not wholly contained within a suite shall swing on a vertical axis in the direction of travel to the exit.

4)   If a pair of doors is installed in a corridor that provides access to exit in both directions, the doors shall swing in opposite directions, with the door on the right hand side swinging in the direction of travel to the exit.

5)   Doors that serve storage suites not more than 28 m2 in area in warehousing buildings need not conform to Sentence (1).

3.3.1.12. Sliding Doors

1)   Except as permitted by Sentences (2) and 3.3.1.11.(5), a sliding door provided in the locations described in Article 3.3.1.11. shall

a)   be designed and installed to swing on the vertical axis in the direction of travel to the exit when pressure is applied, and

b)   be identified as a swinging door by means of a label or decal affixed to it.

2)   In a Group B, Division 1 occupancy, or in an impeded egress zone in other occupancies, sliding doors used in an access to exit need not conform to Sentence (1) and Article 3.3.1.11.

3)   Movable partitions used to separate a public corridor from an adjacent business and personal services occupancy or a mercantile occupancy need not conform to Sentence (1) and Sentences 3.3.1.11.(1) and (2), provided the partitions are not located in the only means of egress. (See Note A-3.3.1.12.(3).)

3.3.1.13. Doors and Door Hardware

(See also Sentence 3.8.3.6.(17).)

1)   Except as required by Article 3.3.3.4., a door that opens into or is located within a public corridor or other facility that provides access to exit from a suite shall

a)   provide a clear opening of not less than 850 mm if there is only one door leaf,

b)   in a doorway with multiple leaves, have the active leaf providing a clear opening of not less than 850 mm,

c)   not open onto a step, and

d)   have a threshold not more than 13 mm higher than the surrounding finished floor surface, and where it is higher than 6 mm, shall be beveled to a slope not steeper than 1 in 2, except where it

i)   is used to confine the spillage of flammable liquids within a service room or within a room in an industrial occupancy, or

ii)   provides access to an exterior balcony, unless the balcony is required by Clause 3.3.1.7.(1)(c).

2)   Except as provided in Sentences (6) and (7), a door in an access to exit shall be readily openable in travelling to an exit without requiring keys, special devices or specialized knowledge of the door-opening mechanism.

3)   Except as permitted by Sentence (4), door release hardware shall comply with Clause 3.8.3.8.(1)(b) and the door shall be openable with not more than one releasing operation. (See also Sentence 3.8.3.6.(4).)

4)   An egress door from an individual dwelling unit or from a suite of residential occupancy is permitted to be provided with additional devices that require a releasing operation additional to the main door release hardware, provided the devices are readily operable from the inside without the use of keys, special devices or specialized knowledge. (See Note A-3.3.1.13.(4).)

5)   Except as provided in Sentence 3.4.6.17.(9), door release hardware shall be installed between 900 mm and 1 100 mm above the finished floor.

6)   An egress door in an access to exit serving a contained use area or an impeded egress zone is permitted to be equipped with locking devices, provided they can be released either locally or remotely in conformance with Sentence (8) or (9). (See Note A-3.3.1.13.(6).)

7)   A door in an access to exit is permitted to be equipped with an electromagnetic lock conforming to Sentence 3.4.6.16.(5) or (6).

8)   Local locking devices permitted by Sentence (6) shall be operable by a key from both sides of the door.

9)   Controls for the remote release of door locking devices permitted by Sentence (6) shall be located in an area readily available to security personnel.

10)   Locking devices permitted by Sentence (6) that are electrically operated shall be

a)   designed to operate on emergency power, and

b)   capable of manual release by security personnel.

3.3.1.14. Ramps and Stairways

1)   Except as permitted by Sentence (2), Article 3.3.4.7. and Subsection 3.3.2., ramps and stairways that do not serve as exits shall conform to the requirements for exit ramps and stairways stated in Sentence 3.4.3.2.(8) and Articles 3.4.3.4., and 3.4.6.1. to 3.4.6.9.

2)   Ramps and stairways that serve service rooms, service spaces or industrial occupancies need not comply with Sentence (1), provided

a)   they are intended only for occasional use for servicing equipment and machinery, and

b)   they do not serve as exits.

3.3.1.15. Exterior Passageways

1)   An exterior passageway leading to a required exit shall conform to the requirements of Section 3.4. for exterior exit passageways.

3.3.1.16. Tapered Treads in a Curved Flight

1)   Flights of stairs shall consist solely of

a)    straight flights, or

b)   curved flights complying with Sentence (2).

2)   Tapered treads in a curved flight that is not required as an exit shall have

a)   a minimum run of 150 mm,

b)   a run not less than 280 mm when measured at a point 300 mm from the centre line of the handrail at the narrow end of the tread, and

c)   a riser conforming to Sentence 3.4.6.8.(2).

3)   Tapered treads shall have a consistent angle and uniform run and rise dimensions in accordance with the construction tolerances stipulated in Article 3.4.6.8. when measured at a point 300 mm from the centre line of the handrail at the narrow end of the tread.

4)   All tapered treads within a flight shall turn in the same direction.

3.3.1.17. Capacity of Access to Exits

(See Article 3.3.1.9. for minimum widths of corridors.)

1)   The capacity of an access to exit shall be based on the occupant load of the portion of the floor area served.

2)   In an access to exit the required width of ramps with a slope not more than 1 in 8, doorways, and corridors shall be based on not less than 6.1 mm per person.

3)   In an access to exit the required width of a ramp with a slope more than 1 in 8 shall be based on not less than 9.2 mm per person.

4)   In an access to exit from a floor area used or intended to be used for patients in a Group B, Division 2 occupancy or residents in a Group B, Division 3 occupancy, the required width of corridors, doorways, and ramps shall be based on not less than 18.4 mm per person.

5)   The capacity of stairs in an access to exit shall conform to the requirements for stairs in Sentences 3.4.3.2.(1) to (3).

6)   In a building that is not sprinklered throughout in accordance with Sentence 3.2.5.12.(1), an access to exit that is part of the principal entrance serving a dance hall or a licensed beverage establishment with an occupant load more than 250 shall provide at least one half of the required exit width.

3.3.1.18. Guards

1)   Except as provided in Sentence (5) and Article 3.3.2.9., a guard not less than 1 070 mm high shall be provided

a)   around any roof to which access is provided for purposes other than maintenance,

b)   at openings into smoke shafts referred to in Subsection 3.2.6. that are less than 1 070 mm above the floor, and

c)   at each raised floor, mezzanine, balcony, gallery, interior or exterior vehicular ramp, and at other locations where (see Note A-9.8.8.1.)

i)   the difference in elevation is more than 600 mm between the walking surface and the adjacent surface, or

ii)   the adjacent surface within 1.2 m of the walking surface has a slope of more than 1 in 2.

2)   Except as provided in Sentences (3) and 3.3.2.9.(4) and Articles 3.3.4.7. and 3.3.5.10., openings through guards shall be of a size that prevents the passage of a spherical object whose diameter is more than 100 mm.

3)   Openings through guards other than those required by Sentence (1) that serve occupancies other than industrial occupancies shall be of a size that

a)   prevents the passage of a spherical object whose diameter is 100 mm, or

b)   permits the passage of a spherical object whose diameter is 200 mm.

(See Note A-9.8.8.5.(4).)

4)   Except for guards conforming to Article 3.3.5.10., guards that protect a level located more than one storey or 4.2 m above the adjacent level shall be designed so that no member, attachment or opening located between 140 mm and 900 mm above the level protected by the guard facilitates climbing. (See Note A-9.8.8.6.(1).)

5)   Sentence (1) does not apply

a)   to the front edges of stages,

b)   to floor pits in repair garages,

c)   to loading docks, or

d)   where access is provided for maintenance purposes only.

3.3.1.19. Tactile Walking Surface Indicators

1)   Except as provided in Sentence (2), tactile attention indicators complying with Clauses 4.3.5.3.1, 4.3.5.3.3 and 4.3.5.3.4 of CSA B651, “Accessible design for the built environment,” shall be installed

a)   at the top of flights of stairs that are unenclosed, and

b)   at drop-off edges with a change in elevation greater than 300 mm that are unprotected by a guard.

(See Note A-3.3.1.19.(1).)

2)   Sentence (1) does not apply to service spaces, bleachers addressed in Subsection 3.3.2., stages, loading docks, industrial occupancies, within dwelling units, and to stairs and drop-off edges serving not more than two dwelling units.

3.3.1.20. Transparent Doors and Panels

1)   Except as permitted by Sentence (5), a glass or transparent door shall be designed and constructed so that the existence and position of the door is readily apparent, by attaching visually contrasting hardware, bars or other permanent fixtures to it.

2)   The visibility of fully glazed transparent doors, sidelights and panels shall be enhanced through the inclusion of mullions, markings or other elements that

a)   are visually contrasting,

b)   are at least 50 mm high,

c)   extend the full width of the door, sidelight or panel, and

d)   are located between 1 350 mm and 1 500 mm above the floor.

3)   A glass door shall be constructed of

a)   laminated or tempered safety glazing conforming to CAN/CGSB-12.1, “Safety Glazing,” or

b)   wired glass conforming to CAN/CGSB-12.11-M, “Wired Safety Glass.”

4)   Except as permitted by Sentence (5), transparent panels used in an access to exit that, because of their physical configuration or design, could be mistaken as a means of egress shall be made inaccessible by barriers or railings.

5)   Sliding glass partitions that separate a public corridor from an adjacent occupancy and that are open during normal working hours need not conform to Sentences (1) and (4), provided the partitions are suitably marked in conformance with Sentence (2) to indicate their existence and position.

6)   Where vision glass is provided in doors or transparent sidelights, the lowest edge of the glass shall be no higher than 900 mm above floor level.

7)   Glass in doors and in sidelights that could be mistaken for doors, within or at the entrances to dwelling units and in public areas, shall conform to the requirements of Article 9.6.1.4.

8)   A window in a public area that extends to less than 1 000 mm above the floor and is located above the second storey in a building of residential occupancy, shall be protected by a barrier or railing to not less than 1 070 mm above the floor, or the window shall be non-openable and designed to withstand the lateral design loads for balcony guards required by Article 4.1.5.14.

3.3.1.21. Exhaust Ventilation and Explosion Venting

1)   Except as provided in Sentence (2), an exhaust ventilation system designed in conformance with the appropriate requirements of Part 6 shall be provided in a building or part of a building in which dust, fumes, gases, vapour or other impurities or contaminants have the potential to create a fire or explosion hazard. (See also Article 4.2.4.13.)

2)   Where a fire separation required to have a fire-resistance rating is penetrated by a ventilation system required by Sentence (1) for power-ventilated enclosures in laboratories, the ducts shall be

a)   continuously enclosed from the first penetrated fire separation to any subsequent fire separations or concealed spaces and all the way through to the outdoors so that the highest fire-resistance rating of all the penetrated fire separations is maintained, and

b)   exempted from the requirement to be equipped with a fire damper, smoke damper and combination smoke/fire damper as stated in Article 3.1.8.7.

3)   Explosion relief devices, vents or other protective measures conforming to Subsection 6.3.1. and Article 6.9.1.2. shall be provided for a space in which substances or conditions that have the potential to create an explosion hazard are present as a result of the principal use of a building.

3.3.1.22. Janitors' Rooms

1)   Except as permitted by Sentences (2) and (3), a room or space within a floor area for the storage of janitorial supplies shall be separated from the remainder of the building by a fire separation having a fire-resistance rating not less than 1 h.

2)   The fire-resistance rating of the fire separation required by Sentence (1) is permitted to be less than 1 h but not less than 45 min provided the fire-resistance rating required by Subsection 3.2.2. is permitted to be less than 1 h for

a)   the floor assembly above the floor area, or

b)   the floor assembly below the floor area, if there is no floor assembly above.

3)   The fire separation required by Sentence (1) is not required to have a fire-resistance rating if the floor area in which the room or space is located is sprinklered throughout.

3.3.1.23. Common Laundry Rooms

1)   Except as permitted by Sentences (2) and (3), in a building of residential occupancy, a laundry room in a floor area that is not within a dwelling unit shall be separated from the remainder of the building by a fire separation having a fire-resistance rating not less than 1 h.

2)    The fire-resistance rating of the fire separation required by Sentence (1) is permitted to be less than 1 h but not less than 45 min provided the fire-resistance rating required by Subsection 3.2.2. is permitted to be less than 1 h for

a)   the floor assembly above the floor area, or

b)   the floor assembly below the floor area, if there is no floor assembly above.

3)   The fire separation required by Sentence (1) is not required to have a fire-resistance rating if the floor area in which the laundry room is located is sprinklered throughout.

3.3.1.24. Obstructions

1)   No obstruction shall be permitted in any occupancy that would restrict the width of a normal means of egress from any part of a floor area to less than 750 mm unless an alternative means of egress is provided adjacent to, accessible from, and plainly visible from the obstructed means of egress. (See Note A-3.3.1.24.(1).)

3.3.1.25. Signs in Service Spaces

1)   Illuminated signs conforming to Sentences 3.4.5.1.(2) and (6) shall be provided to indicate the direction to egress points in a service space referred to in Sentence 3.2.1.1.(8).

3.3.1.26. Welding and Cutting

1)   Except as provided in Sentence (2), welding and cutting operations shall be carried out in a room

a)   separated from the remainder of the building by a fire separation having a fire-resistance rating not less than 1 h, or

b)   protected by an automatic fire extinguishing system.

2)   Sentence (1) shall not apply to industrial occupancies where the welding and cutting operations do not present a fire or explosion hazard to adjacent areas.

3.3.2. Assembly Occupancy

3.3.2.1. Scope

1)   This Subsection applies to assembly occupancies and to outdoor places of assembly.

2)   Except as required in Sentence (3), provisions 12.2.3.2, 12.2.3.3, 12.2.5.4, 12.2.5.5, 12.2.5.6, 12.2.11.1, 12.4.1 and 12.4.2 of Chapter 12 of NFPA 101, “Life Safety Code,” are permitted to be used in lieu of Articles 3.3.2.4., 3.3.2.5., 3.3.2.9., 3.3.2.11. and 3.3.2.12. (See Note A-3.3.2.1.(2).)

3)   The minimum clear width of aisle accessways between rows of seats shall be calculated according to provisions 12.2.5.5.2, 12.2.5.5.4.1 and 12.2.5.5.5.1 of Chapter 12 of NFPA 101, “Life Safety Code,” except that in no case shall the width be less than 400 mm.

3.3.2.2. Fire Separations

1)   Except as permitted by Sentence (2), the seating area of a Group A, Division 1 occupancy shall be separated from adjacent occupancies in the floor area by a fire separation having a fire-resistance rating not less than 1 h if the occupant load in the seating area exceeds 200.

2)   The fire-resistance rating of the fire separation required by Sentence (1) is permitted to be less than 1 h but not less than 45 min provided the fire-resistance rating required by Subsection 3.2.2. is permitted to be less than 1 h for

a)   the floor assembly above the floor area, or

b)   the floor assembly below the floor area, if there is no floor assembly above.

3)   If usable space exists under tiers of seats in arena-type buildings, a fire separation with a fire-resistance rating not less than 45 min shall be provided between the space and the seats or the space shall be sprinklered.

3.3.2.3. Non-fixed Seating

1)   Non-fixed seating shall conform to the British Columbia Fire Code.

3.3.2.4. Fixed Seats

1)   Except for the requirements of Article 3.3.2.8. for bench-type seats and except as required or permitted by Sentence (2) and Articles 3.3.2.11. and 3.3.2.12., fixed seats in places of assembly shall be

a)   attached or secured to the floor, platform or platform riser,

b)   provided with arms and back, and

c)   arranged in rows having an unobstructed passage not less than 400 mm wide measured horizontally between plumb lines from the backs of the seats in one row and the edges of the furthest forward projection of the seats in the next row in the unoccupied position.

2)   For fixed seats with backs and with folding tablet arms, the value of 400 mm required by Clause (1)(c) shall be measured when the tablet arms are in the use position, but is permitted to be measured in the stored position provided

a)   there are not more than 7 seats between any seat and the nearest aisle,

b)   the seats are located in a lecture hall or an auditorium used for instructional purposes, and

c)   the tablet arm, when raised manually to a vertical position, falls by the force of gravity to the stored position.

(See Note A-3.3.2.4.(2).)

3)   Except as permitted by Sentence (4), aisles shall be located so that there are not more than 7 seats with backs or 20 seats without backs between any seat and the nearest aisle.

4)   The requirements of Sentence (3) do not apply if

a)   egress doorways are provided to serve both ends of rows of seats,

b)   each doorway referred to in Clause (a) serves not more than 3 rows of seats, and

c)   each row contains not more than 100 seats.

3.3.2.5. Aisles

1)   Except as required by Articles 3.3.2.11. and 3.3.2.12., aisles leading to exits shall be provided in conformance with Sentences (2) to (17) in places of assembly which contain fixed seats.

2)   The minimum clear width of aisles shall be not less than 1 100 mm, except that the width is permitted to be reduced to not less than

a)   750 mm if serving not more than 60 seats, and

b)   900 mm if serving seats on one side only.

3)   Except in the case of bleacher seats, the minimum clear width of aisles referred to in Sentence (2) shall be measured at the point farthest from an exit, cross aisle or foyer and shall be increased by 25 mm for each metre of distance toward the exit, cross aisle or foyer.

4)   Aisles shall terminate in a cross aisle, foyer or exit, and the width of the cross aisle, foyer or exit shall be not less than the required width of the widest aisle plus 50% of the total required width of the remaining aisles that it serves.

5)   Dead-end aisles shall be not more than 6 m long.

6)   The length of travel to an exit door by any aisle shall be not more than 45 m.

7)   Side aisles shall be not less than 1 100 mm wide if seating is provided in conformance with Sentence 3.3.2.4.(4).

8)   An aisle that has a slope not more than 1 in 8 shall not be stepped.

9)   An aisle that slopes more than 1 in 8 shall be stepped.

10)   The passageway between rows of seats served by a stepped aisle shall be level at right angles to the line of travel.

11)   The riser of a step in an aisle shall be

a)   not less than 110 mm high, and

b)   not more than 200 mm high.

12)   Variations are permitted in riser height provided

a)   the height of adjacent risers does not vary by more than 6 mm, and

b)   the width of a tread or a platform in the direction of travel is not less than 430 mm.

13)   Steps in an aisle shall

a)   have a run not less than 230 mm exclusive of nosings,

b)   have a tread width not less than 250 mm,

c)   extend to the adjacent rows of seats in a manner that will not create a hazard from tripping, and

d)   have a finish on the treads conforming to Sentence 3.4.6.1.(1).

14)   The location of every riser in an aisle shall be made apparent from both directions of travel by strategically placed lighting or contrasting marking stripes.

15)   A platform in an aisle shall be level, except that a slope not more than 1 in 50 is permitted for a platform that is not less than 430 mm wide in the direction of exit travel.

16)   If a step is used at the entry to a row of seats from a stepped aisle, an unobstructed platform not less than 800 mm square shall be provided adjacent to the aisle.

17)   The finish of the surface of a platform in or adjacent to a stepped aisle shall conform to Sentence 3.4.6.1.(1).

3.3.2.6. Corridors

1)   Except as permitted by Sentences (2) to (4), a corridor used by the public in an assembly occupancy as an access to exit shall be separated from the remainder of the floor area by a fire separation having a fire-resistance rating not less than 1 h.

2)   The fire-resistance rating of the fire separation required by Sentence (1) is permitted to be less than 1 h but not less than 45 min provided the fire-resistance rating required by Subsection 3.2.2. is permitted to be less than 1 h for

a)   the floor assembly above the floor area, or

b)   the floor assembly below the floor area, if there is no floor assembly above.

3)   The fire-resistance rating required by Sentence (1) is permitted to be waived if the floor area in which the corridor is located is sprinklered throughout.

4)   The requirement for a fire separation stated in Sentence (1) is permitted to be waived if the distance from any point in the floor area to an exit measured along the path of travel to the exit does not exceed the travel distance permitted by Article 3.4.2.5.

3.3.2.7. Doors

1)   A door equipped with a latching mechanism in an access to exit from a room or suite of assembly occupancy containing an occupant load more than 100 shall be equipped with a device that complies with Sentence 3.4.6.16.(3).

3.3.2.8. Fixed Bench-Type Seats without Arms

1)   If fixed bench-type seats without arms are provided, the seat width per person shall be assumed to be 450 mm.

2)   The centre-to-centre spacing between rows of bench-type seats shall be not less than 760 mm if back rests are provided, and not less than 550 mm if back rests are not provided.

3)   A clear space of not less than 300 mm shall be provided between the back of each seat and the front of the seat immediately behind it.

3.3.2.9. Guards

1)   Except as required by Sentences (2) to (4) for bleacher seats, guards shall be installed in outdoor and indoor places of assembly with fixed seats so that

a)   at the fascia of every box, balcony or gallery where the seats extend to the edge, the height of guards is not less than

i)   760 mm in front of the seats, and

ii)   920 mm if located at the end of aisles or at the foot of steps,

b)   the height of guards along every cross aisle other than those adjacent to the fascia of every box, balcony or gallery is not less than 660 mm, except that guards need not be provided if the backs of the seats along the front side of the aisle are not less than 600 mm above the floor of the aisle, and

c)   where the seating is arranged in successive tiers and the height of rise between platforms is more than 450 mm, the height of guards is not less than 660 mm along the entire row of seats at the edge of the platform.

2)   The backs and ends of bleacher seats more than 1 200 mm above the ground or floor that are not adjacent to a wall shall be protected with a guard

a)   not less than 1 070 mm high above an adjacent aisle surface or foot rest, and

b)   not less than 920 mm high above the centre of an adjacent seat board.

3)   If the front of a bleacher is more than 600 mm above the ground or floor, it shall be protected with a guard not less than 840 mm high above the front foot rest.

4)   The size of any opening in a guard required by Sentences (2) and (3) shall not allow the passage of a sphere whose diameter is more than 300 mm.

3.3.2.10. Handrails in Aisles with Steps

(See Note A-3.3.2.10.)

1)   Handrails shall be provided in aisles with steps in conformance with Table 3.3.2.10.

Table 3.3.2.10.

Types and Location of Handrails in Aisles with Steps

Forming Part of Sentence 3.3.2.10.(1)

| Aisle Width | Aisle Serving Seating on One Side | Aisle Serving Seating on Both Sides |
| --- | --- | --- |
|  | Handrail Requirements |  |
| Less than 1 100 mm | a continuous handrail located on the side of the aisle opposite the seats that conforms to Sentences 3.4.6.5.(5) to (8), (11), (13) and (14) | a handrail located on one side at the end of each row of seats that conforms to Sentences 3.4.6.5.(5) to (8), (11), (13) and (14) |
| 1 100 mm or more | a centre-line handrail that conforms to Sentence (2) or a continuous handrail located on the side of the aisle opposite the seats that conforms to Sentences 3.4.6.5.(5) to (8), (11), (13) and (14), plus a handrail located at the end of each row of seats that conforms to Sentences 3.4.6.5.(5) to (8), (11), (13) and (14) | a centre line handrail that conforms to Sentence (2) |

2)   Handrails installed along aisle centre lines as required by Table 3.3.2.10. shall

a)   comply with Sentences 3.4.6.5.(5) to (7) and (14),

b)   have gaps not less than 560 mm and not more than 915 mm wide, measured horizontally, at intervals not exceeding five rows,

c)   comply with Sentence 3.4.6.5.(11) at terminations and required gaps, and

d)   have an intermediate rail located 305 mm below the principal handrail.

3.3.2.11. Outdoor Places of Assembly

1)   A Group A, Division 4 occupancy and each tier or balcony that has a capacity of more than

a)   1 000 persons shall have not less than 3 separate exits, or

b)   4 000 persons shall have not less than 4 separate exits.

2)   In a Group A, Division 4 occupancy, every seat shall be located so that the travel distance is not more than 45 m measured along the path of travel from the seat to

a)   the ground,

b)   an exit,

c)   an opening to a passageway leading from the seating area, or

d)   a portal, a vomitory or any other opening through the seating deck structure.

3)   Exits from outdoor stadia or grandstands shall be located not more than 25 m apart.

4)   The capacity of a means of egress for a Group A, Division 4 occupancy shall conform to the requirements of Sentence 3.4.3.2.(3).

5)   Aisles in a Group A, Division 4 occupancy shall

a)   be located so that there are not more than 20 seats between any seat and the nearest aisle, and

b)   be not less than 1 200 mm wide, except that an aisle serving less than 60 persons is permitted to be 750 mm wide.

3.3.2.12. Bleachers

1)   Steps provided in aisles of bleachers of the telescopic type shall

a)   have risers not more than 250 mm high, and

b)   have treads with a run not less than 280 mm.

2)   If the vertical distance between seating platforms in bleachers is more than 280 mm, an intermediate step shall be provided the full width of the aisle and proportioned to provide 2 equal risers between platforms.

3)   If the vertical distance between seating platforms in bleachers is more than 450 mm, 2 intermediate steps shall be provided the full width of the aisle so that there are 3 equal risers between platforms.

4)   If the passageway between rows of seats is not a closed deck, footboards shall be provided so that

a)   the total width of the footboards shall be not less than three quarters of the centre-to-centre spacing between rows of seats, and

b)   the spacing between footboard members shall be not more than 25 mm.

5)   Openings above footboards and below the seats in rows of bleacher seats shall be provided with intermediate construction so that there is no opening that would permit the passage of a sphere of more than 100 mm in diameter.

3.3.2.13. Libraries

1)   Except as permitted by Sentence (2), a library book storage room that is not normally accessible to the public shall be separated from the remainder of the building by a fire separation with a fire-resistance rating not less than 2 h if it

a)   is more than 250 m2 in area, or

b)   contains book stacks that

i)   are more than 10 m high, or

ii)   penetrate more than one floor assembly.

2)   The fire separation required by Sentence (1) is not required if the book storage room is sprinklered.

3)   Open book shelves are permitted above and below a mezzanine floor in a library building provided the height of the shelves is not more than 2.1 m but not more than 75% of the floor-to-ceiling height of the space above or below the mezzanine floor assembly.

3.3.2.14. Stages for Theatrical Performances

1)   A stage for theatrical performances and ancillary spaces, including workshops, dressing rooms and storage areas, shall be sprinklered.

2)   A fire separation with a fire-resistance rating not less than 1 h shall be provided between a stage for theatrical performances and ancillary spaces, including workshops, dressing rooms and storage areas.

3)   Except as permitted by Sentence (6), a stage for theatrical performances and ancillary spaces, including workshops, dressing rooms and storage areas, shall be separated from the seating area by a fire separation having a fire-resistance rating not less than 1 h, except for a proscenium opening protected with

a)   a sprinkler deluge system conforming to the requirements of NFPA 13, “Standard for the Installation of Sprinkler Systems,”

b)   an unframed fire curtain if the opening is not more than 20 m wide, or

c)   a semi-rigid fire curtain if the opening is more than 20 m wide.

4)   A fire curtain required by Sentence (3) shall be of a type acceptable to the authority having jurisdiction and designed to close

a)   automatically upon the actuation of the sprinkler system,

b)   automatically upon actuation of the fire alarm system, and

c)   manually by remote control devices located at the curtain control panel and at each side of the stage.

5)   At least 2 vents for the purpose of venting fire and smoke to the outside of a building shall be provided above a stage designed for theatrical performances and shall

a)   have an aggregate area not less than one eighth of the area of the stage behind the proscenium opening, and

b)   be arranged to open automatically upon actuation of the sprinkler system.

6)   The fire separation referred to in Sentence (3) is not required between a stage and a seating area in a building that is sprinklered throughout, provided a sprinkler deluge system is installed at the boundary between the stage and the seating area.

3.3.2.15. Risers for Stairs

1)   In a Group A, Division 2 occupancy used for the serving of food and beverages, an interior flight of stairs with fewer than 3 risers is permitted provided it

a)   is not less than 900 mm wide,

b)   is illuminated at all times that occupants are on the premises, and

c)   has a handrail on each side.

3.3.2.16. Storage Rooms

1)   Where storage rooms are required by Part 4 of Division B of the British Columbia Fire Code for the storage of flammable liquids or combustible liquids in assembly occupancies, such rooms shall not be located above or below the first storey.

3.3.2.17. Safety Glazing

1)   Except as permitted in Sentence (3), glazing in all fixed and operable panels of doors shall conform to Class A of CAN/CGSB-12.1, “Safety Glazing.”

2)   Except as permitted in Sentence (4), glazing in all fixed and operable panels of windows shall conform to Class A of CAN/CGSB-12.1, “Safety Glazing.”

3)   Glazing in individual fixed or operable panels of a door need not comply with Sentence (1), where

a)   the bottom exposed edge of the glazing is located more than 1 525 mm above the walking surface on each side of the door, or

b)   the glazed opening in the door does not permit the passage of a sphere whose diameter is more than 75 mm.

4)   Glazing in individual fixed or operable panels of a window need not comply with Sentence (2), where

a)   the bottom exposed edge of the glazing is located more than 1 525 mm above the walking surface on each side of the window, or

b)   the glazing is located more than 915 mm away from the walking surface on each side of the window measured perpendicular to the plane of the glazing.

3.3.2.18. Daycare Facilities for Children under 30 Months

(See Note A-3.3.2.18.)

1)   A daycare facility for children where children under 30 months are accommodated shall be located

a)   in a building that is sprinklered throughout, or

b)   not more than 1 storey above or below a storey with an exit that opens directly to the exterior of the building at ground level.

2)   A fire alarm system shall be installed in a building that contains a daycare facility described in Sentence (1) if

a)   the building contains one or more other suites, or

b)   the daycare facility shares an interior means of egress.

3)   If a fire alarm system is required by Sentence (2) or Subsection 3.2.4. to be installed in a daycare facility described in Sentence (1), smoke detectors shall be installed in

a)   each room of the daycare facility, and

b)   each corridor serving as part of a means of egress from the daycare facility.

4)   If a fire alarm system is not installed in a daycare facility described in Sentence (1), smoke alarms conforming to CAN/ULC-S531, “Standard for Smoke Alarms,” shall be installed in

a)   each room of the daycare facility, and

b)   each corridor serving as part of a means of egress from the daycare facility.

5)   Smoke alarms required by Sentence (4) shall

a)   comply with Sentences 3.2.4.20.(6) and (12), and

b)   if more than one smoke alarm is required, be wired so that the actuation of one of the required smoke alarms will cause all the required smoke alarms to sound.

3.3.3. Care, Treatment or Detention Occupancies

3.3.3.1. Application

1)   This Subsection applies to care, treatment and detention occupancies. (See Note A-3.3.3.1.(1).)

3.3.3.2. Separations between Care, Treatment or Detention Occupancies and Repair Garages

1)   The fire separation required by Sentence 3.3.5.5.(1) between a care, treatment or detention occupancy and a repair garage shall have no openings.

3.3.3.3. Corridors

1)   Except as provided in Sentence (2), a corridor used by the public or serving patients' or residents' sleeping rooms shall have no dead-end portion.

2)   Corridors are permitted to have dead-portions, where

a)   the area served by the dead-end portion has a second and separate means of egress, or

b)   the corridor serves a suite of care occupancy and the dead-end portion does not exceed 6 m.

3)   Corridors shall be not less than

a)   2 400 mm wide in buildings of treatment occupancy where the corridors may be used to move patients or residents in beds,

b)   1 650 mm wide

i)   in buildings of care or treatment occupancy where the corridors will not be used to move patients or residents in beds, and

ii)   in buildings of care occupancy with more than 10 residents and where the corridors serve the residents, or

c)   1 100 mm wide in buildings of care occupancy with not more than 10 residents.

4)   Paired doors in a corridor referred to in Clause (3)(a) shall

a)   swing in opposite directions, the right-hand door swinging in the direction of travel, and

b)   be not less than 1 100 mm wide.

3.3.3.4. Doorway Width

1)   Except as provided in Sentence (2) and within individual suites of care occupancy, the minimum clear width of a doorway shall be 850 mm where it opens into or is located within a public corridor or other facility that provides access to exit for patients or residents in floor areas containing care or treatment occupancies.

2)   The minimum clear width of doorways through which it is necessary to move patients in bed shall be 1 050 mm. (See Note A-3.3.3.4.(2).)

3.3.3.5. Compartments and Fire Separations

1)   Floor areas containing patients' or residents' sleeping rooms in a care or treatment occupancy where overnight sleeping accommodation is provided for more than a total of 10 patients or residents shall conform to Sentences (2) to (13).

2)   Except as permitted by Sentence (3), a floor area described in Sentence (1) shall be divided into not less than 2 fire compartments, each not more than 1 000 m2 in area.

3)   The floor area on either side of a horizontal exit conforming to Article 3.4.6.10. is permitted to be considered as a fire compartment in applying the requirements of this Article.

4)   Except as permitted by Sentence (5), fire separations separating fire compartments required by Sentence (2) shall have a fire-resistance rating not less than 1 h.

5)   The fire-resistance rating of a fire separation referred to in Sentence (4) is permitted to be less than 1 h but not less than 45 min provided the fire-resistance rating required by Subsection 3.2.2. is permitted to be less than 1 h for

a)   the floor assembly above the floor area, or

b)   the floor assembly below the floor area, if there is no floor assembly above.

6)   The travel distance from any point within each fire compartment referred to in Sentence (2) to a door to an adjoining fire compartment shall be not more than 45 m.

7)   Each fire compartment referred to in Sentence (2) shall be capable of accommodating, in addition to its own occupants, the occupants of the largest adjacent fire compartment based on a clear floor space of 2.5 m2 per patient in the adjacent fire compartment.

8)   Except as provided in Sentences (9) to (13), walls between patients' or residents' sleeping rooms and the remainder of the floor area shall be constructed as fire separations but are not required to have a fire-resistance rating unless one is required by other provisions in this Part. (See Note A-3.1.8.1.(1)(b).)

9)   The fire separation requirements of Sentence (8) do not apply to walls within a group of intercommunicating patients' or residents' sleeping rooms, provided the group of rooms does not

a)   contain more than 5 patients or residents, or

b)   include storage, bathing or toilet facilities serving persons not occupying the group of rooms.

(See Note A-3.3.3.5.(9).)

10)   The fire separation requirements of Sentence (8) do not apply to walls within individual suites of care occupancy.

11)   A door in a fire separation required by Sentence (8) is permitted to be equipped with a roller latch.

12)   Except as permitted by Sentence (13), a fire separation required by Sentence (8) shall not have any grilles, louvres or other openings.

13)   A door or wall separating a patient's or resident's sleeping room from an ensuite toilet room, shower room or similar ancillary space is permitted to incorporate grilles and louvres, provided

a)   the adjacent rooms are not used to store flammable or combustible materials, and

b)   the openings are located so that smoke cannot pass through these rooms to other parts of the building.

(See Note A-3.3.3.5.(13).)

14)   Walls between individual suites of care occupancy and the remainder of the floor area in buildings of care occupancy shall be constructed as fire separations with a fire-resistance rating not less than that specified for residential occupancies in Sentences 3.3.4.2.(1) and (2).

15)   Floor assemblies within individual suites of care occupancy need not be constructed as fire separations, provided the suites meet the conditions described in Clauses 3.3.4.2.(3)(a) and (b).

16)   The fire-resistance rating of the fire separation required by Sentence 3.3.5.6.(1) is permitted to be waived if the fire separation is located between individual suites of care occupancy and an attached storage garage containing not more than 5 vehicles, provided the conditions described in Sentence 3.3.4.2.(4) are met.

3.3.3.6. Areas of Refuge

1)   Compartments containing rooms such as operating rooms, recovery rooms, delivery rooms and intensive care units, from which it is impracticable to move patients in an emergency, shall be

a)   separated from adjacent spaces by fire separations having a fire-resistance rating not less than 1 h, and

b)   provided with a mechanical air supply so that during a period of 2 h after the start of a fire in another space, the compartments will not contain more than 1% by volume of contaminated air from the fire area.

3.3.3.7. Contained Use Areas

1)   A contained use area shall conform to Sentences (2) to (5).

2)   A contained use area shall be separated from the remainder of the building by a fire separation having a fire-resistance rating not less than 1 h.

3)   Except as permitted by Sentence (4), a building that includes a contained use area shall be sprinklered throughout.

4)   A contained use area, in a building for which Articles 3.2.2.20. to 3.2.2.92. do not require the installation of an automatic sprinkler system, is not required to be sprinklered as required by Sentence (3) provided

a)   the building is designed so that during a period of 2 h after the start of a fire in the contained use area other fire compartments will not contain more than 1% by volume of contaminated air from the contained use area,

b)   the building is designed so that during a period of 2 h after the start of a fire in another part of the building the contained use area will not contain more than 1% by volume of contaminated air from the other part of the building,

c)   all doors are designed to be remotely released in conformance with Sentence 3.3.1.13.(6), and

d)   the contained use area does not contain any rooms lined with combustible padding.

5)   A corridor serving a contained use area shall have no dead-end portion unless the area served by the dead-end portion has a second and separate means of egress.

3.3.4. Residential Occupancy

3.3.4.1. Scope

1)   This Subsection applies to residential occupancies.

3.3.4.2. Fire Separations

1)   Except as permitted by Sentences (2) and 3.2.2.9.(2), suites of residential occupancy shall be separated from each other and the remainder of the building by a fire separation having a fire-resistance rating not less than 1 h.

2)   The fire-resistance rating of the fire separation required by Sentence (1) is permitted to be less than 1 h but not less than 45 min provided the fire-resistance rating required by Subsection 3.2.2. is permitted to be less than 1 h for

a)   the floor assembly above the floor area, or

b)   the floor assembly below the floor area, if there is no floor assembly above.

3)   Floor assemblies within a dwelling unit need not be constructed as fire separations provided

a)   the distance between the lowest floor level and the uppermost floor level within the dwelling unit is not more than 6 m, and

b)   the dwelling unit is separated from the remainder of the building by a fire separation having a fire-resistance rating not less than

i)   1 h if the building is not sprinklered throughout,

ii)   45 min if the building is sprinklered throughout and it is not more than 3 storeys in building height, or

iii)   1 h if the building is sprinklered throughout and it is more than 3 storeys in building height.

4)   The fire-resistance rating of the fire separation required by Sentence 3.3.5.6.(1) is permitted to be waived if the fire separation is located between a dwelling unit and an attached storage garage containing not more than 5 vehicles, provided

a)   the dwelling unit and the attached storage garage are sprinklered,

b)   the dwelling unit and the attached storage garage are separated from the remainder of the building in conformance with Sentences (1) to (3),

c)   there are no air duct systems connecting the storage garage and the dwelling unit,

d)   the construction between the storage garage and the dwelling unit provides an effective barrier to gas and exhaust fumes, and

e)   every door between the storage garage and the dwelling unit is

i)   tight fitting and weather-stripped to provide an effective barrier against the passage of gas and exhaust fumes,

ii)   fitted with a self-closing device, and

iii)   not located in a room intended for sleeping.

5)   The fire separation required by Sentence 3.3.5.6.(1) is not required between a dwelling unit and an attached storage garage, serving that dwelling unit only, provided

a)   the dwelling unit and its attached storage garage are separated from the remainder of the building in conformance with Sentences (1) to (3),

b)   there are no air duct systems connecting the storage garage and the dwelling unit,

c)   the construction between the storage garage and the dwelling unit provides an effective barrier to gas and exhaust fumes, and

d)   every door between the storage garage and the dwelling unit is

i)   tight fitting and weather-stripped to provide an effective barrier against the passage of gas and exhaust fumes,

ii)   fitted with a self-closing device, and

iii)   not located in a room intended for sleeping.

3.3.4.3. Storage Rooms

1)   Sprinklers shall be installed in a storage room provided for the use of tenants in a residential occupancy within a floor area but not contained within a suite.

2)   Except as permitted by Sentence (3), a storage room referred to in Sentence (1) shall be separated from the remainder of the building by a fire separation having a fire-resistance rating not less than 1 h.

3)   The fire-resistance rating of the fire separation required by Sentence (2) is permitted to be less than 1 h but not less than 45 min provided the fire-resistance rating required by Subsection 3.2.2. is permitted to be less than 1 h for

a)   the floor assembly above the floor area, or

b)   the floor assembly below the floor area, if there is no floor assembly above.

4)   Except for the storage of flammable liquids and combustible liquids inside a single-family dwelling unit and garages or sheds attached to these dwelling units, where storage rooms are required by Part 4 of Division B of the British Columbia Fire Code for the storage of flammable liquids or combustible liquids in residential occupancies, such rooms shall not be located above or below the first storey.

3.3.4.4. Egress from Dwelling Units

1)   Single storey dwelling units in an apartment building need not lead to a public corridor or exterior passageway on the same storey provided the dwelling units are served by private stairways leading directly to a public access to exit on the storey

a)   immediately above, and

b)   immediately below.

(See Note A-3.3.4.4.(1).)

2)   Except as permitted by Sentences (3) and (4), a dwelling unit containing more than one storey shall have an exit door or an egress door opening directly into a public access to exit from the uppermost storey and from the lowest storey of the dwelling unit so that each of these storeys is served by an exit or egress door located not more than 1.5 m above or below its floor level.

3)   A single exit is permitted from a dwelling unit provided the exit is an exterior doorway not more than 1.5 m above adjacent ground level and

a)   it is not necessary to travel up or down more than one storey to reach the exit door, or

b)   the uppermost floor level opens to a balcony not more than 6 m above adjacent ground level.

4)   An egress door from either the uppermost storey or the lowest storey of a dwelling unit, as required by Sentence (2), need not be provided if that storey is served by a stairway that

a)   leads to a public access to exit,

b)   has no direct access to any other storey in the dwelling unit, and

c)   is separated from the other storeys in the dwelling unit by a fire separation having a fire-resistance rating not less than 45 min.

5)   In a building of residential occupancy not more than 3 storeys in building height, a doorway from a dwelling unit is permitted to open directly into an exit stairway provided the dwelling unit has a second and separate means of egress.

6)   If a dwelling unit has a second and separate means of egress, one means of egress from a dwelling unit is permitted to pass through

a)   an interior corridor served by a single exit,

b)   an exterior balcony served by a single exit stairway, or

c)   an exterior passageway served by a single exit stairway.

3.3.4.5. Automatic Locking Prohibition

1)   Except for hotels and motels, a door opening onto a public corridor which provides access to exit from a suite shall be designed not to lock automatically. (See Note A-3.3.4.5.(1).)

3.3.4.6. Sound Transmission

1)   Occupants of dwelling units shall be protected from airborne noise in conformance with Section 5.8.

3.3.4.7. Stairs, Ramps, Landings, Handrails and Guards for Dwelling Units

1)   Except as required in Article 3.3.4.8., stairs, ramps, landings, handrails and guards within a dwelling unit shall conform to the appropriate requirements in Section 9.8.

2)   Exterior stairs, ramps, landings, handrails and guards serving a single dwelling unit, and loads on guards serving not more than two dwelling units, shall conform to the appropriate requirements in Section 9.8.

3.3.4.8. Protection of Openable Windows

1)   Except as provided in Sentence (2), openable windows in suites of residential occupancy shall be protected by

a)   a guard with a minimum height of 1 070 mm constructed in accordance with Article 3.3.1.18., or

b)   a mechanism that can only be released with the use of tools or special knowledge to control the free swinging or sliding operation of the openable part of the window so as to limit any clear unobstructed opening to not more than 100 mm measured either vertically or horizontally.

2)   Windows need not be protected in accordance with Sentence (1) where

a)   the only opening having greater dimensions than those allowed by Clause (1)(b) is located higher than 1 070 mm above the finished floor, or

b)   the bottom edge of the openable portion of the window is located less than 1 800 mm above the floor or ground on the other side of the window.

3.3.4.9. Resistance to Forced Entry

1)   Dwelling units shall conform to Article 9.7.2.1. and Subsection 9.7.5.

3.3.5. Industrial Occupancy

3.3.5.1. Scope

1)   This Subsection applies to industrial occupancies.

3.3.5.2. Fire Extinguishing Systems

1)   In addition to other requirements in this Code for the installation of automatic fire extinguishing systems, an appropriate fire extinguishing system shall be installed in every industrial occupancy floor area to provide protection if required by

a)   provincial or territorial regulations or municipal bylaws, or

b)   the British Columbia Fire Code, in the absence of the regulations or bylaws referred to in Clause (a).

3.3.5.3. Basements

1)   A basement shall not be used for the storage, manufacture or handling of volatile solids, liquids or gases that generate explosive air-vapour mixtures or for processes that involve explosive dusts.

2)   Entrances and exits to a basement and to rooms containing building services shall be separate from the remainder of the building in a building in which

a)   the storage, manufacture or handling of volatile materials can generate explosive air-vapour mixtures, or

b)   processes occur that produce explosive dusts.

3)   Basements and rooms referred to in Sentence (2) shall be separated from the remainder of the building with a vapour-tight separation.

3.3.5.4. Repair and Storage Garages

1)   If access is provided from a storage garage to a stair tower or elevator serving occupancies above the level of the storage garage, the access shall be through a vestibule conforming to Sentence 3.3.5.7.(4).

2)   Treads and landings in interior stairs that extend to the roof of a storage garage shall be designed to be free of accumulations of ice and snow.

3)   A mechanical storage garage not more than 4 storeys in building height, in which no persons other than parking attendants are permitted above the street floor level, need not have a fire separation between the exits and the remainder of the building.

4)   A garage shall be provided with natural or mechanical ventilation in conformance with the requirements of Subsection 6.3.1. and Article 6.9.1.2. to prevent excessive accumulation of carbon monoxide, exhaust fumes or flammable and toxic vapours.

5)   The clear height in a storage garage shall be not less than 2 m.

6)   Where garage floors or ramps are 600 mm or more above the adjacent ground or floor level, every opening through such floors and the perimeter of floors and ramps shall be provided with

a)   a continuous curb not less than 140 mm high, a guard not less than 1 070 mm high, and a vehicle guardrail not less than 500 mm high conforming to Sentence (7), or

b)   a full-height wall conforming to Sentence (7).

7)   Vehicle guardrails and full-height walls required in Sentence (6) shall be designed and constructed to withstand the loading values stipulated in Sentence 4.1.5.15.(1).

8)   Except for open-air storeys, every storey of a storage garage or repair garage located below grade shall be sprinklered.

3.3.5.5. Repair Garage Separation

1)   A repair garage and any ancillary spaces serving it, including waiting rooms, reception rooms, tool and parts storage areas and supervisory office space, shall be separated from other occupancies by a fire separation having a fire-resistance rating not less than 2 h.

3.3.5.6. Storage Garage Separation

1)    Except as permitted by Sentences 3.3.4.2.(4) and (5), a storage garage shall be separated from other occupancies by a fire separation with a fire-resistance rating not less than 1.5 h.

3.3.5.7. Vestibules

1)   Except as provided in Sentence (2), if access is provided through a fire separation between a storage garage and a Group A, Division 1 or Group B occupancy, the access shall be through a vestibule conforming to Sentence (4).

2)   If access is provided through a fire separation between a storage garage and a Group B, Division 3 occupancy with not more than 10 occupants, access need not be through a vestibule, provided the fire separation complies with Clauses 3.3.4.2.(5)(b) to (d).

3)   In a building more than 3 storeys in building height, access through a fire separation between a storage garage and a Group A, Division 2, 3 or 4, or a Group C occupancy, shall be through a vestibule conforming to Sentence (4).

4)   If access is provided through a vestibule, as required by Sentences (1), (3) and 3.3.5.4.(1), the vestibule shall

a)   be not less than 1.8 m long,

b)   be ventilated

i)   naturally to outside air by a vent that has an unobstructed area of not less than 0.1 m2 for each door that opens into the vestibule but not less than 0.4 m2, or

ii)   mechanically at a rate of 14 m3/h for each square metre of vestibule floor surface area, and

c)   have openings between the vestibule and an adjoining occupancy provided with self-closing doors with no hold-open devices.

3.3.5.8. Dispensing of Fuel

1)   Facilities for the dispensing of fuel having a flash point below 37.8°C shall not be installed above any space intended for occupancy.

2)   Facilities for the dispensing of fuel having a flash point below 37.8°C shall not be installed in any building, except that this requirement does not apply to a canopy which is open on not less than 75% of its perimeter.

3.3.5.9. Multiple-Tenant Self-Storage Warehouses

1)   Except as provided in Sentence 3.9.3.1.(5) or unless the building is sprinklered throughout, each individual tenancy in a multiple tenant self storage warehouse classified as an industrial occupancy shall be separated from the remainder of the building by a fire separation having a fire-resistance rating not less than 45 min.

3.3.5.10. Guards

1)   Except where they serve storage garages, guards in industrial occupancies are permitted to consist of

a)   a top railing, and

b)   one or more intermediate rails spaced such that openings through the guard are of a size that prevents the passage of a spherical object whose diameter is 535 mm.

3.3.6. Design of Hazardous Areas

3.3.6.1. Application

1)   This Subsection applies to design and fire protection requirements for buildings or parts thereof used for the storage, handling, use and processing of dangerous goods, including flammable liquids and combustible liquids, in quantities in excess of those identified in Table 3.2.7.1. of Division B of the British Columbia Fire Code. (See Note A-3.3.6.1.(1).)

3.3.6.2. Storage of Dangerous Goods

1)   Solid and liquid dangerous goods classified as oxidizers or organic peroxides shall be separated from the remainder of the building by a fire separation having a fire-resistance rating of not less than 2 h.

2)   Reactive materials shall be separated from the remainder of the building by a fire separation having a fire-resistance rating of not less than 2 h. (See Note A-3.3.6.2.(2).)

3)   The design of buildings or parts thereof used for the storage of dangerous goods classified as explosives shall conform to the “Explosives Act” and its Regulations, published by Natural Resources Canada.

4)   Where wiring or electrical equipment is located in areas in which flammable gases or vapours, combustible dusts or combustible fibres are present in quantities sufficient to create a hazard, such wiring and electrical equipment shall conform to the requirements for hazardous locations as required by the Safety Standards Act and pursuant regulations. (See Note A-3.3.6.2.(4).)

3.3.6.3. Indoor Storage of Anhydrous Ammonia and Flammable, Toxic and Oxidizing Gases

1)   Where required by the British Columbia Fire Code, cylinders of dangerous goods classified as flammable gases stored indoors shall be located in a room

a)    that is separated from the remainder of the building by a gas-tight fire separation having a fire-resistance rating of at least 2 h,

b)   that is located on an exterior wall of the building,

c)   that can be entered from the exterior, and

d)   whose closures leading to the interior of the building are

i)   equipped with self-closing devices that keep the closures closed when not in use, and

ii)   constructed so as to prevent the migration of gases from the room into other parts of the building.

2)   Where required by the British Columbia Fire Code, cylinders of anhydrous ammonia or dangerous goods classified as toxic or oxidizing gases stored indoors shall be located in a room

a)   that is separated from the remainder of the building by a gas-tight fire separation having a fire-resistance rating of at least 1 h,

b)   that is located on an exterior wall of the building,

c)   that can be entered from the exterior, and

d)   whose closures leading to the interior of the building are

i)   equipped with self-closing devices that keep the closures closed when not in use, and

ii)   constructed so as to prevent the migration of gases from the room into other parts of the building.

3.3.6.4. Storage and Dispensing Rooms for Flammable Liquids and Combustible Liquids

1)   Fire separations for rooms where flammable liquids and combustible liquids are stored are required to be constructed with a fire-resistance rating in conformance with Subsection 4.2.9. of Division B of the British Columbia Fire Code.

2)   Where Class IA or IB liquids specified in Subsection 4.1.2. of Division B of the British Columbia Fire Code are dispensed within a storage room, the room shall be designed to prevent critical structural and mechanical damage from an internal explosion in conformance with good engineering practice such as that described in NFPA 68, “Standard on Explosion Protection by Deflagration Venting.” (See Note A-3.3.6.4.(2).)

3.3.6.5. Tire Storage

1)   A tire storage area designed to contain more than 375 m3 of rubber tires shall be separated from the remainder of the building by a fire separation having a fire-resistance rating of not less than 2 h. (See Note A-3.3.6.5.(1).)

3.3.6.6. Ammonium Nitrate Storage

1)   Where Article 3.2.9.1. of Division B of the British Columbia Fire Code applies due to the quantity and nature of the stored product, and as stipulated in Sentences (2) to (6), buildings used for the storage of ammonium nitrate shall be classified as medium-hazard industrial occupancies (Group F, Division 2).

2)   Buildings intended for the storage of ammonium nitrate shall be not more than one storey in building height.

3)   Buildings intended for the storage of ammonium nitrate shall not

a)   have basements or crawl spaces, or

b)   contain open floor drains, tunnels, elevator pits or other pockets that might trap molten ammonium nitrate.

4)   Buildings intended for the storage of ammonium nitrate shall have not less than 0.007 m2 of vent area for each square metre of storage area, unless mechanical ventilation is provided.

5)   All flooring in storage areas described in Sentence (1) shall be constructed of noncombustible materials.

6)   Buildings intended for the storage of ammonium nitrate shall be designed to prevent the ammonium nitrate from coming into contact with building materials that

a)   will cause the ammonium nitrate to become unstable,

b)   may corrode or deteriorate by reason of contact with the ammonium nitrate, or

c)   will become impregnated with the ammonium nitrate.

(See Note A-3.3.6.6.(6).)

3.3.6.7. Flooring Materials

1)   Floors in areas where dangerous goods are stored shall be constructed of impermeable materials to prevent the absorption of chemicals.

3.3.6.8. Fire Separations in Process Plants

1)   In process plants, areas where unstable liquids are handled or where small-scale unit chemical processes occur shall be separated from the remainder of the building by a fire separation having a fire-resistance rating of not less than 2 h.

3.3.6.9. Basements and Pits

1)   Process plants where Class I and II flammable liquids and combustible liquids are handled shall not be constructed with basements or covered pits.

Section  3.4.   Exits

3.4.1. General

3.4.1.1. Scope

1)   Exit facilities complying with this Section shall be provided from every floor area that is intended for occupancy. (See Note A-3.4.1.1.(1).)

3.4.1.2. Separation of Exits

1)   Except as permitted by Sentence (2), if more than one exit is required from a floor area, each exit shall be separate from every other exit leading from that floor area.

2)   If more than 2 exits are provided from a floor area, exits are permitted to converge in conformance with Sentence 3.4.3.1.(2), provided the cumulative capacity of the converging exits does not contribute more than 50% of the total required exit width for the floor area.

3.4.1.3. Access to Exits

1)   Access to exits shall conform to Section 3.3.

3.4.1.4. Types of Exit

1)   Subject to the requirements of this Section, an exit from any floor area shall be one of the following, used singly or in combination:

a)   an exterior doorway,

b)   an exterior passageway,

c)   an exterior ramp,

d)   an exterior stairway,

e)   a fire escape (conforming to Subsection 3.4.7.),

f)   a horizontal exit,

g)   an interior passageway,

h)   an interior ramp, or

i)   an interior stairway.

3.4.1.5. Exterior Exit Passageways

1)   Access to an exterior exit passageway from a floor area shall be through exit doors at the floor level.

3.4.1.6. Restricted Use of Horizontal Exits

1)   Except as permitted by Sentence (2), horizontal exits shall not comprise more than one half of the required number of exits from any floor area.

2)   In a hospital or nursing home with treatment, horizontal exits serving patients' sleeping rooms shall comprise not more than two thirds of the required number of exits from any floor area. (See Note A-3.4.1.6.(2).)

3.4.1.7. Slide Escapes

1)   A slide escape shall not be erected on any building as a required exit, but is permitted to be provided as an additional egress facility if unusual hazards are foreseen.

3.4.1.8. Transparent Doors and Panels

1)   Glass and transparent panels in an exit shall conform to the appropriate requirements of Article 3.3.1.20. for glass and transparent panels in an access to exit.

3.4.1.9. Mirrors near Exits

1)   No mirror shall be placed in or adjacent to any exit in a manner that would confuse the direction of exit.

3.4.1.10. Combustible Glazing in Exits

1)   Combustible glazing is not permitted in wall or ceiling assemblies or in closures used to construct an exit enclosure.

3.4.2. Number and Location of Exits from Floor Areas

3.4.2.1. Minimum Number of Exits

1)   Except as permitted by Sentences (2) to (4), every floor area intended for occupancy shall be served by at least 2 exits.

2)   A floor area in a building not more than 2 storeys in building height, is permitted to be served by one exit provided the total occupant load served by the exit is not more than 60, and

a)   in a floor area that is not sprinklered throughout, the floor area and the travel distance are not more than the values in Table 3.4.2.1.-A, or

b)   in a floor area that is sprinklered throughout

i)   the travel distance is not more than 25 m, and

ii)   the floor area is not more than the value in Table 3.4.2.1.-B.

Table 3.4.2.1.-A

Criteria for One Exit (Floor Area Not Sprinklered Throughout)

Forming Part of Sentence 3.4.2.1.(2)

| Occupancy of Floor Area | Maximum Floor Area, m2 | Maximum Travel Distance, m |
| --- | --- | --- |
| Group A | 150 | 15 |
| Group B | 75 | 10 |
| Group C | 100 | 15 |
| Group D | 200 | 25 |
| Group E | 150 | 15 |
| Group F, Division 2 | 150 | 10 |
| Group F, Division 3 | 200 | 15 |

Table 3.4.2.1.-B

Criteria for One Exit (Floor Area Sprinklered Throughout)

Forming Part of Sentence 3.4.2.1.(2)

| Occupancy of Floor Area | Maximum Floor Area, m2 |
| --- | --- |
| Group A | 200 |
| Group B | 100 |
| Group C | 150 |
| Group D | 300 |
| Group E | 200 |
| Group F, Division 2 | 200 |
| Group F, Division 3 | 300 |

3)   Except as permitted by Sentence (4), if Sentence (2) permits a single exit from a floor area classified as Group B or Group C occupancy, the exit shall be an exterior doorway not more than 1.5 m above adjacent ground level.

4)   The requirements of Sentences (1) and (2) are permitted to be waived for dwelling units that have an access to exit conforming to Sentences 3.3.4.4.(1) to (4).

5)   Exits are not required directly from rooftop enclosures that comply with Sentences 3.3.1.3.(8) and (9) or where they are served by means of egress in conformance with Sentences 3.3.1.3.(4) to (5).

3.4.2.2. Means of Egress from Mezzanines

1)   Except as permitted by Sentences (2) and (3), the space above a mezzanine shall be served by means of egress leading to exits accessible at the mezzanine level on the same basis as floor areas.

2)   The means of egress from a mezzanine need not conform to Sentence (1), provided

a)   the mezzanine is not required to terminate at a vertical fire separation, as permitted in Sentence 3.2.8.2.(1),

b)   the occupant load of the mezzanine is not more than 60,

c)   the area of the mezzanine does not exceed the area limits stated in Table 3.4.2.2., and

d)   the distance limits stated in Table 3.4.2.2. measured along the path of travel are not exceeded from any point on the mezzanine to

i)   an egress door serving the space that the mezzanine overlooks, if the space is served by a single egress door, or

ii)   the egress stairway leading to an access to exit in the space below if that space is required to be served by 2 or more egress doorways in conformance with Sentence 3.3.1.5.(1).

3)   At least half of the required means of egress from a mezzanine shall comply with Sentence (1) if the mezzanine is not required to terminate at a fire separation as permitted by Sentence 3.2.8.2.(1).

Table 3.4.2.2.

Criteria for Egress from Mezzanine Space

Forming Part of Sentence 3.4.2.2.(2)

| Occupancy of Space | Maximum Area, m2 | Distance Limits, m |
| --- | --- | --- |
| Assembly occupancy | 150 | 15 |
| Residential occupancy | 100 | 15 |
| Business and personal services occupancy | 200 | 25 |
| Mercantile occupancy | 150 | 15 |
| Medium-hazard industrial occupancy | 150 | 10 |
| Low-hazard industrial occupancy | 200 | 15 |

3.4.2.3. Distance between Exits

1)   Except as provided in Sentence (2), the least distance between 2 exits from a floor area shall be

a)   one half the maximum diagonal dimension of the floor area, but need not be more than 9 m for a floor area having a public corridor, or

b)   one half the maximum diagonal dimension of the floor area, but not less than 9 m for all other floor areas.

(See Note A-3.4.2.3.(1).)

2)   Exits need not comply with Sentence (1) where

a)   the floor area is divided so that not less than one third of the floor area is on each side of a fire separation, and

b)   it is necessary to pass through the fire separation to travel from one exit to another exit.

3)   The minimum distance between exits referred to in Sentence (1) shall be the shortest distance that smoke would have to travel between the exits, assuming that the smoke will not penetrate an intervening fire separation.

4)   The distance between 2 exterior discharges of exit stairs serving the same floor area shall be

a)   not less than 9 m, or

b)   not less than 6 m, where

i)   the building is sprinklered throughout, and

ii)   the 2 exterior discharges are located within 15 m of a street.

3.4.2.4. Travel Distance

1)   Except as permitted by Sentence (2), for the purposes of this Subsection, travel distance means the distance from any point in the floor area to an exit measured along the path of travel to the exit.

2)   The travel distance from a suite or a room not within a suite is permitted to be measured from an egress door of the suite or room to the nearest exit, provided

a)   the suite or room is separated from the remainder of the floor area by a fire separation

i)   having a fire-resistance rating not less than 45 min in a floor area that is not sprinklered throughout, or

ii)   which is not required to have a fire-resistance rating, in a floor area that is sprinklered throughout, and

b)   the egress door opens onto

i)   an exterior passageway,

ii)   a corridor used by the public that is separated from the remainder of the floor area in conformance with the requirements in Article 3.3.1.4. for the separation of public corridors, or

iii)   a public corridor that is separated from the remainder of the floor area in conformance with Article 3.3.1.4. (see Note A-3.1.8.1.(1)(b)).

3)   Travel distance to an exit shall be not more than 50 m from any point in a service space referred to in Sentence 3.2.1.1.(8).

3.4.2.5. Location of Exits

1)   Except as permitted by Sentences (2) and 3.3.2.5.(6), if more than one exit is required from a floor area, the exits shall be located so that the travel distance to at least one exit shall be not more than

a)   25 m in a high-hazard industrial occupancy,

b)   40 m in a business and personal services occupancy,

c)   45 m in a floor area that contains an occupancy other than a high-hazard industrial occupancy, provided it is sprinklered throughout,

d)   105 m in any floor area, served by a public corridor, in which rooms and suites are not separated from the remainder of the floor area by a fire separation, provided

i)   the public corridor is not less than 9 m wide,

ii)   the ceiling height in the public corridor is not less than 4 m above all floor surfaces,

iii)   the building is sprinklered throughout, and

iv)   not more than one half of the required egress doorways from a room or suite open into the public corridor if the room or suite is required to have more than one egress doorway,

e)   60 m in any storage garage that conforms to the requirements of Article 3.2.2.92., and

f)   30 m in any floor area other than those referred to in Clauses (a) to (e).

2)   Except for a high-hazard industrial occupancy, Sentence (1) need not apply if exits are placed along the perimeter of the floor area and are not more than 60 m apart, measured along the perimeter, provided each main aisle in the floor area leads directly to an exit.

3)   Exits shall be located and arranged so that they are clearly visible or their locations are clearly indicated and they are accessible at all times.

3.4.2.6. Principal Entrances

1)   For the purposes of this Section, at least one door at every principal entrance to a building providing access from the exterior at ground level shall be designed in accordance with the requirements for exits.

2)   In a building that is not sprinklered throughout in accordance with Sentence 3.2.5.12.(1), the principal entrance serving a dance hall or a licensed beverage establishment with an occupant load more than 250 shall provide at least one half of the required exit width.

3.4.3. Width and Height of Exits

3.4.3.1. Exit Width Based on Occupant Load

1)   For the purpose of determining the aggregate width of exits, the occupant load of every room or floor area shall be determined in conformance with Subsection 3.1.17.

2)   Except as permitted by Sentence 3.4.3.2.(4), the required exit width shall be cumulative if 2 or more exits converge.

3.4.3.2. Exit Width

1)   Except as permitted by Sentence (3), the minimum aggregate required width of exits serving floor areas intended for assembly occupancies, residential occupancies, business and personal services occupancies, mercantile occupancies, and industrial occupancies shall be determined by multiplying the occupant load of the area served by

a)   6.1 mm per person for ramps with a slope of not more than 1 in 8, doorways, corridors and passageways,

b)   8 mm per person for a stair consisting of steps whose rise is not more than 180 mm and whose run is not less than 280 mm, or

c)   9.2 mm per person for

i)   ramps with a slope of more than 1 in 8, or

ii)   stairs, other than stairs conforming to Clause (b).

2)   The minimum aggregate width of exits serving floor areas intended for a care, treatment or detention occupancy shall be determined by multiplying the occupant load of the area served by 18.4 mm per person.

3)   The minimum aggregate width of means of egress serving a Group A, Division 4 occupancy shall be determined by multiplying the occupant load of the area served by

a)   1.8 mm per person for

i)   aisles,

ii)   stairs other than exit stairs, and

iii)   ramps and passageways in vomitories and exits, and

b)   2.4 mm per person for exit stairs.

4)   Except as required by Sentences 3.4.3.2.(5) and (6), the required exit width need not be cumulative in an exit serving 2 or more floor areas located one above the other.

5)   The required exit width for an exit stair in an assembly hall or theatre serving more than one balcony level shall conform to Sentence (6).

6)   The required exit width for exit stairs that serve interconnected floor space designed in accordance with Articles 3.2.8.3. to 3.2.8.8. shall be cumulative, unless

a)   the stairs provide not less than 0.3 m2 of area of treads and landings for each occupant of the interconnected floor space (see Note A-3.4.3.2.(6)(a)), or

b)   protected floor spaces conforming to Article 3.2.8.5. are provided at each floor level and the protected floor space on a floor level has not less than 0.5 m2 of space for each occupant of that floor level of the interconnected floor space.

(See Note A-3.4.3.2.(6).)

7)   If more than one exit is required, every exit shall be considered as contributing not more than one half of the required exit width.

8)   The minimum widths of exits shall conform to Tables 3.4.3.2.-A and 3.4.3.2.-B.

Table 3.4.3.2.-A

Minimum Widths of Exit Corridors, Passageways, Ramps, Stairs and Doorways
in Group A, Group B, Division 1, and Groups C, D, E and F Occupancies

Forming Part of Sentence 3.4.3.2.(8)

| Occupancy Classification | Exit Corridors and Passageways, mm | Ramps, mm | Stairs, mm | Doorways, mm |
| --- | --- | --- | --- | --- |
| Group A, Group B, Division 1, Group C, Group D, Group E, Group F | 1 100 | 1 100 | 900(1) 1 100(2) | 850 |

Notes to Table 3.4.3.2.-A:

(1) Serving not more than 2 storeys above the lowest exit level or not more than 1 storey below the lowest exit level.

(2) Serving more than 2 storeys above the lowest exit level or more than 1 storey below the lowest exit level.

Table 3.4.3.2.-B

Minimum Widths of Exit Corridors, Passageways, Ramps, Stairs and Doorways in Group B, Division 2 and Division 3 Occupancies

Forming Part of Sentence 3.4.3.2.(8)

| Occupancy Classification | Exit Corridors and Passage-ways, mm | Ramps, mm |  | Stairs, mm |  | Doorways, mm |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Not serving patients' or residents' sleeping rooms(1) | Serving patients' or residents' sleeping rooms(1) | Not serving patients' or residents' sleeping rooms(1) | Serving patients' or residents' sleeping rooms(1) | Not serving patients' or residents' sleeping rooms(1) | Serving patients' or residents' sleeping rooms(1) |
| Group B, Division 2 | 1 100 | 1 100 | 1 650 | 900(2) 1 100(3) | 1 650 | 850 | 1 050 |
| Group B, Division 3 |  |  |  |  |  |  |  |
| with more than 10 residents | 1 100 | 1 100 | 1 100 | 900(2) 1 100(3) | 1 100(2) 1 650(3) | 850 | 850 |
| with not more than 10 residents | 1 100 | 1 100 | 1 100 | 900(2) 1 100(3) | 900(2) 1 100(3) | 850 | 850 |

Notes to Table 3.4.3.2.-B:

(1) Minimum widths of ramps, stairs and doorways do not apply within individual suites of care occupancy.

(2) Serving not more than 2 storeys above the lowest exit level or not more than 1 storey below the lowest exit level.

(3) Serving more than 2 storeys above the lowest exit level or more than 1 storey below the lowest exit level.

3.4.3.3. Exit Width Reduction

1)   Except as permitted by Sentences (2) and (4), no fixture, turnstile or construction shall project into or be fixed within the required width of an exit.

2)   Swinging doors in their swing shall not reduce the required width of exit stairs or landings to less than 750 mm or reduce the width of an exit passageway to less than the minimum required width.

3)   Doors shall be installed so that, when open, they do not diminish nor obstruct the required width of the exit.

4)   Handrails and construction below handrails, including handrail supports and stair stringers, shall not project more than 100 mm into the required width of a means of egress.

3.4.3.4. Headroom Clearance

(See Note A-3.4.3.4.)

1)   Except as permitted by Sentences (4) and (5), every exit shall have a clear height over the clear width of the exit of not less than 2 050 mm.

2)   The clear height of stairways shall be measured vertically over the clear width of the stairway, from the straight line tangent to the tread and landing nosings to the lowest element above. (See Note A-9.8.7.4.)

3)   The clear height of landings shall be measured within the clear width of the landing vertically to the lowest element above.

4)   Except as permitted by Sentence (5), the headroom clearance for doorways shall be not less than 2 030 mm.

5)   No door closer or other device shall be installed so as to reduce the headroom clearance of a doorway to less than 1 980 mm.

3.4.4. Fire Separation of Exits

3.4.4.1. Fire-Resistance Rating of Exit Separations

1)   Except as permitted by Sentences (2), 3.3.5.4.(3), 3.4.4.2.(2) and 3.4.4.3.(1), every exit shall be separated from the remainder of the building by a fire separation having a fire-resistance rating not less than that required by Subsection 3.2.2., but not less than 45 min, for

a)   the floor assembly above the storey, or

b)   the floor assembly below the storey, if there is no floor assembly above.

2)   The fire-resistance rating of the fire separation referred to in Sentence (1) need not be more than 2 h.

3)   If an exit stair in an assembly hall or theatre serves more than one balcony level, the exit stair shall be separated from the remainder of the building in conformance with Sentence (1).

3.4.4.2. Exits through Lobbies

1)   Except as permitted by Sentence (2), no exit from a floor area above or below the first storey shall lead through a lobby.

2)   Not more than one exit from a floor area is permitted to lead through a lobby, provided

a)   the lobby floor is not more than 4.5 m above grade,

b)   the path of travel through the lobby to the outdoors is not more than 15 m,

c)   the adjacent rooms or premises having direct access to the lobby do not contain a care, residential or industrial occupancy,

d)   the lobby is not located within an interconnected floor space other than as described in Sentence 3.2.8.2.(6),

e)   the lobby conforms to the requirements for exits, except that

i)   rooms other than service rooms and storage rooms are permitted to open onto the lobby,

ii)   the fire separation between the lobby and a room used for the sole purpose of control and supervision of the building need not have a fire-resistance rating,

iii)   the fire separation between the lobby and adjacent occupancies that are permitted to open onto the lobby need not have a fire-resistance rating provided the lobby and adjacent occupancies are sprinklered, and

iv)   passenger elevators are permitted to open onto the lobby, provided the elevator doors are designed to remain closed except while loading and unloading passengers, and

(see Note A-3.4.4.2.(2)(e))

f)   a fire separation, constructed in accordance with Sentence 3.4.4.1.(1), is maintained between the lobby and any exit permitted by this Sentence to lead through the lobby.

3.4.4.3. Exterior Passageway Exceptions

1)   The requirements of Sentences 3.4.4.1.(1) and 3.2.3.13.(1) and (3) do not apply to an exterior exit passageway provided

a)   not less than 50% of the exterior side is open to the outdoors, and

b)   an exit stair is provided at each end of the passageway.

3.4.4.4. Integrity of Exits

1)   A fire separation that separates an exit from the remainder of the building shall have no openings except for

a)   standpipe and sprinkler piping,

b)   electrical wires and cables, totally enclosed noncombustible raceways and noncombustible piping that serve only the exit,

c)   openings required by the provisions of Subsection 3.2.6.,

d)   exit doorways, and

e)   wired glass and glass block permitted by Article 3.1.8.16.

2)   Exits within scissors stairs and other contiguous exit stairways shall be separated from each other by a smoke-tight fire separation having a fire-resistance rating not less than that required for the floor assembly through which they pass.

3)   Fire separations separating contiguous stairs described in Sentence (2) shall not be pierced by doorways, ductwork, piping or any other openings that affect the continuity of the separation.

4)   A fuel-fired appliance shall not be installed in an exit.

5)   An exit shall not be used as a plenum for a heating, ventilating or air-conditioning system.

6)   An exit shall be designed for no purpose other than for exiting, except that an exit is permitted also to be designed to serve as an access to a floor area.

7)   A service room shall not open directly into an exit.

8)   Storage rooms, washrooms, toilet rooms, laundry rooms and similar ancillary rooms shall not open directly into an exit.

9)   Service spaces referred to in Sentence 3.2.1.1.(8) shall not open directly into an exit.

3.4.5. Exit Signs

3.4.5.1. Exit Signs

1)   Every exit door shall have an exit sign providing visual information placed over or adjacent to it if the exit serves

a)   a building more than 2 storeys in building height,

b)   a building having an occupant load of more than 150, or

c)   a room or floor area that has a fire escape as part of a required means of egress.

2)   Every exit sign providing visual information shall

a)   be visible on approach to the exit,

b)   consist of a green and white or lightly tinted graphical symbol meeting the colour specifications referred to in ISO 3864-1, “Graphical symbols – Safety colours and safety signs – Part 1: Design principles for safety signs and safety markings,” and

c)   conform to ISO 7010, “Graphical symbols – Safety colours and safety signs – Registered safety signs,” for the following symbols (see Note A-3.4.5.1.(2)(c)):

i)   E001 emergency exit (left hand),

ii)   E002 emergency exit (right hand),

iii)   E005 Direction, arrow (90° increments), safe condition , and

iv)   E006 Direction, 45° arrow (90° increments), safe condition .

3)   Internally illuminated exit signs shall be continuously illuminated and

a)   where illumination of the sign is powered by an electrical circuit, be constructed in conformance with CSA C22.2 No. 141, “Emergency lighting equipment,” or

b)   where illumination of the sign is not powered by an electrical circuit, be constructed in conformance with CAN/ULC-S572, “Standard for Photoluminescent and Self-Luminous Exit Signs and Path Marking Systems.”

(See Note A-3.4.5.1.(3).)

4)   Externally illuminated exit signs shall be continuously illuminated and be constructed in conformance with CAN/ULC-S572, “Standard for Photoluminescent and Self-Luminous Exit Signs and Path Marking Systems.” (See Note A-3.4.5.1.(4).)

5)   The circuitry serving lighting for externally and internally illuminated exit signs shall

a)   serve no equipment other than emergency equipment, and

b)   be connected to an emergency power supply as described in Article 3.2.7.4.

6)   Where no exit is visible from a public corridor, from a corridor used by the public in a Group A or B major occupancy, or from principal routes serving an open floor area having an occupant load of more than 150, an exit sign conforming to Clauses (2)(b) and (c) with an arrow or pointer indicating the direction of egress shall be provided.

7)   Except for egress doorways described in Sentence 3.3.2.4.(4), an exit sign conforming to Sentences (2) to (5) shall be placed over or adjacent to every egress doorway from rooms with an occupant load of more than 60 in Group A, Division 1 occupancies, dance halls, licensed beverage establishments, and other similar occupancies that, when occupied, have lighting levels below that which would provide easy identification of the egress doorway.

3.4.5.2. Exit Signs with Tactile Information

1)   An exit sign displaying the word “EXIT” in tactile form that complies with Subsection 3.8.3. shall be mounted on the approach side of exit doors described in Sentence 3.4.5.1.(1), in the direction of travel to the exit.

3.4.5.3. Signs for Stairs and Ramps at Exit Level

1)   In a building more than 2 storeys in building height, any part of an exit ramp or stairway that continues up or down past the lowest exit level shall have a posted sign clearly indicating that it does not lead to an exit.

3.4.6. Types of Exit Facilities

(See Note A-3.4.6.)

3.4.6.1. Slip Resistance of Ramps and Stairs

1)   The surfaces of ramps, and landings and treads

a)   shall have a finish that is slip resistant, and

b)   if accessible to the public, shall have either a colour contrast or a distinctive pattern, readily visible from both directions of travel, to demarcate the leading edge of the tread and the leading edge of the landing, as well as the beginning and end of a ramp.

2)   Treads and landings of exterior exit stairs more than 10 m high shall be designed to be free of ice and snow accumulations.

3.4.6.2. Minimum Number of Risers

1)   Except as permitted by Sentence 3.3.2.15.(1), every flight of interior stairs shall have not less than 3 risers.

3.4.6.3. Maximum Vertical Rise of Stair Flights and Required Landings

1)   No flight of stairs shall have a vertical rise of more than 3.7 m between floors or landings, except that a flight of stairs serving as an exit in a Group B, Division 2 occupancy shall have a vertical rise not more than 2.4 m between floors or landings.

2)   Except as provided in Sentence (3), a landing shall be provided

a)   at the top and bottom of each flight of interior and exterior stairs,

b)   at the top and bottom of every section of ramp,

c)   where a doorway opens onto a stair or ramp,

d)   where a ramp opens onto a stair, and

e)   where a stair opens onto a ramp.

3)   A landing may be omitted at the bottom of an exterior stair or ramp, provided there is no gate, door or fixed obstruction within the lesser of

a)   the width of the stair or ramp, or

b)   1 100 mm.

3.4.6.4. Dimensions of Landings

(See Note A-3.4.6.4.)

1)   Except as provided in Sentence (2), a landing shall be at least as wide and as long as the width of the stairway in which it occurs.

2)   In a straight stairway and in a stairway that turns less than 90°, the length of the landing need not be more than the lesser of

a)   the required width of stair, or

b)   1 100 mm.

3)   The length of a landing shall be measured perpendicular to the nosing of adjacent steps, at a distance equal to half the length required in Sentence (2), from the narrow edge of the landing.

4)   Where a doorway or stairway empties onto a ramp through a side wall, there shall be a level area extending across the full width of the ramp, and for a distance of 300 mm on either side of the wall opening, except one side if it abuts on an end wall.

5)   Where a doorway or stairway empties onto a ramp through an end wall, there shall be a level area extending across the full width of the ramp and along its length for not less than 900 mm.

3.4.6.5. Handrails

1)   One handrail shall be provided on stairs that are less than 1 100 mm in width.

2)   One handrail shall be provided on each side of

a)   stairs that are 1 100 mm or more in width,

b)   curved flights of any width, and

c)   ramps.

3)   In addition to Sentence (2), intermediate handrails shall be provided so that

a)   a handrail is reachable within 750 mm of all portions of the required exit width,

b)   at least one portion of the stair or ramp between two handrails is the minimum width required for stairways or ramps (see Sentences 3.4.3.2.(8) and 3.4.3.3.(4)), and

c)   all other portions of the stair or ramp between two handrails have a clear width of 510 mm or more.

4)   Where a stair or ramp is wider than its required exit width, handrails shall be located along the most direct path of travel. (See Note A-3.4.6.5.(4).)

5)   Handrails shall be continuously graspable along their entire length, be free of any sharp or abrasive elements, and have

a)   a circular cross-section with an outside diameter not less than 30 mm and not more than 50 mm, or

b)   a non-circular cross-section with a perimeter not less than 100 mm and not more than 160 mm and whose largest cross-sectional dimension is not more than 57 mm.

6)   The height of handrails on stairs, on aisles with steps and on ramps shall be measured vertically from the top of the handrail to

a)   a straight line drawn tangent to the tread nosings of the stair or aisle step served by the handrail (see Note A-9.8.7.4.), or

b)   the surface of the ramp, floor or landing served by the handrail.

7)   Except as provided in Sentence (8) and Clause 3.8.3.5.(1)(e), the height of handrails on stairs, on aisles with steps and on ramps shall be

a)   not less than 865 mm, and

b)   not more than 1 070 mm.

8)   Handrails installed in addition to required handrails need not comply with Sentence (7).

9)   Required handrails shall be continuously graspable throughout the length of

a)   a ramp, and

b)   a flight of stairs, from the bottom riser to the top riser.

(See Note A-9.8.7.2.)

10)   Except where interrupted by doorways, at least one handrail shall be continuous throughout the length of a stairway or ramp, including at landings.

11)   Handrails shall be terminated in a manner that will not obstruct pedestrian travel or create a hazard. (See Note A-3.4.6.5.(11)).

12)   At least one handrail at the side of a stairway or ramp shall extend horizontally not less than 300 mm beyond the top and bottom of the stairway or ramp.

13)   The clearance between a handrail and any surface behind it shall be not less than

a)   50 mm, or

b)   60 mm if the surface behind the handrail is rough or abrasive.

14)   Handrails and their supports shall be designed and constructed to withstand the loading values specified in Sentence 4.1.5.14.(7).

15)   A ramp shall have handrails on both sides.

3.4.6.6. Guards

1)   Every exit shall have a wall or a well-secured guard on each side, where

a)   there is a difference in elevation of more than 600 mm between the walking surface and the adjacent surface, or

b)   the adjacent surface within 1.2 m of the walking surface has a slope of more than 1 in 2.

(See Note A-9.8.8.1.)

2)   Except as required by Sentence (4), the height of guards for exit stairs and exit ramps as well as their landings shall be not less than 1 070 mm.

3)   The height of guards shall be measured vertically to the top of the guard from

a)   a line drawn through the outside edges of the stair nosings, or

b)   the surface of the ramp or landing.

4)   The height of guards for exterior stairs and landings more than 10 m above adjacent ground level shall be not less than 1 500 mm measured vertically to the top of the guard from the surface of the landing or from a line drawn through the outside edges of the stair nosings.

5)   Except as provided in Sentence 3.3.1.18.(3) and Articles 3.3.4.7. and 3.3.5.10., guards in exits shall not have any openings that permit the passage of a spherical object whose diameter is more than 100 mm.

6)   In a stairway, a window for which the distance measured vertically between the bottom of the window and a line drawn through the outside edges of the stair nosings is less than 900 mm, or a window that extends to less than 1 070 mm above the landing, shall

a)   be protected by a guard that is

i)   located approximately 900 mm above a line drawn through the outside edges of the stair nosings, or

ii)   not less than 1 070 mm high measured to the top of the guard from the surface of the landing, or

b)   be fixed in position and designed to resist the lateral design loads specified for guards and walls in Articles 4.1.5.14. and 4.1.5.16.

7)   Except for guards conforming to Article 3.3.5.10., guards that protect a level located more than one storey or 4.2 m above the adjacent level shall be designed so that no member, attachment or opening located between 140 mm and 900 mm above the level being protected by the guard facilitates climbing. (See Note A-9.8.8.6.(1).)

3.4.6.7. Ramp Slope

(See also Article 3.8.3.5.)

1)   Except as provided in Sentence (2) and (3) and as provided for aisles in Article 3.3.2.5., ramps shall have a uniform slope along their length and a maximum slope of 1 in 12.

2)   Except as provided in Section 3.8., ramps in industrial occupancies shall have a uniform slope along their length and a maximum slope of

a)   1 in 6 for interior ramps, and

b)   1 in 10 for exterior ramps.

3)   Curb ramps shall be designed in accordance with Clause 3.8.3.4.(1)(b).

3.4.6.8. Treads and Risers

(See Note A-9.8.4.)

1)   Except as permitted for dwelling units and by Sentence 3.4.7.5.(1) for fire escapes, steps for stairs shall have a run of not less than 280 mm between successive steps.

2)   Steps for stairs referred to in Sentence (1) shall have

a)   a rise between successive treads not less than 125 mm and not more than 180 mm, and

b)   a riser with either no rakeback or a rakeback of not more than 38 mm, or if nosing is provided, the underside of the nosing with an angle of not less than 60° from the horizontal.

3)   Except as provided in Article 3.3.4.7. and except for fire escape stairs, stairs that are principally used for maintenance and service, and stairs that serve industrial occupancies other than storage garages, steps for stairs shall have no open risers.

4)   Except in fire escape stairs and where an exterior stair adjoins a walkway as permitted in Sentence 3.4.6.3.(3), risers, measured as the vertical nosing-to-nosing distance, shall be of uniform height in any one flight, with a maximum tolerance of

a)   5 mm between adjacent treads or landings, and

b)   10 mm between the tallest and shortest risers in a flight.

5)   Except in fire escape stairs, treads shall have a uniform run with a maximum tolerance of

a)   5 mm between adjacent treads, and

b)   10 mm between the deepest and shallowest treads in a flight.

6)   Treads and risers shall not differ significantly in run and rise in successive flights in any stair system.

7)   The slope of treads or landings shall not exceed 1 in 50.

8)   Except as permitted by Sentence (10), the top of the nosing of stair treads shall have a rounded or beveled edge extending not less than 6 mm and not more than 13 mm measured horizontally from the front of the nosing.

9)   The front edge of stair treads in exits and public access to exits shall be at right angles to the direction of exit travel.

10)   If resilient material is used to cover the nosing of a stair tread, the minimum rounded or beveled edge required by Sentence (8) is permitted to be reduced to 3 mm.

3.4.6.9. Curved Flights in Exits

1)   Exit stair flights shall consist solely of

a)   straight flights, or

b)   curved flights complying with Sentence (2).

2)   A curved flight used as an exit shall have

a)   a handrail on each side,

b)   a minimum run of 240 mm,

c)   a run that conforms to Article 3.4.6.8. when measured at a point 300 mm from the centre line of the handrail at the narrow end of the tread, and

d)   an inside radius that is not less than twice the stair width.

3)   Tapered treads shall have a consistent angle and uniform run and rise dimensions in accordance with the construction tolerances stipulated in Article 3.4.6.8. when measured at a point 300 mm from the centre line of the handrail at the narrow end of the tread.

4)   All tapered treads within a flight shall turn in the same direction.

3.4.6.10. Horizontal Exits

1)   The floor area on each side of a horizontal exit shall be sufficient to accommodate the occupants of both floor areas, allowing not less than 0.5 m2 of clear floor space per person, except that 1.5 m2 shall be provided for each person in a wheelchair and 2.5 m2 for each bedridden patient.

2)   If vestibules, enclosed balconies or bridges are used as parts of a horizontal exit, their clear width shall be not less than that of the exit doorways opening into them, except that handrails are not permitted to project into this clear width more than 100 mm.

3)   In a horizontal exit where there is a difference in level between the connected floor areas, slopes not more than those specified for ramps in Article 3.4.6.7. are permitted to be used.

4)   No stairs or steps shall be used in a horizontal exit.

5)   If 2 doors are provided in a horizontal exit that comprises a part of the required number of exits from the floor areas on both sides of the exit

a)   the doors shall be mounted adjacent to each other with the door on the right side in the direction of travel through the horizontal exit swinging in the direction of travel through the horizontal exit, and

b)   signs shall be provided on each side of the horizontal exit to indicate the door that swings in the direction of travel from that side.

(See Note A-3.4.6.10.(5).)

6)   If a horizontal exit utilizes bridges between buildings or outside balconies, the bridges or balconies shall conform to Article 3.2.3.19.

3.4.6.11. Doors

(See also Sentence 3.8.3.6.(17).)

1)   The distance between a stair riser and the leading edge of a door during its swing shall be not less than 300 mm.

2)   Except as provided in Sentence (3) and where doorways are used to confine the spillage of flammable liquids within a service room or within a room in an industrial occupancy, a threshold for a doorway in an exit shall be not more than 13 mm higher than the surrounding finished floor surface.

3)   Except for doors providing access to ground level as required by Clauses 3.3.1.7.(1)(d) and (e), an exit door is permitted to open onto not more than one step which shall be not more than 150 mm high where there is a risk of blockage by ice or snow.

4)   Exit doors shall be clearly identifiable. (See Note A-3.4.6.11.(4).)

5)   No door leaf in an exit doorway with more than one leaf shall be less than 610 mm wide.

6)   Where an exit door leading directly to the outside is subject to being obstructed by parked vehicles or storage because of its location, a visible sign or a physical barrier prohibiting such obstructions shall be installed on the exterior side of the door.

3.4.6.12. Direction of Door Swing

1)   Except for doors serving a single dwelling unit and except as permitted by Sentence (2) and Article 3.4.6.14., every exit door shall

a)   open in the direction of exit travel, and

b)   swing on its vertical axis.

2)   Exit doors need not conform to Sentence (1), where

a)   they serve storage garages serving not more than one dwelling unit,

b)   they serve accessory buildings serving not more than one dwelling unit,

c)   they

i)   serve storage suites not more than 28 m2 in area that are on the first storey in warehousing buildings, and

ii)   open directly outdoors at ground level, or

d)   they serve individual self-service storage units referred to in Section 3.9.

3.4.6.13. Self-closing Devices

1)   An exit door that is normally required to be kept closed

a)   shall be provided with a self-closing mechanism, and

b)   shall never be secured in an open position except as permitted by Sentence 3.1.8.14.(1).

3.4.6.14. Sliding Doors

1)   Except as permitted by Sentences (2) and 3.4.6.12.(2), an exit door leading directly to outdoors at ground level is permitted to be a sliding door provided it conforms to Sentence 3.3.1.12.(1).

2)   An exit door serving a Group B, Division 1 occupancy, or an impeded egress zone in other occupancies, is permitted to be a sliding door that does not conform to Sentence 3.3.1.12.(1) provided it is designed to be released in conformance with Article 3.3.1.13.

3.4.6.15. Revolving Doors

1)   Except as permitted by Sentence (3), a revolving door, if used, shall

a)   be collapsible,

b)   have hinged doors providing equivalent exiting capacity located adjacent to it,

c)   be used as an exit from the ground floor level only,

d)   not be used at the foot of any stairway, and

e)   have all glass in door leaves and enclosure panels conforming to

i)   CAN/CGSB-12.1, “Safety Glazing,” or

ii)   CAN/CGSB-12.11-M, “Wired Safety Glass.”

2)   Except as permitted by Sentence (3), a revolving door shall not be considered to have an exiting capacity for more than 45 persons.

3)   An electrically powered revolving door is not required to conform to Sentences (1) and (2) provided

a)   the door leaves will collapse and stop automatic rotation of the door system and not obstruct the doorway if a force not more than that specified in Sentence 3.4.6.16.(2) is applied at the centre of a door leaf,

b)   the door leaves are capable of being opened from inside the building without requiring keys, special devices, or specialized knowledge of the door opening mechanism,

c)   the allowable exiting capacity is based on the clear width of passage through the door enclosure when the doors are fully collapsed,

d)   a permanent sign, whose centre line is between 1 000 mm and 1 500 mm above the floor, is placed on each face of each door leaf indicating the method for collapsing the door leaf in an emergency, and

e)   glass used for door leaves and enclosure panels is safety glazing conforming to

i)   CAN/CGSB-12.1, “Safety Glazing,” or

ii)   CAN/CGSB-12.11-M, “Wired Safety Glass.”

3.4.6.16. Door Release Hardware

1)   Except for devices on doors serving a contained use area or an impeded egress zone designed to be remotely released in conformance with Article 3.3.1.13., and except as permitted by Sentences (5) and (6) and Article 3.4.6.17., locking, latching and other fastening devices on a principal entrance door to a building as well as those on every exit door shall include release hardware complying with Clause 3.8.3.8.(1)(b) to permit the door to be readily opened from the inside with not more than one releasing operation and without requiring keys, special devices or specialized knowledge of the door-opening mechanism. (See Note A-3.4.6.16.(1).)

2)   If a door is equipped with a latching mechanism, a device complying with Sentence (3) shall be installed on

a)   every exit door from a floor area containing an assembly occupancy having an occupant load more than 100,

b)   every door leading to an exit lobby from an exit stair shaft, and every exterior door leading from an exit stair shaft in a building having an occupant load more than 100, and

c)   every exit door from a floor area containing a high-hazard industrial occupancy.

3)   The device required in Sentence (2) shall

a)   extend across not less than one half of the width of the door,

b)   release the latch, and

c)   allow the door to swing wide open when a force not more than that specified in Sentence 3.8.3.6.(8) is applied to the device in the direction of travel to the exit.

4)   Except as required by Sentence 3.8.3.6.(8), every exit door shall be designed and installed so that, when the latch is released, the door will open under a force of not more than 90 N, applied at the knob or other latch releasing device.

5)   Electromagnetic locks that do not incorporate latches, pins or other similar devices to keep the door in the closed position are permitted to be installed on doors, other than those leading directly from a high-hazard industrial occupancy, provided

a)   the building is equipped with a fire alarm system,

b)   the locking device releases upon actuation of the alarm signal from the building's fire alarm system,

c)   the locking device releases immediately upon loss of power controlling the electromagnetic locking mechanism and its associated auxiliary controls,

d)   except for locking devices installed in conformance with Sentence (6), the locking device releases immediately upon actuation of a manually operated switch readily accessible only to authorized personnel,

e)   except as provided in Clause (l), a force of not more than 90 N applied to the door opening hardware initiates an irreversible process that will release the locking device within 15 s and not re-lock until the door has been opened,

f)   upon release, the locking device must be reset manually by the actuation of the switch referred to in Clause (d),

g)   a visual information sign complying with Subsection 3.8.3. is permanently mounted on the door to indicate that the locking device will release within 15 s of applying pressure to the door-opening hardware,

h)   a tactile information sign complying with Subsection 3.8.3. is permanently mounted near the door to indicate that the locking device will release within 15 s of applying pressure to the door-opening hardware,

i)   the total time delay for all electromagnetic locks in any path of egress to release is not more than 15 s,

j)   where a bypass switch is installed to allow testing of the fire alarm system, actuation of the switch

i)   can prevent the release of the locking device by the fire alarm system, as stated in Clause (b), during the test, and

ii)   causes an audible and visible signal to be indicated at the fire alarm annunciator panel required by Article 3.2.4.9. and at the monitoring station specified in Sentence 3.2.4.8.(4),

k)   emergency lighting complying with Sentence 3.2.7.3.(1) is provided, and

l)   where they are installed on doors providing emergency crossover access to floor areas from exit stairs in accordance with Article 3.4.6.18.,

i)   the locking device releases immediately upon the operation of a manual station for the fire alarm system located on the wall on the exit stair side not more than 600 mm from the door,

ii)   a visual information sign displaying the words “Re-entry door unlocked by fire alarm” that complies with Subsection 3.8.3. is permanently mounted on the door on the exit stair side, and

iii)   a tactile information sign displaying the words “Re-entry door unlocked by fire alarm” that complies with Subsection 3.8.3. is permanently mounted near the door on the exit stair side.

(See Note A-3.4.6.16.(5).)

6)   Electromagnetic locks that do not incorporate latches, pins or other similar devices to keep the door in the closed position are permitted to be installed on doors in Group B, Division 2 and Division 3 occupancies, provided

a)   the building is

i)   equipped with a fire alarm system, and

ii)   sprinklered,

b)   the electromagnetic lock releases upon

i)   actuation of the alarm signal from the building's fire alarm system,

ii)   loss of its power supply and of power to its auxiliary controls,

iii)   actuation of a manually operated switch that is readily accessible at a constantly attended location within the locked space, and

iv)   actuation of the manual station installed within 0.5 m of each door and equipped with an auxiliary contact, which directly releases the electromagnetic lock,

c)   upon release, the electromagnetic lock requires manual resetting by actuation of the switch referred to in Subclause (b)(iii),

d)   a visual information sign complying with Subsection 3.8.3. that displays the words “Emergency exit unlocked by fire alarm” is permanently mounted on the door,

e)   a tactile information sign complying with Subsection 3.8.3. that displays the words “Emergency exit unlocked by fire alarm” is permanently mounted near the door,

f)   the operation of any by-pass switch, where provided for testing of the fire alarm system, sets off an audible signal and a visible signal at the fire alarm annunciator panel and at the monitoring station referred to in Sentence 3.2.4.7.(4), and

g)   emergency lighting complying with Sentence 3.2.7.3.(1) is provided.

(See Note A-3.4.6.16.(6).)

7)   Except as provided in Sentence 3.4.6.17.(9), door release hardware for the operation of the doors referred to in this Section shall be installed between 900 mm and 1 100 mm above the finished floor.

3.4.6.17. Security for Banks and Mercantile Floor Areas

1)   If a building is sprinklered throughout, the requirements of Sentence 3.4.6.16.(1) are permitted to be waived for exit and egress doors complying with Sentences (2) to (9) that serve a floor area or part of a floor area used exclusively for

a)   a bank, or

b)   the sale of retail merchandise.

(See Note A-3.4.6.17.(1).)

2)    Exit and egress doors referred to in Sentence (1) shall be designed to prevent locking at any time that the part of the floor area that they serve is open to the public.

3)   A sign with the words “This door shall not be locked at any time that the public is present” in letters not less than 50 mm high shall be permanently affixed to both sides of doors referred to in Sentence (1).

4)   Exit and egress facilities complying with Sentences (5) to (9) shall be incorporated for egress by persons other than the public from a floor area or a part of a floor area referred to in Sentence (1) during times when the public is neither present nor being admitted to the area that they serve.

5)   In exit and egress facilities referred to in Sentence (4), at least one door at each exit and egress location shall

a)   be operable in conformance with Sentence 3.4.6.16.(1), or

b)   be equipped with locks conforming to Sentence 3.4.6.16.(5) that release immediately

i)   if an alert signal or alarm signal is initiated in the fire alarm system, or

ii)   the sprinkler system is actuated.

6)   A door referred to in Sentence (5) shall be permanently and distinctly marked to indicate that it is an emergency exit.

7)   Exit and egress facilities required for evacuation of persons other than the public from a floor area or a part of a floor area referred to in Sentence (1) shall have an aggregate width based on the maximum number of persons other than the public and determined in accordance with Articles 3.4.3.1. to 3.4.3.3.

8)    Travel distance to an exit referred to in Sentence (7) shall not exceed the travel distance determined in accordance with Subsection 3.4.2.

9)   Exit and egress doors serving a floor area or part of a floor area referred to in Sentence (1) are permitted to be equipped with locks that require keys, special devices or specialized knowledge of the door opening mechanism, provided

a)   the doors do not lead into exit stairs,

b)   the doors do not lead from exit stairs to the exterior of the building,

c)   the doors do not serve any other occupancy,

d)   the area served contains at least one telephone

i)   that is accessible and in operation at all times,

ii)   that is not coin or card operated, and

iii)   marked to indicate that it is for emergency use,

e)   the area served is illuminated by normal power or by emergency power when the doors are locked,

f)   there are provisions that enable an announcement to be made throughout the area served before the locks are fastened, and

g)   the locks are designed for use during times that the building is not occupied.

3.4.6.18. Emergency Crossover Access to Floor Areas

1)   Except as permitted in Sentence (2), doors providing access to floor areas from exit stairs shall not have locking devices to prevent entry into any floor area from which the travel distance up or down to an unlocked door is more than 2 storeys.

2)   Doors referred to in Sentence (1) are permitted to be equipped with electromagnetic locks, provided they comply with Sentences 3.4.6.16.(5) and (6).

3)   Doors referred to in Sentence (1) shall be identified by visual and tactile information signs complying with Subsection 3.8.3. mounted on the stairway side to indicate that they are openable from that side.

4)   Locked doors intended to prevent entry into a floor area from an exit stair shall

a)   be identified by visual and tactile information signs complying with Subsection 3.8.3. mounted on the stairway side to indicate the location of the nearest unlocked door in each direction of travel, and

b)   be openable with a master key that fits all locking devices and is kept in a designated location accessible to firefighters or be provided with a wired glass panel not less than 0.0645 m2 in area and located not more than 300 mm from the door opening hardware.

5)   Where access to floor areas through unlocked doors is required by Sentence (1), it shall be possible for a person entering the floor area to have access through unlocked doors within the floor area to at least one other exit.

3.4.6.19. Floor Numbering and Identification of Stair Shafts

1)   Arabic numerals indicating the assigned floor number in both visual and tactile forms in accordance with Subsection 3.8.3. shall be mounted permanently on the wall on the stair side and on the floor side at the latch side of doors to exit stair shafts.

2)   Upper case letters indicating the designation assigned to each exit stair shaft in both visual and tactile forms in accordance with Subsection 3.8.3. shall be mounted permanently on the wall on the stair side and on the floor side at the latch side of doors to exit stair shafts.

3.4.7. Fire Escapes

3.4.7.1. Scope

1)   Except as permitted by Sentence (2), fire escapes shall not be erected on a building.

2)   If it is impracticable to provide one or more of the exit facilities listed in Article 3.4.1.4., fire escapes conforming to Articles 3.4.7.2. to 3.4.7.7. are permitted to serve floor areas in an existing building provided the floor areas served are not more than

a)   2 storeys above ground level in care, treatment or detention occupancies, and

b)   5 storeys above ground level in other occupancies.

3.4.7.2. Fire Escape Construction

1)   Fire escapes shall be of metal or concrete, of the stair type extending to ground level, constructed throughout in a strong substantial manner and securely fixed to the building, except that wooden fire escapes are permitted to be used on buildings of combustible construction if all posts and brackets are not less than 89 mm in their least dimension and all other woodwork is not less than 38 mm in its least dimension.

3.4.7.3. Access to Fire Escapes

1)   Access to fire escapes shall be from corridors through doors at floor level, except that access from a dwelling unit is permitted to be through a casement window having an unobstructed opening not less than 1 100 mm high by 550 mm wide with a sill height of not more than 900 mm above the inside floor.

2)   The clear area of a fire escape balcony onto which a door opens, shall be not less than 1 m2.

3.4.7.4. Protection of Fire Escapes

1)   If a fire escape serves any storey above the second, openings located in a zone described in Sentence (2), including access doorways in the exterior walls of the building to which the fire escape is attached, shall be protected by closures conforming to Subsection 3.1.8.

2)   The zone referred to in Sentence (1) extends from any balcony, platform or stairway of a fire escape to a distance

a)   3 m horizontally,

b)   10 m below, or

c)   1.8 m above.

3.4.7.5. Stairs

1)   Stairs shall be inclined at an angle of not more than 45° with the horizontal, and their steps shall have risers not more than 210 mm high and treads not less than 220 mm wide exclusive of nosing.

2)   Stairway headroom shall be not less than 1 950 mm plus the height of one riser measured vertically above the nosing of any tread or platform.

3)   The width of a fire escape shall conform to Articles 3.4.3.1. to 3.4.3.3., except that the width is permitted to be reduced to 550 mm provided the fire escape serves

a)   not more than 3 storeys, and

b)   not more than 15 persons.

4)   If a flight of stairs leading to the ground at the foot of a fire escape is not fixed in position, it shall be held in the raised position without a latch or locking device, and shall be fitted with a counterbalancing device that will permit it to be easily and quickly brought into position for use.

3.4.7.6. Guards and Railings

1)   The open sides of every platform, balcony and stairway forming part of a fire escape shall be protected by guards not less than 920 mm high measured vertically above the nosing of any tread or platform.

2)   The top rail of a guard is permitted to serve as a handrail if it is free from obstructions which could break a handhold.

3)   A wall handrail shall be installed if the fire escape is more than 550 mm wide.

4)   Unless it can be shown that the size of openings that exceed this limit does not present a hazard, there shall be no opening that permits the passage of a sphere whose diameter is more than 100 mm through a guard for a fire escape.

5)   Unless it can be shown that the location and size of an opening do not present a hazard, a guard for a fire escape shall be designed so that no member, attachment or opening located between 140 mm and 900 mm above a platform or the nosing of any tread will facilitate climbing.

3.4.7.7. Landings

1)   Platforms for a fire escape shall be provided in conformance with the requirements for stair landings in Articles 3.4.6.3. and 3.4.6.4.

Section  3.5.   Vertical Transportation

3.5.1. General

3.5.1.1. Scope

1)   This Section applies to vertical transportation facilities installed in a building, including elevators, escalators and dumbwaiters.

2)   Elevators in a building within the scope of Subsection 3.2.6. shall conform to Articles 3.2.6.4., 3.2.6.5. and 3.2.6.6.

3.5.2. Standards

3.5.2.1. Elevators, Escalators and Dumbwaiters

1)   The design, construction, installation and alteration of every elevator, escalator and dumbwaiter shall conform to the Safety Standards Act and pursuant regulations.

(See Note A-3.5.2.1.(1).)

2)   Before being placed in service, every elevator, escalator or dumbwaiter installation, including safety and control devices, shall be inspected and tested in accordance with the Safety Standards Act and pursuant regulations.

(See Note A-3.5.2.1.(1).)

3)   Passenger elevators shall conform to Appendix E of ASME A17.1/CSA B44, “Safety Code for Elevators and Escalators.”

3.5.3. Fire Separations

3.5.3.1. Fire Separations for Elevator Hoistways

1)   Except as permitted by Sentence (2), a vertical service space used as an elevator hoistway shall be separated from all other portions of each adjacent storey by a fire separation having a fire-resistance rating conforming to Table 3.5.3.1. for the fire-resistance rating required by Subsection 3.2.2. for

a)   the floor assembly above the storey, or

b)   the floor assembly below the storey, if there is no floor assembly above.

Table 3.5.3.1.

Fire Separation for Vertical Transportation Space

Forming Part of Articles 3.5.3.1. and 3.5.3.2.

| Fire-Resistance Rating of Fire Separation Required for Floor Assembly | Minimum Fire-Resistance Rating of Vertical Service Space for Elevator Hoistway | Minimum Fire-Resistance Rating of Vertical Service Space for Dumbwaiters |
| --- | --- | --- |
| less than 45 min | 45 min | — |
| 45 min | 45 min | 45 min |
| 1 h | 1 h | 45 min |
| 1.5 h | 1.5 h | 1 h |
| 2 h or more | 2 h | 1 h |

2)   Passenger elevators, other than those provided for firefighters in accordance with Article 3.2.6.5., are permitted to be located within interconnected floor space without being enclosed in a hoistway separated from the remainder of the building, provided the elevator machinery is located in a room separated from the remainder of the building by a fire separation having a fire-resistance rating not less than that required for hoistways by Sentence (1).

3.5.3.2. Vertical Service Spaces for Dumbwaiters

1)   A vertical service space containing a dumbwaiter shall be separated from all other portions of each adjacent storey by a fire separation having a fire-resistance rating conforming to Table 3.5.3.1. for the fire-resistance rating required by Subsection 3.2.2. for

a)   the floor assembly above the storey or

b)   the floor assembly below the storey, if there is no floor assembly above.

3.5.3.3. Fire Separations for Elevator Machine Rooms

1)   Except as permitted by Sentence (2), a room containing elevator machinery shall be separated from all other parts of the building by a fire separation having a fire-resistance rating not less than that required for the vertical service space containing the elevator hoistway.

2)   A room containing elevator machinery need not be separated from the elevator hoistway that it serves provided the room and the hoistway are separated from all other parts of the building by a fire separation having a fire-resistance rating not less than that required for the vertical service space containing the elevator hoistway.

3.5.4. Dimensions and Signs

3.5.4.1. Elevator Car Dimensions

1)   Except as provided in Sentence (2), if one or more elevators are provided in a building, at least one elevator on each storey with access to an elevator shall have inside dimensions that will accommodate and provide adequate access for a patient stretcher 2 010 mm long and 610 mm wide in the prone position. (See Note A-3.5.4.1.(1).)

2)   The inside dimensions stipulated in Sentence (1) do not apply to limited-use/limited-application elevators designed and installed in accordance with ASME A17.1/CSA B44, “Safety Code for Elevators and Escalators.”

3)   An elevator satisfying the requirements of Sentence (1) shall be clearly identified on the main entrance level of the building.

3.5.4.2. Floor Numbering

1)   Arabic numerals indicating the assigned floor number shall be mounted permanently on both jambs of passenger elevator hoistway entrances in conformance with Appendix E of ASME A17.1/CSA B44, “Safety Code for Elevators and Escalators.”

Section  3.6.   Service Facilities

3.6.1. General

3.6.1.1. Scope

1)   The provisions of this Section apply to horizontal service spaces, vertical service spaces, attic or roof spaces, ducts, crawl spaces, shaft spaces, service rooms, and mechanical penthouses, and facilities contained therein.

3.6.1.2. Electrical Wiring and Equipment

1)   The installation of electrical wiring and electrical equipment shall conform to the requirements of the Safety Standards Act and pursuant regulations.

3.6.1.3. Lightning Protection Systems

1)   A lightning protection system, when provided, shall conform to the requirements of  CAN/CSA-B72-M, “Installation Code for Lightning Protection Systems.”

3.6.1.4. Storage Use Prohibition

1)   Service spaces shall not be designed to facilitate subsequent use as storage space.

3.6.1.5. Appliances Installed outside a Building

1)   A fuel-fired appliance installed on the roof of a building or in another location outside the building shall be installed not less than

a)   1.2 m from a property line, measured horizontally, and

b)   3 m from an adjacent wall of the same building if that wall contains any opening within 3 storeys above and 5 m horizontally from the appliance, unless every opening within these limits is protected by

i)   a closure having a fire-protection rating not less than 45 min determined in accordance with Article 3.1.8.4., or

ii)   a wired glass assembly permitted for use in a vertical fire separation and described in Article D-2.3.15. of Appendix D.

3.6.2. Service Rooms

3.6.2.1. Fire Separations around Service Rooms

1)   Except as permitted by Sentences (2), (8), (9) and (10), fuel-fired appliances shall be installed in service rooms separated from the remainder of the building by fire separations having a fire-resistance rating not less than 1 h.

2)   Except as required by Sentence (3), a fuel-fired appliance that serves only one room or suite is not required to be installed in a service room separated from the remainder of the building.

3)   A solid-fuel-burning appliance shall not be located in a repair garage, a storage garage, or any other location where it could be exposed to flammable vapours or gases, unless

a)   it is enclosed in a service room that is separated from the remainder of the building by a fire separation having a fire-resistance rating not less than 1 h,

b)   it is supplied with combustion air directly from outside the building, and

c)   the heat that it generates is supplied indirectly to the space served by means of ducts or piping.

4)   A service room containing an incinerator shall be separated from the remainder of the building by a fire separation having a fire-resistance rating not less than 2 h.

5)   Equipment that uses a liquid having a flash point below 93.3°C shall be installed in a service room separated from the remainder of the building by a fire separation having a fire-resistance rating not less than 1 h.

6)   Electrical equipment that is required to be located in a service room according to the Safety Standards Act and pursuant regulations shall be installed in a service room separated from the remainder of the building by a fire separation having a fire-resistance rating not less than 1 h.

7)   Except as permitted by Sentence (8), in a storey that is not sprinklered throughout, a service room that contains service equipment other than that addressed by Sentences (1) to (6) shall be separated from the remainder of the building by a fire separation having a fire-resistance rating not less than 1 h.

8)   Where a service room contains a limited quantity of service equipment, and the service equipment neither constitutes a fire hazard nor is essential to the operation of fire safety systems in the building, the requirements for a fire separation shall not apply.

9)   A fire separation is not required between a fireplace and the space it serves.

10)   A fire separation is not required between a rooftop appliance and the building it serves.

3.6.2.2. Service Rooms under Exits

1)   A service room containing service equipment subject to possible explosion, such as boilers operating in excess of 100 kPa (gauge) and some types of refrigerating machinery and transformers, shall not be located directly under a required exit.

3.6.2.3. Service Equipment

1)   A service room containing space heating, space cooling and service water heating appliances is permitted to contain other service equipment such as electrical service equipment.

3.6.2.4. Incinerator Rooms

1)   A service room containing an incinerator shall not contain other fuel-fired appliances.

3.6.2.5. Storage of Combustible Refuse and Recycling

1)   Except as required by Sentence 3.6.3.3.(9), a room for the temporary storage of combustible refuse and materials for recycling shall be

a)   separated from the remainder of the building by a fire separation with a fire-resistance rating not less than 1 h, except that a fire separation with a fire-resistance rating not less than 45 min is permitted where the fire-resistance rating of the floor assembly is not required to exceed 45 min, and

b)   sprinklered.

(See Note A-3.6.2.5.(1).)

3.6.2.6. Door Swing for Service Rooms

1)   A swing-type door from a service room containing a boiler or incinerator shall swing outward from the room, except that the door shall swing inward if the door opens onto a corridor or any room used for an assembly occupancy. (See also Sentence 3.4.4.4.(7).)

3.6.2.7. Electrical Equipment Vaults

1)   An electrical equipment vault required by the Safety Standards Act and pursuant regulations shall conform to Sentences (2) to (8).

2)   An electrical equipment vault referred to in Sentence (1) shall be separated from the remainder of the building by a fire separation of solid masonry or concrete construction having a fire-resistance rating not less than

a)   3 h if the vault is not protected by an automatic fire extinguishing system, or

b)   2 h if the vault is protected by an automatic fire extinguishing system.

3)   If a building is sprinklered throughout, an electrical equipment vault referred to in Sentence (1) need not be sprinklered provided

a)   the vault is designed for no purpose other than to contain the electrical equipment, and

b)   the vault contains a smoke detector which will actuate the building fire alarm system in the event of a fire in the vault.

4)   Only pipes or ducts necessary for fire protection or the proper operation of the electrical installation shall penetrate the fire separation referred to in Sentence (2).

5)   Explosion-relief devices and vents or other protective measures conforming to Sentence 3.3.1.21.(3) shall be provided for an electrical equipment vault referred to in Sentence (1) that contains dielectric-liquid-filled electrical equipment. (See Note A-3.6.2.7.(5).)

6)   An electrical equipment vault referred to in Sentence (1) shall be provided with a ventilation system designed in conformance with Part 6 to prevent the ambient temperature in the vault from exceeding 40°C.

7)   The ventilation system required by Sentence (6) shall be separate from the system for the remainder of the building and shall be designed so that it is automatically shut off in the event of a fire in the vault.

8)   The floor of an electrical equipment vault referred to in Sentence (1) shall be liquid tight and surrounded by liquid tight walls and sills of sufficient height to confine within the vault all of the liquid from the largest item of electrical equipment, but to a height of not less than 100 mm.

9)   Electrical equipment vaults shall be secured against unauthorized entry.

3.6.2.8. Emergency Power Installations

1)   Where a generator intended to supply emergency power for lighting, fire safety and life safety systems is located in a building, except where such building is used solely for the purpose of housing the generator and its ancillary equipment, it shall be located in a room that

a)   is separated from the remainder of the building by a fire separation having a fire-resistance rating not less than 2 h, and

b)   contains only the generating set and equipment related to the emergency power supply system.

3.6.3. Vertical Service Spaces and Service Facilities

3.6.3.1. Fire Separations for Vertical Service Spaces

1)   Except as provided in Articles 3.6.3.3. and 3.6.3.5. and Section 3.5., a vertical service space shall be separated from all other portions of each adjacent storey by a fire separation having a fire-resistance rating conforming to Table 3.6.3.1. for the fire-resistance rating required by Subsection 3.2.2. for

a)   the floor assembly above the storey, or

b)   the floor assembly below the storey, if there is no floor assembly above.

(See Note A-3.6.3.1.(1).)

Table 3.6.3.1.

Fire Separations for Vertical Service Spaces

Forming Part of Sentence 3.6.3.1.(1)

| Fire-Resistance Rating of Fire Separation Required for Floor Assembly | Minimum Fire-Resistance Rating of Vertical Service Space |
| --- | --- |
| less than 45 min | — |
| 45 min | 45 min |
| 1 h | 45 min |
| 1.5 h | 1 h |
| 2 h or more | 1 h |

2)   A vertical service space that does not extend through the roof of a building shall be enclosed at the top with construction having a fire-resistance rating not less than that required for the vertical service space walls.

3)   A vertical service space that does not extend to the bottom of a building shall be enclosed at the lowest level with construction having a fire-resistance rating not less than that required for the vertical service space walls.

4)   A vent from a vertical service space not extending to the roof shall be enclosed within the building with construction having a fire-resistance rating not less than that required for the vertical service space walls.

5)   Only openings that are necessary for the use of the vertical service space shall be permitted through a vertical service space enclosure.

3.6.3.2. Foamed Plastic Protection

1)   Foamed plastic insulation in a vertical service space shall be protected in conformance with Article 3.1.5.15.

3.6.3.3. Linen and Refuse Chutes

1)   A linen chute or refuse chute shall

a)   be impervious to moisture,

b)   have a smooth internal surface,

c)   be corrosion-resistant,

d)   be constructed of noncombustible material, and

e)   be located in a shaft in which there are no services other than noncombustible drain, waste and vent piping or noncombustible water piping.

2)   A shaft containing a linen chute or refuse chute shall have a fire-resistance rating conforming to Sentence 3.6.3.1.(1), but not less than

a)   1 h if the chute outlet for the discharge room is protected by an automatic, self-latching closure held open by a fusible link, or

b)   2 h if no closure is provided at the chute outlet into the discharge room.

3)   An interior linen chute or refuse chute shall extend not less than 1 m above the roof and shall be vented above the roof with a vent which

a)   has an unobstructed area not less than the cross-sectional area of the chute, and

b)   is equipped with a cover that will open automatically, or that can be opened manually, in the event of a fire in the chute.

4)   Intake openings for a linen chute or a refuse chute shall

a)   have an area not more than 60% of the cross-sectional area of the chute, and

b)   be fitted with closures designed to close automatically and latch after use.

5)   Intake openings for a linen chute or a refuse chute shall be located in rooms or compartments that

a)   have no dimension less than 750 mm,

b)   are separated from the remainder of the building by a fire separation with a fire-resistance rating not less than 45 min,

c)   are designed for no other purpose, and

d)   do not open directly into an exit.

6)   Sprinklers shall be installed at the top of each linen chute or refuse chute, at alternate floor levels and in the room or bin into which the chute discharges.

7)   The room into which a linen chute discharges shall be separated from the remainder of the building by a fire separation with a fire-resistance rating not less than 1 h.

8)   A refuse chute shall be equipped at the top with spray equipment for washing-down purposes.

9)   A refuse chute shall discharge only into a room or bin separated from the remainder of the building by a fire separation with a fire-resistance rating not less than 2 h.

10)   The room or bin into which a refuse chute discharges shall be of sufficient size to contain the refuse between normal intervals of emptying, be impervious to moisture and be equipped with a water connection and floor drain for washing-down purposes.

11)   A room into which a refuse chute discharges shall contain no service equipment that is not related to refuse handling and disposal.

3.6.3.4. Exhaust Duct Negative Pressure

1)    If a vertical service space contains an exhaust duct that serves more than one fire compartment,

a)   the duct shall have a fan located at or near the exhaust outlet to ensure that the duct is under negative pressure, and

b)   the individual fire compartments shall not have individual fans that exhaust directly into the duct in the vertical service space.

3.6.3.5. Grease Duct Enclosures

(See Note A-3.6.3.5.)

1)   Except as provided in Sentence (2), fire separations enclosing grease ducts for commercial cooking operations shall conform to NFPA 96, “Standard for Ventilation Control and Fire Protection of Commercial Cooking Operations.”

2)   The fire-resistance rating of field-applied and factory-built grease duct enclosure assemblies shall be determined in conformance with CAN/ULC-S144, “Standard Method of Fire Resistance Test – Grease Duct Assemblies.”

3.6.4. Horizontal Service Spaces and Service Facilities

3.6.4.1. Scope

1)   This Subsection applies to horizontal service spaces and service facilities, including ceiling spaces, duct spaces, crawl spaces and attic or roof spaces.

3.6.4.2. Fire Separations for Horizontal Service Spaces

1)   Except as provided in Article 3.6.3.5., a horizontal service space that penetrates a required vertical fire separation shall be separated from the remainder of the building it serves in conformance with Sentence (2).

2)   If a horizontal service space or other concealed space is located above a required vertical fire separation other than a vertical shaft, this space need not be divided at the fire separation as required by Article 3.1.8.3. provided the construction between this space and the space below is a fire separation with a fire-resistance rating equivalent to that required for the vertical fire separation, except that the fire-resistance rating is permitted to be not less than 30 min if the vertical fire separation is not required to have a fire-resistance rating more than 45 min. (See Note A-3.6.4.2.(2).)

3.6.4.3. Plenum Requirements

1)   A concealed space used as a plenum within a floor assembly or within a roof assembly need not conform to Sentence 3.1.5.18.(1) and Article 3.6.5.1., provided

a)   all materials within the concealed space have a flame-spread rating not more than 25 and a smoke developed classification not more than 50, except for

i)   tubing for pneumatic controls,

ii)   optical fibre cables and electrical wires and cables with combustible insulation, jackets or sheathes that are used for the transmission of voice, sound or data and conform to Sentences 3.1.4.3.(2) and 3.1.5.21.(2),

iii)   totally enclosed non-metallic raceways with an FT6 rating, when tested in accordance with Clause 3.1.5.23.(1)(a), in buildings required to be of noncombustible construction or in buildings or parts of buildings permitted to be of encapsulated mass timber construction, and

iv)   totally enclosed non-metallic raceways with an FT4 rating, when tested in accordance with Clause 3.1.5.23.(1)(a), in buildings permitted to be of combustible construction, and

b)   the supports for the ceiling membrane are of noncombustible material having a melting point not below 760°C.

2)   If a concealed space referred to in Sentence (1) is used as a return-air plenum and incorporates a ceiling membrane that forms part of the required fire-resistance rating of the assembly, every opening through the membrane shall be protected by a fire stop flap that

a)   stops the flow of air into the concealed space in the event of a fire,

b)   is supported in a manner that will maintain the integrity of the ceiling membrane for the duration of time required to provide the required fire-resistance rating,

c)   conforms to CAN/ULC-S112.2, “Standard Method of Fire Test of Ceiling Firestop Flap Assemblies,” and

d)   activates at a temperature approximately 30°C above the normal maximum temperature that occurs in the return-air plenum, whether the air duct system is operating or shut down.

3.6.4.4. Attic or Roof Space Access

1)   An attic or roof space more than 600 mm high shall be provided with access from the floor immediately below by a hatchway not less than 550 mm by 900 mm or by a stairway.

3.6.4.5. Horizontal Service Space Access

1)   A horizontal service space, consisting of ceiling and duct spaces, which is more than 1 200 mm high and 600 mm wide shall have inspection doors not less than 300 mm in both horizontal and vertical dimensions placed so that the entire interior of the duct or space can be viewed.

3.6.4.6. Crawl Space Access

1)   A crawl space shall have at least one access opening not less than 550 mm by 900 mm.

3.6.5. Air Duct and Plenum Systems

3.6.5.1. Duct Materials

1)   Except as permitted by Sentences (2) to (5) and Article 3.6.4.3., all ducts, duct connectors, associated fittings and plenums used in air duct systems shall be constructed of steel, aluminum alloy, copper, clay or other noncombustible material.

2)   Except as permitted by Sentence (3), ducts, associated fittings and plenums are permitted to contain combustible material provided they

a)   conform to the appropriate requirements for Class 1 duct materials in CAN/ULC-S110, “Standard Methods of Test for Air Ducts,”

b)   conform to Article 3.1.5.18. in a building required to be of noncombustible construction or in a building or part of a building permitted to be of encapsulated mass timber construction,

c)   conform to Subsection 3.1.9.,

d)   are used only in horizontal runs in a building required to be of noncombustible construction or in a building or part of a building permitted to be of encapsulated mass timber construction,

e)   are not used in vertical runs serving more than 2 storeys in a building permitted to be of combustible construction, and

f)   are not used in air duct systems in which the air temperature could be more than 120°C.

3)   Combustible ducts which are part of a duct system conveying only ventilation air and are contained entirely within a dwelling unit need not comply with the requirements of Sentences (1) and (2).

4)   Duct sealants shall have a flame-spread rating not more than 25 and a smoke developed classification not more than 50.

5)   Duct connectors that contain combustible materials and that are used between ducts and air outlet units shall

a)   conform to the appropriate requirements for Class 1 air duct materials in CAN/ULC-S110, “Standard Methods of Test for Air Ducts,”

b)   be not more than 4 m long,

c)   be used only in horizontal runs, and

d)   not penetrate a required fire separation.

3.6.5.2. Vibration Isolation Connectors

1)   Except as permitted by Sentence (2), vibration isolation connectors in air duct systems shall be noncombustible.

2)   Combustible fabric vibration isolation connectors are permitted provided they

a)   are not more than 250 mm long,

b)   comply with the flame-resistance requirements of CAN/ULC-S109, “Standard Method for Flame Tests of Flame-Resistant Fabrics and Films,” and

c)   are not used in a location where they are exposed to heated air or radiation from heat sources that could cause the exposed surface temperature to be more than 120°C.

3.6.5.3. Tape

1)   Tape used to seal joints in air ducts, plenums and other parts of air duct systems shall meet the flame-resistance requirements for fabric in CAN/ULC-S109, “Standard Method for Flame Tests of Flame-Resistant Fabrics and Films.”

3.6.5.4. Coverings, Linings, Adhesives and Insulation

1)   Coverings, linings and associated adhesives and insulation for air ducts, plenums and other parts of air duct systems that would have an exposed surface temperature more than 120°C when exposed to heated air or radiation from heat sources shall be of noncombustible material.

2)   Except as permitted by Sentence (3), combustible coverings and linings, including associated adhesives and insulation, shall have

a)   a flame-spread rating not more than 25 on any exposed surface, or any surface that would be exposed by cutting through the material in any direction, and

b)   a smoke developed classification not more than 50.

3)   The outer covering of ducts, plenums and other parts of air duct systems used within an assembly of combustible construction is permitted to have

a)   an exposed surface flame-spread rating not more than 75, and

b)   a smoke developed classification not more than 50.

4)   Combustible coverings and linings referred to in Sentences (2) and (3) shall not flame, glow, smoulder or smoke when tested in accordance with the method of test in ASTM C411, “Standard Specification for Hot-Surface Performance of High-Temperature Thermal Insulation,” at the maximum temperature to which the coverings and linings are to be exposed in service.

5)   Except as permitted by Sentence (6), foamed plastic insulation shall not be used as part of an air duct system or for insulating an air duct.

6)   Foamed plastic insulation is permitted to be installed in a ceiling space that is used as a return air plenum provided the foamed plastic insulation is protected from exposure to the plenum in accordance with Article 3.1.5.15.

7)   Combustible coverings and linings of ducts, including associated adhesives and insulation, shall be interrupted where the duct penetrates a fire separation and at the immediate area of operation of heat sources in a duct system, including electric resistance heaters or fuel-burning heaters or furnaces.

3.6.5.5. Insulation and Coverings

1)   Insulation and coverings on pipes in which the temperature of the fluid exceeds 120°C shall

a)   be made of noncombustible material, or

b)   not flame, glow, smoulder or smoke when tested in accordance with ASTM C411, “Standard Specification for Hot-Surface Performance of High-Temperature Thermal Insulation,” at the maximum temperature to which the insulation or covering is to be exposed in service.

2)   Except as permitted by Sentence (5), where combustible insulation is used on piping in a horizontal service space or a vertical service space, the insulation and coverings on that piping shall have a flame-spread rating, on any exposed surface and on any surface that would be exposed by cutting through the material in any direction,

a)   not more than 25 in a building required to be of noncombustible construction or in a building or part of a building permitted to be of encapsulated mass timber construction, or

b)   not more than 75 in a building permitted to be of combustible construction.

3)   Except as permitted by Sentence (5), insulation and coverings on piping located in rooms and spaces other than the service spaces described in Sentence (2) shall have a flame-spread rating not more than that required for the interior finish of the ceiling of the room or space.

4)   Except as permitted by Sentence (5), combustible insulation and covering used on piping in a building within the scope of Subsection 3.2.6. shall have a smoke developed classification not more than 100.

5)   No flame-spread rating or smoke developed classification limits are required for combustible insulation and coverings used on piping located within a

a)   concealed space in a wall,

b)   floor slab, or

c)   noncombustible enclosure.

3.6.5.6. Clearance of Ducts and Plenums

1)   The clearance of furnace plenums from combustible material shall conform to the requirements of the appropriate standards referenced in Sentence 6.2.1.5.(1).

2)   If the plenum clearance required in accordance with Sentence (1) is not more than 75 mm, the clearance between a supply duct and combustible material shall be not less than

a)   the required plenum clearance within a horizontal distance of 450 mm from the plenum, and

b)   12 mm at a horizontal distance of 450 mm or more from the plenum, except that this clearance is permitted to be reduced to zero beyond a bend or offset in the duct sufficiently large to shield the remainder of the supply duct from direct radiation from the furnace heat exchanger.

(See Note A-3.6.5.6.(2).)

3)   If the plenum clearance required in accordance with Sentence (1) is more than 75 mm but not more than 150 mm, the clearance between a supply duct and combustible material shall be not less than

a)   the required plenum clearance within a horizontal distance of 1 800 mm from the plenum, and

b)   12 mm at a horizontal distance of 1 800 mm or more from the plenum, except that this distance is permitted to be reduced to zero beyond a bend or offset in the duct sufficiently large to shield the remainder of the supply duct from direct radiation from the furnace heat exchanger.

(See Note A-3.6.5.6.(3).)

4)   If the plenum clearance required in accordance with Sentence (1) is more than 150 mm, the clearance between a supply duct and combustible material shall be not less than

a)   the required plenum clearance within a horizontal distance of 1 000 mm from the plenum,

b)   150 mm within a horizontal distance between 1 000 mm and 1 800 mm from the plenum, and

c)   25 mm at a horizontal distance of 1 800 mm or more from the plenum, except that this distance is permitted to be reduced to 8 mm beyond a bend or offset in the duct sufficiently large to shield the remainder of the supply duct from direct radiation from the furnace heat exchanger.

(See Note A-3.6.5.6.(4).)

5)   If a register is installed in a floor directly over a pipeless furnace, a double-walled register box with not less than 100 mm between walls, or a register box with the warm-air passage completely surrounded by the cold-air passage, shall be permitted instead of the clearances listed in Sentences (2) to (4).

3.6.5.7. Supply, Return, Intake and Exhaust-Air Openings

1)   Combustible grilles, diffusers and other devices for supply, return, and exhaust-air openings in rooms shall conform to the flame-spread rating and smoke developed classification requirements for the interior finish of the surface on which they are installed.

3.6.5.8. Return-Air System

1)   Except as required by Sentences (2) and (3), return ducts shall be constructed of material having a flame-spread rating not more than 150.

2)   If any part of a return duct will be exposed to radiation from the furnace heat exchanger or other radiating part within the furnace, that part of a return duct directly above or within 600 mm of the outside furnace casing shall be noncombustible.

3)   Return ducts serving solid-fuel-burning furnaces shall be constructed of noncombustible material.

4)   Combustible return ducts shall be lined with noncombustible material

a)   below floor registers,

b)   at the bottom of vertical ducts, and

c)   under furnaces having a bottom return.

Section  3.7.   Health Requirements

3.7.1. Height of Rooms

3.7.1.1. Room and Space Height

1)   The height of every room and space shall be sufficient so that the ceiling or ceiling fixtures do not obstruct movement or activities below.

2)   The unobstructed height in dwelling units shall conform to Subsection 9.5.3.

3.7.2. Plumbing Facilities

3.7.2.1. Plumbing and Drainage Systems

1)   Except as provided in Sentence (2), for the purpose of this Subsection, the occupant load shall be determined in accordance with Subsection 3.1.17.

2)   For the purpose of this Subsection, the occupant load for floor areas that are classified as an industrial occupancy is permitted to be based solely on the total number of staff for which the floor area is designed, where the floor area is only intermittently occupied or where the presence of occupants is transitory. (See Note A-3.7.2.1.(2).)

3)   Except as permitted in Sentence (4), if the installation of a sanitary drainage system is not possible because of the absence of a water supply, sanitary privies, chemical closets or other means for the disposal of human waste shall be provided.

4)   Waterless urinals are permitted to be used in buildings provided with a water supply.

3.7.2.2. Water Closets

1)   Except as permitted by Sentence (2), water closets shall be provided for each sex assuming that the occupant load is equally divided between males and females, unless the proportion of each sex expected in the building can be determined with reasonable accuracy.

2)   Both sexes are permitted to be served by a single water closet if the occupant load in an occupancy referred to in Sentence (4), (8), (10), (11), (12) or (14) is not more than 10.

3)   Urinals are permitted to be substituted for two thirds of the number of water closets required by this Article for males, except that if only 2 water closets are required for males, one urinal is permitted to be substituted for one of the water closets.

4)   Except as permitted by Sentences (2), (5) and (6), the number of water closets required for assembly occupancies shall conform to Table 3.7.2.2.-A.

Table 3.7.2.2.-A

Water Closets for an Assembly Occupancy

Forming Part of Sentence 3.7.2.2.(4)

| Number of Persons of Each Sex | Minimum Number of Water Closets |  |
| --- | --- | --- |
|  | Male | Female |
| 1 - 25 | 1 | 1 |
| 26 - 50 | 1 | 2 |
| 51 - 75 | 2 | 3 |
| 76 - 100 | 2 | 4 |
| 101 - 125 | 3 | 5 |
| 126 - 150 | 3 | 6 |
| 151 - 175 | 4 | 7 |
| 176 - 200 | 4 | 8 |
| 201 - 250 | 5 | 9 |
| 251 - 300 | 5 | 10 |
| 301 - 350 | 6 | 11 |
| 351 - 400 | 6 | 12 |
| Over 400 | 7, plus 1 for each additional increment of 200 males in excess of 400 | 13, plus 1 for each additional increment of 100 females in excess of 400 |

5)   The number of water closets required for primary schools and daycare facilities, including daycare facilities for children shall be at least one for each 30 males and one for each 25 females.

6)   The number of water closets required for places of worship and undertaking premises shall be at least one for each 150 persons of each sex.

7)   The number of water closets required for a treatment or detention occupancy shall be determined on the basis of the special needs of the occupancy.

8)   Except as permitted by Sentences (2) and (5), the number of water closets required for a care or residential occupancy shall be at least one for each 10 persons of each sex.

9)   At least one water closet shall be provided for each dwelling unit.

10)   Except as permitted by Sentence (2), the number of water closets required for a business and personal services occupancy shall conform to Table 3.7.2.2.-B.

Table 3.7.2.2.-B

Water Closets for a Business and Personal Services Occupancy

Forming Part of Sentences 3.7.2.2.(10) and (14)

| Number of Persons of Each Sex | Minimum Number of Water Closets for Each Sex |
| --- | --- |
| 1 - 25 | 1 |
| 26 - 50 | 2 |
| Over 50 | 3, plus 1 for each additional increment of 50 persons of each sex in excess of 50 |

11)   Except as permitted by Sentences (2) and (14), the number of water closets required for a mercantile occupancy shall be at least one for each 300 males and one for each 150 females.

12)   Except as permitted by Sentence (2), the number of water closets required for an industrial occupancy shall conform to Table 3.7.2.2.-C.

Table 3.7.2.2.-C

Water Closets for an Industrial Occupancy

Forming Part of Sentence 3.7.2.2.(12)

| Number of Persons of Each Sex | Minimum Number of Water Closets for Each Sex |
| --- | --- |
| 1 - 10 | 1 |
| 11 - 25 | 2 |
| 26 - 50 | 3 |
| 51 - 75 | 4 |
| 76 - 100 | 5 |
| Over 100 | 6, plus 1 for each additional increment of 30 persons of each sex in excess of 100 |

13)   In a building whose floor area is more than 600 m2 and that includes one or more individual tenant spaces for a business and personal services occupancy or mercantile occupancy, water closets shall be located so that they are accessible to the public when the building is occupied.

14)   The number of water closets required in a suite of mercantile occupancy whose area is not more than 500 m2 is permitted to be determined in accordance with Table 3.7.2.2.-B based solely on the total number of staff.

3.7.2.3. Lavatories

1)   Except as permitted by Sentence (2), at least one lavatory shall be provided in a room containing one or 2 water closets or urinals, and at least one additional lavatory shall be provided for each additional 2 water closets or urinals.

2)   Wash fountains in circular form are permitted to be provided in lieu of lavatories required by Sentence (1) provided each 500 mm of circumference is considered to be the equivalent of one lavatory.

3)   Any shelf or projection above a lavatory shall be located so that it will not be a hazard.

4)   Lavatories required by Sentence (1) shall be equipped with faucets that

a)   operate automatically, or

b)    have a manual control that

i)   complies with Clause 3.8.3.8.(1)(b),

ii)   does not require the application of continuous force to maintain water flow, and

iii)   where metered, provides at least 10 s of water flow.

3.7.2.4. Safety Glazing

1)   Glazing used for a shower or bathtub enclosure shall conform to Class A of CAN/CGSB-12.1, “Safety Glazing.”

3.7.2.5. Surface Protection

1)   Wall and floor surfaces below the uppermost surfaces of a urinal shall be protected from deterioration by impervious and durable material for a distance from the urinal to a point not less than 900 mm from the projected outline of the urinal on to the wall or floor.

2)   Floor surfaces around a water closet shall be protected from deterioration by an impervious and durable material for a distance not less than 900 mm from the projected outline of the water closet on the floor.

3.7.2.6. Floor Drain

1)   A floor drain shall be installed in a washroom containing a urinal equipped with an automatic flushing device.

3.7.2.7. Grab Bars

1)   Grab bars shall

a)   be slip-resistant and free of any sharp or abrasive elements,

b)   be mounted on surfaces that are free of any sharp or abrasive elements,

c)   be able to resist a load of not less than 1.3 kN applied vertically or horizontally,

d)   be 30 mm to 40 mm in diameter, and

e)   where mounted on a wall, have a clearance of 35 mm to 45 mm from the wall.

3.7.2.8. Bathtubs

1)   Where a bathtub is installed in a hotel or a motel, it shall

a)   have a clear floor space at least 750 mm wide along its length, except that a water closet and a lavatory are permitted to project into this space provided they do not restrict access to the bathtub,

b)   have faucets and other controls that conform to Clause 3.8.3.8.(1)(b),

c)   have a slip-resistant bottom surface,

d)   have grab bars that

i)   conform to Sentence 3.7.2.7.(1),

ii)   are not less than 1 200 mm long located vertically at the end of the bathtub that is adjacent to the clear floor space, with the lower end between 180 mm and 280 mm above the bathtub rim, and

iii)   are not less than 1 200 mm long located horizontally along the length of the bathtub at 180 mm to 280 mm above the bathtub rim, and

e)   be capable of being accessed along its full length with no tracks mounted on the bathtub rim.

3.7.3. Medical Gas Piping Systems

3.7.3.1. Medical Gas Piping

1)   If a non-flammable medical gas piping system is installed, it shall be installed in conformance with

a)   CSA Z7396.1, “Medical gas pipeline systems – Part 1: Pipelines for medical gases, medical vacuum, medical support gases, and anaesthetic gas scavenging systems,” and

b)   Part 3 of Division B of the British Columbia Fire Code.

Section  3.8.   Accessibility

(See Note A-3.8.)

3.8.1. Scope

3.8.1.1. Scope

1)   This Section is concerned with the design and construction of buildings and occupancies to make them accessible.

2)   Buildings and facilities required to be accessible in accordance with Subsection 3.8.2. shall be designed in accordance with Subsection 3.8.3.

3)   Alterations and additions to existing buildings shall conform to Subsection 3.8.4.

4)   Dwelling units required to be adaptable dwelling units shall be designed in accordance with Subsection 3.8.5.

3.8.2. Application

3.8.2.1. Exceptions

(See Note A-3.8.2.1.)

1)   Except as required by Sentence (2), the requirements of this Section apply to all buildings except

a)   detached houses, semi-detached houses, houses with a secondary suite, duplexes, triplexes, townhouses, row houses and boarding houses (see Note A-1.4.1.2.(1) of Division A, Secondary Suite),

b)   buildings of Group F, Division 1 major occupancy, and

c)   buildings that are not intended to be occupied on a daily or full-time basis, including automatic telephone exchanges, pumphouses and substations.

2)   Buildings described in Clause (1)(a) shall comply with Sentence 3.8.5.1.(2).

3.8.2.2. Entrances

(See Note A-3.8.2.2.)

1)   Except for service entrances and entrances to suites described in Clause 3.8.2.3.(2)(l), all pedestrian entrances to an accessible storey of a building referred to in Sentence 3.8.2.1.(1) shall be accessible and shall connect to an accessibleexterior path of travel complying with Sentence 3.8.2.5.(1).

2)   An accessible entrance required by Sentence (1) shall be designed in accordance with Subsection 3.8.3.

3)   At an accessible entrance that includes more than one doorway, only one of the doorways is required to be designed in accordance with Subsection 3.8.3.

4)   If a walkway or pedestrian bridge connects two accessible storeys in different buildings, the path of travel from one storey to the other storey by means of the walkway or bridge shall be accessible.

3.8.2.3. Areas Requiring Access

(See Note A-3.8.2.3.)

1)   Except as permitted by Sentence (2), an accessible path of travel from the entrances required by Sentence 3.8.2.2.(1) to be accessible shall be provided throughout the entrance storey and within all other normally occupied areas of buildings. (See Article 3.3.1.7. for additional requirements regarding floor areas which an accessible path of travel is required.)

2)   Access is not required

a)   to service rooms,

b)   to elevator machine rooms,

c)   to janitors' rooms,

d)   to service spaces,

e)   to crawl spaces,

f)   to attic or roof spaces,

g)   to the floor level above or below the entrance level in suites with more than one level, provided the floor level above or below (see Note A-3.8.2.3.(2)(g))

i)   is not served by a ramp, a passenger elevator, a platform-equipped passenger-elevating device, an escalator or an inclined moving walk,

ii)   is less than 600 m2 in floor area,

iii)   contains only facilities that are also contained on the entrance level, and

iv)   does not contain an assembly occupancy more than 100 m2 in floor area,

h)   within a parking level with no accessible parking spaces,

i)   within high-hazard industrial occupancies,

j)   within portions of a floor area with fixed seats in an assembly occupancy where those portions are not part of the accessible path of travel to spaces designated for wheelchair use,

k)   within floor levels of a suite of residential occupancy that are not at the same level as the entry level to the suite,

l)   within a suite of residential occupancy that has not been designated by this Code or an authority having jurisdiction to be accessible or designed and constructed as an adaptable dwelling unit , or

m)    in a building of residential occupancy that is not more than two storeys that contains multiple dwelling units and common interior space served by a common building entrance, on a floor level that

i)   is not served by a ramp, passenger elevator, a platform-equipped passenger-elevating device, an escalator or an inclined moving walk,

ii)   is less than 600 m2 in floor area,

iii)   is not a building entrance level, and

iv)   does not contain common facilities that are not also provided on an accessible level.

3)   In an assembly occupancy, the number of spaces designated for wheelchair use within rooms or areas with fixed seats shall conform to Table 3.8.2.3. (See also Article 3.8.3.22. for additional requirements.)

4)   The number of spaces designated for wheelchair use within waiting rooms or areas with fixed seats shall conform to Table 3.8.2.3. (See Note A-3.8.2.3.(4).) (See also Article 3.8.3.22. for additional requirements.)

5)   Except as provided in Sentence (6), in an assembly occupancy with more than 25 fixed seats, each row of seats served by two aisles shall have one adaptable seat conforming to Subsection 3.8.3. located adjacent to one of the aisles. (See Note A-3.8.2.3.(5) and (6) and 3.8.3.22.(1) and (4).)

6)   At least 5% of the adaptable seats required by Sentence (5) but no more than 20 adaptable seats shall adjoin an accessible path of travel. (See Note A-3.8.2.3.(5) and (6) and 3.8.3.22.(1) and (4).)

Table 3.8.2.3.

Designated Wheelchair Spaces

Forming Part of Sentences 3.8.2.3.(3) and (4)

| Number of Fixed Seats in Seating Area | Number of Spaces Required for Wheelchairs |
| --- | --- |
| 2 - 99 | 2 |
| 100 - 499 | 3, plus 1 for each additional increment of 70 seats in excess of 100 |
| 500 - 1 999 | 9, plus 1 for each additional increment of 80 seats in excess of 500 |
| 2 000 - 7 999 | 28, plus 1 for each additional increment of 95 seats in excess of 2 000 |
| Over 7 999 | 91, plus 1 for each additional increment of 100 seats in excess of 8 000 |

3.8.2.4. Access to Storeys Served by Escalators and Moving Walks

1)   In a building in which a ramp, escalator or inclined moving walk provides access to any floor level, an interior accessible path of travel shall also be provided to that floor level. (See Note A-3.8.2.4.(1).)

2)   The route from the ramp, escalator or inclined moving walk to the accessible path of travel that leads from floor to floor as required by Sentence (1) shall be clearly indicated by appropriate signs.

3.8.2.5.  Paths of Travel to Building Entrances and Exterior Passenger-Loading Zones

(See Note A-3.8.2.5.)

1)   A direct exterior accessible path of travel that complies with Subsection 3.8.3. shall be provided between an accessible entrance referred to in Article 3.8.2.2. and

a)   a designated accessible parking area, where provided,

b)   an exterior passenger-loading zone, where provided,

c)   common ancillary buildings on the lot, and

d)   a public thoroughfare.

(See Note A-3.8.2.5.(1) and (2).)

2)   In storage garages, an accessible path of travel that complies with Subsection 3.8.3. shall be provided between each parking level with parking spaces designated for persons with disabilities and all other parts of the building required to be provided with access in accordance with Subsection 3.8.2. that are served by that storage garage. (See Note A-3.8.2.5.(1) and (2).)

3)   Exterior passenger-loading zones shall comply with Subsection 3.8.3.

3.8.2.6. Controls and Outlets

1)   Except as provided in Sentence 3.5.2.1.(3), controls for the operation of building services or safety devices, including electrical switches, thermostats, faucets, door and window hardware and intercom systems and switches, that are intended to be operated generally by the occupant shall comply with Subsection 3.8.3. (See Note A-3.8.2.6.(1).)

2)   Electrical outlets that are intended for general occupant use shall be located in conformance with Subsection 3.8.3. (See Note A-3.8.2.6.(2).)

3.8.2.7. Power Door Operators

1)   Except as provided in Sentences (2) and (3), and except for doors provided with hold-open devices, doors equipped with a self-closing device shall be equipped with power door operators complying with Subsection 3.8.3. that allow persons to activate the opening of the doors in the intended direction of travel, where the doors are located

a)   in an entrance referred to in Article 3.8.2.2., including the interior doors of a vestibule where provided,

b)   in an accessible path of travel, between the entrance referred to in Clause (a) and the entrance doors to suites or rooms served by a public corridor or a corridor used by the public (see Note A-3.8.2.7.(1)(b)), and

c)   in an entrance to an accessible washroom.

2)   Only the active leaf in a multiple leaf door in an accessible path of travel need conform to the requirements of this Article.

3)   Where more than one doorway is provided at an accessible entrance, only one of them is required to comply with this Article. (See Note A-3.8.2.7.(3).)

3.8.2.8. Plumbing Facilities

1)   Except as permitted by Sentence (3) and (16), at each location where washrooms are provided in a storey to which an accessible path of travel is required in accordance with Article 3.8.2.3., at least one universal washroom complying with Subsection 3.8.3. shall be provided. (See Note A-3.8.2.8.(1) to (4).)

2)   Except as permitted by Sentence (3), where more than two water closets or a combination of more than one water closet and one urinal are provided in a washroom located in a storey to which an accessible path of travel is required in accordance with Article 3.8.2.3., at least one water-closet stall shall be accessible in accordance with Subsection 3.8.3. (See Note A-3.8.2.8.(1) to (4).)

3)   Except as required by Article 3.8.2.13., washrooms located within a suite of residential occupancy or a suite of care occupancy need not conform to the requirements of Sentence (1) or (2). (See Note A-3.8.2.8.(1) to (4).)

4)   In a building in which water closets are required in accordance with Subsection 3.7.2., at least one universal washroom shall be provided in the entrance storey, unless

a)   an accessible path of travel is provided to a universal washroom elsewhere in the building, or

b)   the water closets required by Subsection 3.7.2. are for dwelling units only.

(See Note A-3.8.2.8.(1) to (4).)

5)   At least one water-closet stall or enclosure in a washroom required to be accessible shall comply with Subsection 3.8.3.

6)   Where urinals are provided in an accessible washroom, at least one urinal for persons with limited mobility conforming to Subsection 3.8.3. shall be provided for every 10 urinals.

7)   Where water-closet stalls are provided in an accessible washroom, at least one stall for persons with limited mobility conforming to Subsection 3.8.3. shall be provided for every 10 stalls.

8)   An accessible washroom shall be provided with a lavatory that complies with Subsection 3.8.3.

9)   Where mirrors are provided in an accessible washroom, at least one mirror shall comply with Subsection 3.8.3.

10)   At each location where one or more drinking fountains are provided, at least one of them shall comply with Subsection 3.8.3.

11)   At each location where one or more water-bottle filling stations are provided, at least one of them shall comply with Subsection 3.8.3.

12)   Except within a suite of care occupancy or a suite of residential occupancy, where showers are provided in a building, at least one shower stall in each group of showers shall comply with Subsection 3.8.3.

13)   At each location where a showering facility is provided for use by the general public or customers, or as part of a common-use area for employees, at least one universal dressing and shower room conforming to Subsection 3.8.3. shall be provided. (See Note A-3.8.2.8.(13).)

14)   Where a bathtub is installed in a suite of residential occupancy required to be accessible, it shall comply with Subsection 3.8.3.

15)   In buildings containing Group A, Group B, Division 2 or Group E major occupancies where at least one of these major occupancies has an occupant load of more than 500, at least one universal washroom on the storey on which the main accessible entrance to the building is located shall incorporate an accessible change space conforming to Subsection 3.8.3. (See Note A-3.8.2.8.(15).)

16)   In occupancies or parts of occupancies designed to be accessible and used predominantly by children, in patient areas in treatment occupancies, and in resident areas in care occupancies, it is permissible to design and locate plumbing fixtures and grab bars differently than described in Subsection 3.8.3. to accommodate the special needs of children, patients, residents, and care providers.

3.8.2.9. Assistive Listening Systems

1)   In a building of assembly occupancy, all classrooms, auditoria, meeting rooms and theatres with an area of more than 100 m2, including courtrooms of any size, shall be equipped with an assistive listening system complying with Subsection 3.8.3.

2)   In each location where information, goods or services are provided to the public at service counters in buildings of assembly occupancy, at least one of the service counters shall be equipped with

a)   an assistive listening system or adaptive technology conforming to Subsection 3.8.3., and

b)   an amplification system, where there is a barrier to communication, such as a glass screen.

(See Note A-3.8.2.9.(2).)

3.8.2.10. Signs and Indicators

1)   Unless the degree of access provided is such as to make these signs unnecessary, signs providing visual information in accordance with Subsection 3.8.3. shall be installed to indicate the location of

a)   accessible entrances,

b)   alternative access routes,

c)   accessible spaces in seating areas,

d)   accessible refreshment facilities,

e)   accessible checkout lanes,

f)   accessible public telephones,

g)   accessible washrooms,

h)   accessible showers,

i)   accessible passenger-elevating devices,

j)   accessible parking spaces,

k)   accessible passenger loading zones, and

l)   assistive listening systems or adaptive technologies.

2)   Where a washroom is not designed to accommodate persons with physical disabilities in a storey to which an accessible path of travel is required, signs providing visual and tactile information in accordance with Subsection 3.8.3. shall be installed to indicate the location of accessible washrooms.

3)   Except for doors that serve service spaces or are located within a suite, signs installed at or near doors shall provide the same information in both visual and tactile forms in accordance with Subsection 3.8.3.

4)   Directional signs shall provide visual information in accordance with Subsection 3.8.3. (See Note A-3.8.2.10.(4).)

3.8.2.11. Counters

1)   Where a service counter is provided, at least one section of it shall comply with Subsection 3.8.3. (See Note A-3.8.2.11.(1).) (See also Note A-3.8.2.3.)

3.8.2.12. Telephones

1)   In each location where one or more public telephones are installed, at least one telephone shall comply with Subsection 3.8.3.

3.8.2.13. Sleeping Rooms and Bed Spaces

1)   At least one for every 20 or part thereof of sleeping rooms or bed spaces shall conform to Subsection 3.8.3. where provided in

a)   hotels and motels (see also Clause 3.2.4.19.(1)(g) and Sentences 3.2.4.20.(7) and (8)), and

b)   not including apartments and condominiums and the buildings described in 3.8.2.1.(1)(a), other buildings or parts of buildings used for residential major occupancies (see also Sentence 3.2.4.20.(17)).

3.8.3. Design

3.8.3.1. Design Standards

1)   Buildings or parts thereof and facilities that are required to be accessible shall be designed in accordance with

a)   this Subsection, or

b)   for each accessible application listed independent of other accessible applications, the applicable provisions of CSA B651, “Accessible design for the built environment,” listed in Table 3.8.3.1..

(See Note A-3.8.3.1.(1).)

Table 3.8.3.1.

Accessible Design Provisions

Forming Part of Sentence 3.8.3.1.(1) and (2)

| Accessible Application (Code References) | Applicable CSA B651 Provisions |
| --- | --- |
| Interior accessible routes (3.8.3.2.) | 4.3 and 5.1 |
| Exterior accessible routes (3.8.3.3.) | 8.2.1 to 8.2.5 and 8.2.7 |
| Passenger pickup areas (3.8.3.4.) | 9.3 |
| Ramps (3.8.3.5.) | 5.3 and 5.5 |
| Doors and doorways (3.8.3.6.) | 5.2 |
| Passenger-elevating devices (3.8.3.7.) | 5.6.2 |
| Operating controls (3.8.3.8.) | 4.2 |
| Signage (3.8.3.9.) | 4.5 and 9.4 |
| Drinking fountains (3.8.3.10.) | 6.1 |
| Washroom facilities (3.8.3.12. to 3.8.3.16.) | 6.2 and 6.3 |
| Bathing facilities (3.8.3.17. and 3.8.3.18.) | 6.5 |
| Communication (3.8.3.19. and 3.8.3.21.) | 6.6 |
| Counters (3.8.3.20. and 3.8.3.21.) | 6.7.1 |
| Spaces in seating areas (3.8.3.22.) | 6.7.3 |

2)   The design of each accessible application listed in Table 3.8.3.1. shall comply entirely with Clause (1)(a) or Clause (1)(b).

3.8.3.2. Accessible Path of Travel

1)   Except as required elsewhere in this Part or as permitted by Sentence (2) and Article 3.8.3.6. pertaining to doorways, the clear width of an accessible path of travel shall be not less than 1 000 mm.

2)   The clear width of an accessible path of travel is permitted to be reduced to not less than 850 mm for a length of not more than 600 mm, provided the clear floor space at either end of the reduced-clear width section is level within a rectangular area

a)   with a dimension parallel to each end of the reduced-clear width section is not less than 1 000 mm, and

b)   with a dimension perpendicular to each end of the reduced-clear width section is not less than 1 500 mm.

(See Note A-3.8.3.2.(2).)

3)   Interior and exterior walking surfaces that are within an accessible path of travel shall

a)   have no opening that will permit the passage of a sphere more than 13 mm in diameter,

b)   have any elongated openings oriented approximately perpendicular to the direction of travel,

c)   be stable, firm and slip-resistant,

d)   have a cross slope no steeper than 1 in 50,

e)   be beveled at a maximum slope of 1 in 2 at changes in level between 6 mm and 13 mm,

f)   be provided with sloped floors or ramps at changes in level more than 13 mm, and

g)   be designed as a ramp complying with this Section where the path of travel has a slope steeper than 1 in 20.

(See Note A-3.8.3.2.(3).)

4)   An accessible path of travel is permitted to include ramps, passenger elevators or other platform-equipped passenger-elevating devices to overcome a difference in level.

5)   The width of an accessible path of travel that is more than 24 m long shall be increased to not less than 1 700 mm for a length of 1 700 mm at intervals not exceeding 24 m.

6)   Where a section of an accessible path of travel is less than 1 500 mm wide for a distance of more than 12 m, it shall end in a clear floor space that is

a)   not less than 1 700 mm in diameter,

b)   not less than 1 700 mm by 1 500 mm, or

c)   T-shaped with overall dimensions measuring 1 700 mm wide by 1 500 mm long, where the two arms of the “T” are not less than 1 000 mm wide and extend not less than 300 mm from each side of the base of the “T” and the base is not less than 1 000 mm wide and extends not less than 500 mm from each arm.

(See Note A-3.8.3.2.(6).)

7)   An accessible path of travel shall be equipped to provide illumination in accordance with Sentences 3.2.7.1.(1) and (2). (See also Sentences 3.2.7.1.(3) and Article 9.34.2.7.)

3.8.3.3. Exterior Walks

1)   Exterior walks that form part of an accessible path of travel shall

a)   have a slip-resistant, continuous and even surface,

b)   be not less than 1 600 mm wide,

c)   have a level area conforming to Clause 3.8.3.5.(1)(c) adjacent to an entrance doorway, and

d)   be designed in accordance with Clause 8.2.1 of CSA B651, “Accessible design for the built environment.”

3.8.3.4. Passenger-Loading Zones

1)   If a passenger-loading zone is provided, it shall have

a)   an access aisle not less than 1 500 mm wide and 6 000 mm long adjacent and parallel to the vehicle pull-up space,

b)   a curb ramp, designed in accordance with Clause 8.3.3. of CSA B651, “Accessible design for the built environment,” where there are curbs between the access aisle and the vehicle pull-up space, and

c)   a clear height of not less than 2 750 mm at the pull-up space and along the vehicle access and egress routes.

3.8.3.5. Ramps

1)   Except when designed as a curb ramp in accordance with Clause 3.8.3.4.(1)(b), a ramp located in an accessible path of travel shall

a)   have a clear width not less than 1 000 mm (see Note A-3.4.3.4.),

b)   have a uniform slope along its length not more than 1 in 12 (see Note A-3.8.3.5.(1)(b)),

c)   have a level area not less than 1 700 mm by 1 700 mm at the top and bottom and at intermediate levels of a ramp leading to a door, so that on the latch side the level area extends not less than

i)   600 mm beyond the edge of the door opening where the door opens towards the ramp, or

ii)   300 mm beyond the edge of the door opening where the door opens away from the ramp,

(see Note A-3.8.3.5.(1)(c)),

d)   have a level area not less than 1 350 mm long and at least the same width as the ramp

i)   at intervals not more than 9 m along its length, and

ii)   where there is an abrupt change in the direction of the ramp, and

e)   except as provided in Sentences (2) and (3), be equipped with handrails conforming to Article 3.4.6.5., except that they shall be not less than 865 mm and not more than 965 mm high, and

f)   be equipped with guards conforming to Article 3.4.6.6.

2)   Handrails installed in addition to required handrails need not comply with the height requirements stated in Clause (1)(e).

3)   The requirement for handrails in Clause (1)(e) need not apply to a ramp serving as an aisle for fixed seating.

4)   The surfaces of ramps and landings shall

a)   be hard or resilient where the ramp is steeper than 1 in 15 (see Note A-3.8.3.5.(4)(a)),

b)   have a cross slope no steeper than 1 in 50, and

c)   where exposed to water, be designed to drain.

5)   Ramps and landings not at ground level or adjacent to a wall shall have edge protection consisting of

a)   a curb not less than 75 mm high, or

b)   a raised barrier or rail located not more than 100 mm from the ramp or landing surface.

3.8.3.6. Doorways and Doors

1)   Except where stated otherwise, this Article applies to swinging and sliding doors.

2)   Every doorway that is located in an accessible path of travel shall have a clear width not less than 850 mm

a)   for swinging doors, when measured from the face of the active leaf, in the open position of 90° to the doorway, to the outside edge of the stop on the door frame, and

b)   for sliding doors, when measured from the edge of the door, in the open position, to the outside of the stop on the door frame.

(See Note A-3.8.3.6.(2).)

3)   Doorways in a path of travel to at least one bathroom within a suite of residential occupancy shall have a clear width not less than 850 mm when measured in accordance with Sentence (2). (See Note A-3.8.3.6.(3).)

4)   Door-operating devices shall

a)   comply with Clause 3.8.3.8.(1)(b), and

b)   be operable at a height between 900 mm and 1 100 mm above the floor.

(See also Sentence 3.3.1.13.(4) regarding additional devices.)

(See Note A-3.8.3.6.(4).)

5)   A threshold for a doorway referred to in Sentences (2) and (3) shall be not more than 13 mm higher than the finished floor surface and shall be beveled to facilitate the passage of wheelchairs.

6)   Power door operators required by Sentence 3.8.2.7.(1) shall

a)   activate automatically or through the use of controls that

i)   are located in an accessible path of travel,

ii)   are marked with the International Symbol of Access,

iii)   are located clear of the door swing and not less than 600 mm and no more than 1 500 mm from that door swing,

iv)   comply with Subclause 3.8.3.8.(1)(a)(iii),

v)   are operable from a height between 150 mm and 300 mm as well as between 900 mm and 1 100 mm above the floor, and

vi)   are operable by touching or approaching any part of their surface with a fist, arm or foot, and

b)   unless equipped with safety sensors,

i)   fully open the door in not less than 3 s, and

ii)   require a force not more than 65 N to stop movement of the door.

(See Note A-3.8.3.6.(6) and (7).)

7)   A cane-detectable guard shall be installed on the hinged side of power-assisted doors that swing open into the path of travel. (See Note A-3.8.3.6.(6) and (7).)

8)   Except as provided in Sentence (9) and except for a door with a power door operator complying with Sentence (6), when unlatched, a door in an accessible path of travel shall open when the force applied to the handle, push plate or latch-releasing device is not more than

a)   38 N in the case of an exterior swinging door,

b)   22 N in the case of an interior swinging door, or

c)   22 N in the case of a sliding door.

9)   Sentence (8) does not apply to a door at the entrance to a dwelling unit, or where greater forces are required in order to close and latch the door against the prevailing difference in air pressure on opposite sides of the door. (See Note A-3.8.3.6.(9).)

10)   Except for a door at the entrance to a dwelling unit, a closer for an interior door in an accessible path of travel shall have a closing period of not less than 3 s measured from when the door is in an open position of 70° to the doorway, to when the door reaches a point 75 mm from the closed position, measured from the leading edge of the latch side of the door. (See Note A-3.8.3.6.(10).)

11)   Unless equipped with a power door operator complying with Sentence (6), a swinging door in an accessible path of travel shall have a clear space on the latch side extending the height of the doorway and not less than

a)   600 mm beyond the edge of the door opening if the door swings toward the approach side, and

b)   300 mm beyond the edge of the door opening if the door swings away from the approach side.

(See Note A-3.8.3.6.(11).)

12)   A vestibule located in an accessible path of travel shall be arranged to allow the movement of wheelchairs between doors and shall provide a distance between 2 doors in series of not less than 1 350 mm plus the width of any door that swings into the space in the path of travel from one door to another.

13)   Only the active leaf in a multiple-leaf door in an accessible path of travel need conform to the requirements of this Article.

14)   Except as provided in Clause 3.8.3.5.(1)(c) and Sentence (16), the clear floor space on the pull side of a swinging door in an accessible path of travel shall be level within a rectangular area of not less than 1 700 mm by 1 500 mm measured from the hinged side of the door. (See Note A-3.8.3.6.(14) to (16).)

15)   Except as provided in Clause 3.8.3.5.(1)(c) and Sentence (16), the clear floor space on the push side of a swinging door and on each side of a sliding door in an accessible path of travel shall be level within a rectangular area

a)   whose dimension parallel to the closed door is not less than 1 200 mm, and

b)   whose dimension perpendicular to the closed door is not less than 1 500 mm.

(See Note A-3.8.3.6.(14) to (16).)

16)   Where a door referred to in Sentences (14) and (15) is equipped with a power door operator complying with Sentence (6), the width of the clear floor space parallel to the closed door is permitted to be reduced to not less than 1 000 mm. (See Note A-3.8.3.6.(14) to (16).)

17)   Except for facilities for persons with cognitive disabilities such as dementia, doorways leading from a public corridor or a corridor used by the public that provide access to a public area or an exit shall be provided with a door or door frame that has a readily apparent visual contrast with adjacent wall surfaces. (See Note A-3.8.3.6.(17).) (See also Note A-3.4.6.11.(4).)

3.8.3.7. Passenger-Elevating Devices

1)   A passenger-elevating device referred to in Article 3.8.2.3. located in an accessible path of travel shall

a)   conform to

i)   Appendix E of ASME A17.1/CSA B44, “Safety Code for Elevators and Escalators,” or

ii)   CSA B355, “Platform lifts and stair lifts for barrier-free access,”

b)   have a clear floor space not less than 1 500 mm long by 1 000 mm wide, and

c)   have entry doors or gates

i)   providing a clear width not less than 850 mm in the open position if located on the short side of the passenger-elevating device, or

ii)   providing a clear width not less than 1 000 mm in the open position if located at either end of the long side of the passenger-elevating device.

3.8.3.8. Controls and Outlets

1)   Controls described in this Section shall

a)   where located in a storey where an accessible path of travel is required and unless otherwise stated,

i)   be in or adjacent to the accessible path of travel,

ii)   be mounted 400 mm to 1 200 mm above the floor, and

iii)   be adjacent to and centred on either the length or the width of a clear floor space of 1 350 mm by 800 mm,

b)   be operable

i)   with one hand in a closed fist position, without requiring tight grasping, pinching with fingers, or twisting of the wrist, and

ii)   unless otherwise stated, with a force not more than 22 N, and

c)   where controls provide a feedback signal to the user, it shall be both audible and visible (see Note A-3.8.3.8.(1)(c)).

2)   Electrical outlets described in this Section shall be located in conformance with Subclause (1)(a)(ii).

(See Note A-3.8.2.6.(2).)

3.8.3.9. Accessible Signs

1)   Visual information signs required by Subsections 3.4.5. and 3.4.6. and Article 3.8.2.10. shall comply with Clauses 4.5.1, 4.5.2, 4.5.3 and 4.5.4 of CSA B651, “Accessible design for the built environment.” (See Note A-3.8.3.9.(1) and (2).)

2)   Tactile information signs required by Subsections 3.4.5. and 3.4.6. and Article 3.8.2.10. shall

a)   have Braille and tactile characters in accordance with Clauses 4.5.6.2 and 4.5.6.3 of CSA B651, “Accessible design for the built environment,”

b)   be installed on the wall closest to the latch side of the door or on the nearest wall on the right side of the door, where there is no wall at the latch side, and

c)   be centred 1 500 mm above the finished floor with the edge of the sign located not more than 300 mm from the door.

(See Note A-3.8.3.9.(1) and (2).)

3)   Signs required by Article 3.8.2.10. shall incorporate the International Symbol of Access, Modified International Symbol of Access, or the International Symbol of Access for Hearing Loss and appropriate graphical or textual information that clearly indicates the type of facilities available. (See Note A-3.8.3.9.(3).)

3.8.3.10. Drinking Fountains

1)   Drinking fountains required by Sentence 3.8.2.8.(10) shall be equipped with controls that

a)   activate automatically, or

b)   comply with Clause 3.8.3.8.(1)(b) and are located on the front or on both sides of the fountain.

2)   Where drinking fountains referred to in Sentence (1) are located in a storey where an accessible path of travel is required, they shall

a)   be located along the accessible path of travel,

b)   have a minimum clear floor space of 800 mm by 1 350 mm in front of them,

c)   where they have frontal access, provide a knee clearance in accordance with Clause 3.8.3.16.(1)(e), and

d)   have a spout that

i)   is located near the front of the unit, at a height between 750 mm and 915 mm above the floor, and

ii)   directs water flow in a trajectory that is nearly parallel to the front of the unit, at a height not less than 100 mm.

(See Sentences 3.3.1.8.(2) and (3) on horizontal projections.)

3.8.3.11. Water-Bottle Filling Stations

1)   Water-bottle filling stations required by Sentence 3.8.2.8.(11) shall be equipped with controls that

a)   activate automatically, or

b)   comply with Clause 3.8.3.8.(1)(b).

2)   Water-bottle filling stations required by Sentence 3.8.2.8.(11) that are located in a storey where an accessible path of travel is required shall

a)   be located along the accessible path of travel,

b)   have a clear floor space of 800 mm by 1 350 mm in front of them (see Note A-3.8.3.11.(2)(b) and (d)),

c)   where they have frontal access, provide a knee clearance in accordance with Clause 3.8.3.16.(1)(e),

d)   be operable at a height of not more than 1 200 mm above the floor (see Note A-3.8.3.11.(2)(b) and (d)), and

e)   be equipped with controls that

i)   activate automatically, or

ii)   comply with Sentence 3.8.3.8.(1).

(See Sentences 3.3.1.8.(2) and (3) on horizontal projections.)

3.8.3.12. Accessible Water-Closet Stalls

1)   Water-closet stalls and enclosures required by Sentence 3.8.2.8.(5) shall

a)   be not less than 1 500 mm wide by 1 500 mm deep,

b)   have a clear lateral transfer space adjacent to the water closet that

i)   is at least 1 500 mm long, measured from the wall behind the water closet, and

ii)   is at least 900 mm wide, measured from the closest edge of the water closet seat,

(see Note A-3.8.3.12.(1)(b))

c)   have a clear floor space of 1 700 mm by 1 700 mm in front of the accessible stall,

d)   be equipped with a door that

i)   can be latched from the inside with a mechanism located 900 mm to 1 100 mm above the floor that conforms to Clause 3.8.3.8.(1)(b),

ii)   is aligned with either the transfer space adjacent to the water closet or with a clear floor space not less than 1 700 mm by 1 700 mm within the stall,

iii)   provides a clear opening not less than 850 mm wide when it is open, measured in accordance with Sentence 3.8.3.6.(2),

iv)   is self-closing so that, when at rest, the door is ajar by not more than 50 mm beyond the jamb,

v)   swings outward, unless there is sufficient floor space within the stall for the door to swing inward in addition to a clear floor space of at least 800 mm by 1 350 mm (see Note A-3.8.3.12.(1)(d)(v)),

vi)   where the door swings outward, is provided with a horizontal, D-shaped, visually contrasting door pull not less than 140 mm long located on the inside such that its midpoint is 200 mm to 300 mm from the hinged side of the door and 900 mm to 1100 mm above the floor (see Note A-3.8.3.12.(1)(d)(vi)), and

vii)   is provided with a horizontal, D-shaped, visually contrasting door pull not less than 140 mm long located on the outside such that its midpoint is 120 mm to 220 mm from the latch side and 900 mm to 1100 mm above the floor,

e)   have a water closet located so that the distance between the centre line of the fixture and the wall on one side is 460 mm to 480 mm,

f)   be equipped with an L-shaped grab bar that

i)   is mounted on the side wall closest to the water closet,

ii)   has horizontal and vertical components not less than 760 mm long mounted with the horizontal component 750 mm to 850 mm above the floor and the vertical component 150 mm in front of the water closet (see Note A-3.8.3.12.(1)(f)(ii)), and

iii)   complies with Article 3.7.2.7.,

g)   be equipped with either one grab bar at least 600 mm long and centred over the water closet, or two grab bars at least 300 mm long and located either side of the flush valve, that

i)   conform to Article 3.7.2.7.,

ii)   are mounted on the rear wall, and

iii)   are mounted at the same height as the grab bar on the side wall or 100 mm above the top of the attached water tank, if applicable,

h)   be equipped with a coat hook mounted not more than 1 200 mm above the floor on a side wall and projecting not more than 50 mm from the wall, and

i)   be equipped with a toilet paper dispenser mounted on the side wall closest to the water closet such that

i)   the bottom of the dispenser is 600 mm to 800 mm above the floor, and

ii)   the closest edge of the dispenser is not more than 300 mm from the front of the water closet.

3.8.3.13. Universal Washrooms

(See Note A-3.8.3.13.)

1)   A universal washroom shall

a)   be served by an accessible path of travel,

b)   have a door complying with Article 3.8.3.6. that

i)   has a latch-operating mechanism located 900 mm to 1 100 mm above the floor that complies with Clause 3.8.3.8.(1)(b) and is capable of being locked from the inside, and released from the outside in case of emergency, and

ii)   if it is an outward swinging door that is not self-closing, has a horizontal, D-shaped, visually contrasting door pull not less than 140 mm long located on the inside so that its midpoint is not less than 200 mm and not more than 300 mm from the hinged side of the door and not less than 900 mm and not more than 1 100 mm above the floor (see Note A-3.8.3.12.(1)(d)(vi)),

c)   have one lavatory conforming to Article 3.8.3.16.,

d)   have one water closet conforming to Article 3.8.3.14. and Clause 3.8.3.12.(1)(e),

e)   have a clear lateral transfer space adjacent to the water closet that conforms to Clause 3.8.3.12.(1)(b),

f)   have grab bars conforming to Clauses 3.8.3.12.(1)(f) and (g),

g)   have a coat hook conforming to Clause 3.8.3.12.(1)(h),

h)   have a toilet paper dispenser conforming to Clause 3.8.3.12.(1)(i),

i)   unless a counter space of not less than 200 mm by 400 mm is provided, have a shelf located not more than 1 200 mm above the floor with a useable surface of not less than 200 mm by 400 mm,

j)   be designed to permit a wheelchair to turn in an open space not less than 1 700 mm in diameter, and

k)   provide emergency lighting conforming to Article 3.2.7.3.

2)   A universal washroom required to have an accessible change space as stipulated in Sentence 3.8.2.8.(15) shall

a)   be equipped with an adult-sized change table that is

i)   designed to carry a minimum load of 1.3 kN,

ii)    impervious to water, and

iii)   designed to be easily cleaned,

b)   have a clear floor space to accommodate the adult-sized change table that is 810 mm wide by 1 830 mm long and does not overlap with the clear spaces required by Clauses (1)(e), (1)(j) and (c), and

c)   have a clear transfer space of 900 mm by 1 350 mm adjacent to the long side of the clear floor space for the adult-sized change table.

3.8.3.14. Water Closets

1)   A water closet for a person with physical disabilities shall

a)   be equipped with a seat located 430 mm to 480 mm above the floor,

b)   flush automatically or be equipped with a flushing control that

i)   is located 500 mm to 900 mm above the floor,

ii)   is located no more than 350 mm from the transfer side, and

iii)   complies with Clause 3.8.3.8.(1)(b),

c)   be equipped with a seat lid or other back support, and

d)   where it has a tank, have a securely attached tank top.

(See Note A-3.8.3.14.(1).)

3.8.3.15. Water-Closet Stalls and Urinals for Persons with Limited Mobility

1)   Water-closet stalls for persons with limited mobility required by Sentence 3.8.2.8.(7) shall

a)   be at least 1 500 mm deep and 890 mm to 940 mm wide,

b)   be equipped with a door that

i)   has a latch-operating mechanism conforming to Clause 3.8.3.8.(1)(b) that can be locked from the inside and released from the outside in the event of an emergency,

ii)   provides a clear opening not less than 850 mm wide when it is open, measured in accordance with Sentence 3.8.3.6.(2),

iii)   swings outward, unless the minimum dimensions required by Clause (a) do not overlap with the area of the door swing,

iv)   is self-closing so that, when at rest, the door is ajar by not more than 50 mm beyond the jamb, and

v)   has a horizontal, D-shaped, visually contrasting door pull on both sides of the door, near the latch side, located 900 mm to 1 100 mm above the finished floor,

c)   have one water closet conforming to Article 3.8.3.14. centred within the stall,

d)   have a horizontal grab bar conforming to Article 3.7.2.7. on each side of the water closet that

i)   is located 750 mm to 850 mm above the floor,

ii)   begins not more than 300 mm from the wall behind the water closet, and

iii)   extends at least 450 mm in front of the toilet seat, and

e)   be equipped with a coat hook mounted not more than 1 200 mm above the floor on a side wall and projecting not more than 50 mm from the wall.

2)   Urinals described in Sentence 3.8.2.8.(6) shall

a)   be wall-mounted, with the rim located not more than 430 mm above the floor,

b)   be adjacent to an accessible route,

c)   have a clear width of approach that is at least 800 mm wide by 1 350 mm long centred on the urinal and unobstructed by privacy screens,

d)   have no step in front of it,

e)   have a flush control that

i)   is automatic, or

ii)   complies with Clause 3.8.3.8.(1)(b) and is located 900 mm to 1 100 mm above the floor, and

f)   have a vertically mounted grab bar installed on each side that

i)   complies with Article 3.7.2.7.,

ii)   is not less than 600 mm long, with its centre line 1 000 mm above the floor, and

iii)   is located not more than 380 mm from the centre line of the urinal.

3.8.3.16. Lavatories and Mirrors

1)   Lavatories required by Sentence 3.8.2.8.(8) shall

a)   be equipped with faucets complying with Sentence 3.7.2.3.(4),

b)   be located so that the distance between the centre line of the lavatory and any side wall is not less than 460 mm,

c)   have a clear floor space in front of the lavatory that is at least

i)   800 mm wide, centred on the lavatory, and

ii)   1 350 mm long, of which no more than 430 mm is beneath the lavatory,

d)   have a rim height not more than 865 mm above the floor,

e)   have a clearance beneath the lavatory not less than

i)   800 mm wide, centred on the lavatory,

ii)   735 mm high at the front edge,

iii)   685 mm high at a point 200 mm back from the front edge, and

iv)   230 mm high over the distance from a point 280 mm to a point 430 mm back from the front edge,

(see Note A-3.8.3.16.(1)(e))

f)   have insulated water supply and drain pipes where these pipes are exposed (see Note A-3.8.3.16.(1)(f)),

g)   have a soap dispenser that

i)   is automatic, or

ii)   complies with Clause 3.8.3.8.(1)(b) and is located not more than 1 100 mm above the floor, within 500 mm from the front of the lavatory (see Note A-3.8.3.16.(1)(g)), and

h)   have a towel dispenser or other hand-drying equipment located close to the lavatory, with operating controls not more than 1 200 mm above the floor in an area that is accessible to persons using wheelchairs.

2)   Mirrors required by Sentence 3.8.2.8.(9) shall be

a)   mounted with their bottom edge not more than 1 000 mm above the floor, or

b)   fixed in an inclined position so as to be usable by a person using a wheelchair.

3.8.3.17. Showers

1)   Showers required by Sentence 3.8.2.8.(12) shall

a)   be not less than 1 500 mm wide and 900 mm deep,

b)   have a clear floor space at the entrance to the shower that is not less than 900 mm deep and the same width as the shower, except that fixtures are permitted to project into that space provided they do not restrict access to the shower (see Note A-3.8.3.17.(1)(b)),

c)   have no doors or curtains that obstruct the controls or the clear floor space at the entrance to the shower,

d)   have a slip-resistant floor surface,

e)   have a threshold not more than 13 mm higher than the finished floor, and where it is higher than 6 mm, beveled to a slope no steeper than 1 in 2,

f)   have 2 grab bars

i)   that conform to Sentence 3.7.2.7.(1),

ii)   one of which is not less than 1 000 mm long and located vertically on the side wall 50 mm to 80 mm from the adjacent clear floor space, with its lower end 600 mm to 650 mm above the floor, and,

iii)   one of which is L-shaped and located on the wall opposite the entrance to the shower, with a horizontal member not less than 1 000 mm long mounted 750 mm to 870 mm above the floor and a vertical member not less than 750 mm long mounted 400 mm to 500 mm from the side wall on which the other vertical grab bar is mounted,

(see Note A-3.8.3.17.(1)(f)),

g)   have a hinged seat that is not spring-loaded or a fixed seat with a smooth, slip-resistant surface and no rough edges, the seat being

i)   not less than 450 mm wide and 400 mm deep,

ii)   mounted on the same side wall as the vertical grab bar, at 460 mm to 480 mm above the floor,

iii)   designed to carry a minimum load of 1.3 kN,

iv)   impervious to water, and

v)   designed to be easily cleaned,

h)   have a pressure-equalizing or thermostatic-mixing valve and other controls that

i)   comply with Clause 3.8.3.8.(1)(b), and

ii)   are mounted on the wall opposite the entrance to the shower at not more than 1 200 mm above the floor and within reach of the seat,

i)   have a hand-held shower head with not less than 1 800 mm of flexible hose located so that it

i)   can be reached from a seated position,

ii)   can be used in a fixed position at a height of 1 200 mm and 2 030 mm, and

iii)   does not obstruct the use of the grab bars, and

j)   have recessed soap holders that can be reached from the seated position.

2)   A universal dressing and shower room required by Sentence 3.8.2.8.(13) shall

a)   be located in an accessible path of travel,

b)   have a door capable of being locked from the inside and released from the outside in the event of an emergency,

c)   have a lavatory and a mirror conforming to Article 3.8.3.16.,

d)   have a shower conforming to Sentence (1),

e)   have a bench that is

i)   at least 1 830 mm long by 760 mm wide and 480 mm to 520 mm high,

ii)   designed to carry a minimum load of 1.3 kN,

iii)   impervious to water, and

iv)   designed to be easily cleaned,

f)   have a clear transfer space adjacent to the long side of the bench that is 900 mm wide and as long as the bench (see Note A-3.8.3.17.(2)(f)),

g)   have a coat hook conforming to Clause 3.8.3.12.(1)(h), and

h)   provide emergency lighting conforming to Article 3.2.7.3.

3.8.3.18. Accessible Bathtubs

1)   A bathtub required by Sentence 3.8.2.8.(14) shall

a)   be located in a room with a clear floor space not less than 1 700 mm in diameter,

b)   be not less than 1 500 mm long,

c)   have a clear floor space at the entrance to the bathtub that is not less than 900 mm deep and at least the same length as the bathtub, except that fixtures are permitted to project into that space provided they do not restrict access to the shower,

d)   be capable of being accessed along its full length with no tracks mounted on its rim,

e)   have a pressure-equalizing or thermostatic mixing valve  and other controls that

i)   conform to Clause 3.8.3.8.(1)(b), and

ii)   are located on the centre line or between the centre line of the bathtub and the exterior edge of the bathtub rim, at a maximum height of 450 mm above the rim,

f)   have three grab bars

i)   that conform to Sentence 3.7.2.7.(1),

ii)   that are not less than 1 200 mm long,

iii)   two of which are located vertically at each end of the bathtub, set 80 mm to 120 mm in from the outside edge of the bathtub, with their lower end 180 mm to 280 mm above the bathtub rim, and

iv)   one of which is located horizontally along the length of the bathtub at 180 mm to 280 mm above the bathtub rim,

g)   have a slip-resistant bottom surface, and

h)   be equipped with a hand-held shower head with not less than 1 800 mm of flexible hose that can be used in a fixed position at a height of 1 200 mm and 2 030 mm.

3.8.3.19. Assistive Listening Systems

(See Note A-3.8.3.19.)

1)   Assistive listening systems required by Sentence 3.8.2.9.(1) shall encompass the entire seating area.

2)   Assistive listening systems or adaptive technologies required by Sentence 3.8.2.9.(2) shall provide for the clear communication required for the exchange of information, goods and services.

3.8.3.20. Counters

1)   A section of a service counter required to be accessible in accordance with Sentence 3.8.2.11.(1) shall

a)   be not less than 800 mm long centred over a knee space conforming to Clause (c),

b)   have a surface not more than 865 mm above the floor, and

c)   where forward-facing interaction with a person or a device is required, have a knee space underneath it that is (see Note A-3.8.3.20.(1)(c))

i)   not less than 800 mm wide,

ii)   not less than 685 mm high, and

iii)   not less than 485 mm deep.

3.8.3.21. Telephones

1)   A telephone required to be accessible in accordance with Article 3.8.2.12. shall

a)   be adjacent to and centred on either the length or the width of a clear floor space not less than 1 350 mm by 800 mm,

b)   where a forward approach is provided, have a knee space underneath it conforming to Clause 3.8.3.20.(1)(c), and

c)   be located so that its receiver and operable parts are not more than 1 200 mm above the floor.

2)   Where provided, shelves or counters for public telephones shall

a)   be level,

b)   be not less than 305 mm deep,

c)   have, for each telephone provided, a clear space not less than 250 mm wide having no obstruction within 250 mm above the surface, and

d)   have a section with a surface not more than 865 mm above the floor serving at least one telephone.

(See Note A-3.8.3.21.(2).)

3.8.3.22. Spaces in Seating Area

1)   Spaces designated for wheelchair use in assembly occupancies as required by Sentence 3.8.2.3.(3) shall conform to the following:

a)   at least one designated space shall be clear and level for each increment of 200 seats and the remaining designated spaces shall be level and have removable seats,

b)   they shall be not less than 900 mm wide and 1 700 mm long to permit a wheelchair to enter from a side approach and 1 350 mm long where the wheelchair enters from the front or rear of the space,

c)   they shall be arranged so that

i)   at least two designated spaces are located side by side, and

ii)   at least one fixed seat is located beside each designated space,

d)   they shall be located adjoining an accessible path of travel without infringing on egress from any row of seating or any aisle requirements, and

e)   they shall be situated, as part of the designated seating plan, to provide a choice of viewing location and a clear view of the event taking place.

(See Note A-3.8.2.3.(5) and (6) and 3.8.3.22.(1) and (4).)

2)   Spaces designated for wheelchair use in waiting rooms or areas as required by Sentence 3.8.2.3.(4) shall

a)   be clear and level, and

b)   comply with Clauses (1)(b) and (d).

3)   Adaptable seats required by Sentence 3.8.2.3.(5) shall

a)   be located adjoining an aisle without infringing on egress from any row of seating or any aisle requirements,

b)   be equipped with a movable or removable armrest on the side of the seat adjoining the aisle, and

c)   be situated, as part of the designated seating plan, to provide a choice of viewing location and a clear view of the event taking place.

4)   Storage spaces for mobility aids shall be provided in a location

a)   that is on the same level as and in proximity to the adaptable seats required by Sentence 3.8.2.3.(5),

b)   that is within the room side of the fire separation required by Article 3.3.2.2., and

c)   where they will not infringe on egress.

(See Notes A-3.8.3.22.(4) and A-3.8.2.3.(5) and (6) and 3.8.3.22.(1) and (4).)

3.8.3.23. Sleeping Rooms and Bed Spaces

1)   Sleeping rooms and bed spaces required by Sentence 3.8.2.13.(1) to be accessible shall have

a)   a clear floor space that permits a turning area of not less than 1 700 mm in diameter, or not less than 1 700 mm by 1 500 mm, that could be adjacent a bed,

b)   a pathway clearance of not less than 1 000 mm wide, that could be unobstructed by a bed, to allow functional use of the bedroom,

c)   at least one closet that provides

i)   a clear opening width of not less than 900 mm,

ii)   a clear floor space, that need not be separate from the turning areas required in Clause (a), of not less than 1 700 mm by 1 500 mm on at least one side of the closet (see Note A-3.8.5.6.(1))

iii)   clothes hanger rods capable of being lowered to a height of not more than 1 200 mm, and

iv)   at least one shelf capable of being lowered to a height of not more than 1 200 mm,

d)   when a balcony is provided, an accessible path of travel to an accessible balcony conforming to Sentence 3.3.1.7.(4),

e) except for dedicated electrical outlets for equipment and appliances, where controls, switches and outlets are intended for frequent operation, they shall conform to Subsection 3.8.3., and

f)   a bathroom, where provided as part of the sleeping room or bed space, or access to a bathroom, where not provided as part of the sleeping room or bed space

i)   conforming to Clauses 3.8.3.12.(1)(a), (b), (e), (f), (g), (h) and (i) with a water closet conforming to Article 3.8.3.14.,

ii)   provided with a lavatory and mirror conforming to Article 3.8.3.16., and

iv)   provided with a shower conforming to Article 3.8.3.17. or a bathtub conforming to Article 3.8.3.18., only to the extent of providing the same type of facilities provided in sleeping rooms and bed spaces where access is not required.

3.8.4. Alterations and Additions to Existing Buildings

3.8.4.1. Application

1)   Except as provided in Sentence (2), access as described in Articles 3.8.4.2. to 3.8.4.8. shall be provided

a)   to additions to existing buildings where such additions have internal path of travel connections with the existing buildings,

b)   to existing parts of buildings to which additions described in Clause (a) are made, and

c)   to the extent required by Article 3.8.4.5., to existing buildings

i)   where the occupancy is changed, or

ii)    that are altered or renovated.

2)   This Subsection does not apply to

a)   buildings of new construction,

b)   vertical additions of one storey not more than 600 m2 in floor area regardless of occupancy, or

c)   horizontal or vertical additions to occupancies described in Clauses 3.8.2.1.(1)(a) to (c).

3.8.4.2. Specific Requirements

1)   Exterior access shall be provided to an addition except where access to the addition is provided by way of the existing building.

2)   Walks and ramps for an addition shall conform to Subsection 3.8.3.

3)   An entrance to an addition shall be accessible except where

a)   the addition is accessible by an accessible path of travel from an accessible entrance serving the existing building, and

b)   not less than 50% of the pedestrian entrances to the building are accessible.

3.8.4.3. Vertical Additions

1)   Where there is a vertical addition of one storey and of more than 600 m² in floor area, or of two or more storeys regardless of floor area,

a)   access shall be provided to all additional storeys, and

b)   the additional storeys shall conform to Subsections 3.8.2. and 3.8.3.

3.8.4.4. Horizontal Additions

1)   Where an existing building is extended horizontally, the requirements of Subsections 3.8.2. and 3.8.3. shall be applied to the addition except as described in Articles 3.8.4.2. and 3.8.4.6., and Sentence 3.8.4.8.(2).

3.8.4.5. Alterations and Occupancy Change

1)   Where an existing building is altered or renovated, or where the occupancy is changed, access shall be provided in conformance with Subsections 3.8.2. and 3.8.3. where providing such access would be practical.

3.8.4.6. Sleeping Rooms and Bed Spaces

1)   Where sleeping rooms or bed spaces are provided in an addition, the percentage of accessible sleeping rooms or bed spaces required by Subsection 3.8.2. to conform to Article 3.8.3.23. shall be based on the sum of sleeping rooms or bed spaces in the addition and in the existing building.

2)   The accessible sleeping rooms or bed spaces required by Sentence (1) may be distributed between the addition and the existing building.

3.8.4.7. Existing Facilities

1)   Where an addition is required to be accessible, facilities located in the existing building that are necessary to the operation of the addition shall be accessible.

2) Where alterations are made to an existing building, universal washrooms complying with Subsection 3.8.3. are permitted to be provided in lieu of facilities for persons with disabilities in washrooms. (See Note A-3.8.2.8.(1) to (3).)

3.8.4.8. Egress from Floor Areas

1)   The egress requirements of Article 3.3.1.7. shall apply to the vertical additions described in Sentence 3.8.4.3.(1).

2)   Where an existing storey is extended horizontally and the building is not sprinklered throughout, the protection requirements of Article 3.3.1.7. shall apply to

a)   the extended portion of the storey, or

b)   the combined area of the existing storey and the extension.

3.8.5. Adaptable Dwelling Units

3.8.5.1. Application

1)   Except as provided in Sentence (2), this Subsection applies to

a)   one storey dwelling units served by an accessible interior public corridor and an accessible common building entrance, as required to be accessible by Articles 3.8.2.2. and 3.8.2.3., and

b)   common spaces and facilities intended for use by the residents of the dwelling units described in Clause (a) including common rooftop occupancies.

2)   Buildings described in Clause 3.8.2.1.(1)(a) including secondary suites and all other dwelling units to which this Section applies shall, as required by Sections 3.7. and 9.31., provide at least one bathroom with walls reinforced in accordance with Clause 3.8.5.7.(1)(e).

3.8.5.2. Construction Requirements

1)   The construction of adaptable dwelling units and the building in which they are located shall conform to the requirements of this Subsection and, as required by this Subsection, to access requirements for buildings of residential occupancy elsewhere in this Code.

2)   Unless otherwise required, clear areas and spaces required in this Subsection are permitted to overlap with other clear area and space requirements.

3)   This Subsection does not require an adaptable dwelling unit be provided with a living space, a bedroom, a bathroom or a kitchen, but when provided, those spaces and the paths connecting them shall conform to the applicable requirements of this Subsection.

3.8.5.3. Building Access Requirements

1)   Common areas, spaces and facilities and all common exterior and interior paths of travel serving adaptable dwelling units shall be accessible in accordance with Subsection 3.8.2. with floor areas protected in conformance with Article 3.3.1.7.

2)   Common corridors and passageways serving adaptable dwelling units shall be equipped to provide illumination, measured at floor or tread level, of not less than 50 lx.

3)   Each adaptable dwelling unit shall be provided with special outlet boxes and cover plates as described in Sentences 3.2.4.19.(7).

4)   Unless otherwise required by this Section, common spaces and paths of travel that are not intended to serve the residents of adaptable dwelling units need not be accessible.

3.8.5.4. Adaptable Dwelling Unit Doorways

1)   The principal entrance door to adaptable dwelling units shall have a clear width of not less than 850 mm when the door is in the open position. (See Note 3.8.5.4.(1))

2) Except as provided in Sentence (5), there shall be a clear floor space in accordance with Sentences 3.8.3.6.(14) and (15) adjacent to and on both sides of the adaptable dwelling unit entrance door described in Sentence (1).

3)   Within an adaptable dwelling unit, every doorway along a path of travel connecting the entrance door described in Sentence (1) with a living space, adaptable bedroom, adaptable bathroom, and adaptable kitchen shall have a clear width of not less than 850 mm when the door is in the open position.

4)   Except as provided in Sentence (5), there shall be a clear floor space in accordance with Sentences 3.8.3.6.(14) and (15) adjacent to and on both sides of the doorways described in Sentence (3).

5)   Doorways provided with power door operators, or provided with a special outlet box and cover plates that are designed, located and wired specifically to accommodate the future installation of a power door operator, may provide the clear floor space described in Sentence 3.8.3.6.(16).

3.8.5.5. Adaptable Dwelling Unit Hallways and Corridors

1)   Hallways and corridors in adaptable dwelling units forming a path of travel connecting the entrance door described in Sentence 3.8.5.4.(1) with a living space, adaptable bedroom, adaptable bathroom and adaptable kitchen shall have a clear width conforming to Sentences 3.8.3.2.(1) and (2).

3.8.5.6. Adaptable Dwelling Unit Bedrooms

1)   At least one bedroom or sleeping space in an adaptable dwelling unit shall have

a)   a floor area that permits a turning area of not less than 1 700 mm in diameter, or not less than 1 700 mm by 1 500 mm, that could be adjacent a bed,

b)   a pathway clearance of not less than 850 mm wide, that could be unobstructed by a bed, to allow functional use of the bedroom, and

c)   at least one closet that provides

i)   a clear opening width of not less than 900 mm, and

ii)   a clear floor space, that need not be separate from the turning areas required in Clause (a), of not less than 1 700 mm in diameter or 1 700 mm by 1 500 mm on at least one side of the closet. (See Note A-3.8.5.6.(1).)

3.8.5.7. Adaptable Dwelling Unit Bathrooms

1)   At least one bathroom in an adaptable dwelling unit shall be designed to be adaptable for use by persons with disabilities by providing

a)   a clear lateral transfer space adjacent a water closet conforming to Clause 3.8.3.12.(1)(b),

b)   a distance between the centre line of the water closet and the wall on one side of 460 mm to 480 mm,

c)   a plumbing system that accommodates the future installation of a lavatory with a clear space in accordance with Clauses 3.8.3.16.(1)(a) to (f) that does not impede the space for or use of other fixtures described in this Article (see Note A-3.8.5.7.(1)(c) and (d)),

d)   a plumbing system that accommodates the future installation of a

i)   shower described in Sentence 3.8.3.17.(1) that does not impede the space for or use of other fixtures described in this Article, or

ii)   bathtub described in Sentence 3.8.3.18.(1) that does not impede the space for or use of other fixtures described in this Article (see Note A-3.8.5.7.(1)(c) and (d)), and

e)   walls adjacent the water closet and shower or bathtub location reinforced to accommodate the future installation of grab bars conforming to

i)   Clauses 3.8.3.12.(1)(f) and (g) for water closets, and

ii)   Clause 3.8.3.17.(1)(f) for showers or Clauses 3.8.3.18.(1)(f) for bathtubs (see Note A-3.8.5.7.(1)(e)).

3.8.5.8. Adaptable Dwelling Unit Kitchens

1)   The kitchen in an adaptable dwelling unit shall be designed so that the cooktop and sink are adjacent or can have a continuous counter between them.

2)   A clear floor space shall be provided in the kitchen area that is not less than 1 700 mm in diameter or 1 700 mm by 1 500 mm.

3)   The plumbing system serving the kitchen shall accommodate the future installation of a kitchen sink that could be installed in accordance with the requirements for the installation of a lavatory as described in Clauses 3.8.3.16.(1)(b) to (f). (See Note A-3.8.5.7.(1)(c) and (d).)

3.8.5.9. Controls, Switches and Outlets

1)   Except as provided in Sentence (2), controls and switches for building systems and outlets in adaptable dwelling units, that are intended for frequent operation by occupants, shall not require activities for operation below 400 mm from the floor or above 1 200 mm from the floor.

2)   Sentence (1) does not apply to controls, switches and dedicated outlets for equipment or appliances.

Section  3.9.   Self-service Storage Buildings

3.9.1. General

3.9.1.1. Definition

1)   For the purpose of this Section, the term “self-service storage building” shall mean a building that is open to the public for the sole purpose of providing individual self-service storage units.

3.9.1.2. Application

1)   This Section applies to self-service storage buildings that

a)   are not more than one storey in building height,

b)   do not contain a basement or mezzanine,

c)   consist of individual self-service storage units with external access only,

d)   are used for no purpose other than storage, and

e)   except as provided in Sentences 3.9.3.1.(2) and (4), contain no other major occupancy.

2)   Where there is a conflict between the requirements of this Section and other requirements in Part 3, this Section shall govern.

3)   The requirements in Part 3 regarding occupant load shall not apply to self-service storage buildings.

3.9.1.3. Occupancy Classification

1)   Self-service storage buildings shall be classified as Group F, Division 2 major occupancies.

3.9.2. Building Fire Safety

3.9.2.1. Building Area

1)   For the purpose of applying the requirements of Subsections 3.2.1. and 3.2.2. to self-service storage buildings, building area shall mean

a)   the building area of each building, or

b)   the total of the building areas of all buildings as a group.

(See Note A-3.9.2.1.(1).)

3.9.2.2. Spatial Separation

(See Note A-3.9.2.2.)

1)   Except as provided in Sentence (3), the spatial separation requirements in Subsection 3.2.3. shall apply to self-service storage buildings.

2)   The distance between each group of self-service storage buildings shall be not less than 9 m.

3)   Subsection 3.2.3. need not apply between buildings within a group of self-service storage buildings, where the distance between these buildings is at least 6 m.

3.9.2.3. Access Route

1)   Where Clause 3.9.2.1.(1)(b) is applied to a group of buildings, Article 3.2.5.4. and Sentence 3.2.5.5.(1) shall apply to that group of buildings as if they were a single building.

3.9.3. Floor Areas

3.9.3.1. Safety Requirements Within Floor Areas

1)   Except as provided in Sentences (2) to (6), the requirements of Section 3.3. shall apply. (See Note A-3.9.3.1.(1).)

2)   Not more than one dwelling unit is permitted to be contained within one of the self-service storage buildings on a property.

3)   A dwelling unit referred to in Sentence (2) shall be separated from individual self-service storage units by a fire separation having a fire-resistance rating not less than 2 h.

4)   Where an office not more than 50 m2 in area is adjacent to a dwelling unit referred to in Sentence (2), it shall be considered as part of the dwelling unit.

5)   Fire separations required by Sentences 3.3.1.1.(1) and 3.3.5.9.(1) need not be provided between individual self-service storage units.

6)   The floor area of self-service storage buildings shall be

a)   subdivided into compartments not more than 500 m2 in area by a fire separation having a fire-resistance rating not less than 1 h, or

b)   sprinklered.

(See also Sentence 3.4.6.12.(2) for the exemption applying to exit doors of individual self-service storage units.)

3.9.3.2. Sanitary Facilities

1)   Except as provided in Sentence 3.7.2.1.(3), two public washrooms, each containing a water closet and a lavatory, shall be provided within one of the self-service storage buildings on the property. (See Note A-3.9.3.2.(1).)

Section  3.10.   Objectives and Functional Statements

3.10.1. Objectives and Functional Statements

3.10.1.1. Attributions to Acceptable Solutions

1)   For the purpose of compliance with this Code as required in Clause 1.2.1.1.(1)(b) of Division A, the objectives and functional statements attributed to the acceptable solutions in this Part shall be the objectives and functional statements listed in Table 3.10.1.1. (See Note A-1.1.2.1.(1).)

Table 3.10.1.1.

Objectives and Functional Statements Attributed to the Acceptable Solutions in Part 3

Forming Part of Sentence 3.10.1.1.(1)

| Provision | Functional Statements and Objectives(1) |
| --- | --- |
| 3.1.3.1. Separation of Major Occupancies |  |
| (1) | [F03-OS1.2] |
|  | [F03-OP1.2] |
| (2) | [F03-OS1.2] |
| (3) | [F02,F03,F06-OS1.2] [F10,F05-OS1.5] |
|  | [F02,F03,F06-OP1.2] |
| 3.1.3.2. Prohibition of Occupancy Combinations |  |
| (1) | [F02,F03-OS1.2] [F10-OS1.5] |
| (2) | [F02,F03-OS1.2] |
| 3.1.4.1. Combustible Materials Permitted |  |
| (2) | [F02-OS1.2] |
|  | [F02-OP1.2] |
| 3.1.4.2. Protection of Foamed Plastics |  |
| (1) | [F01-OS1.1] [F02-OS1.2] |
|  | [F01-OP1.1] [F02-OP1.2] |
| (2) | [F01-OS1.1] [F02-OS1.2] |
|  | [F01-OP1.1] [F02-OP1.2] |
| 3.1.4.3. Wires and Cables |  |
| (1) | [F02-OS1.2] |
|  | [F02-OP1.2] |
| (2) | [F02-OS1.2] |
|  | [F02-OP1.2] |
| (3) | [F02-OS1.2] |
|  | [F02-OP1.2] |
| 3.1.4.5. Fire-Retardant-Treated Wood |  |
| (1) | [F02-OS1.2] |
|  | [F02-OP1.2] |
| 3.1.4.8. Exterior Cladding |  |
| (1) | [F02,F03-OP3.1] |
| (2) | [F02,F03-OP3.1] |
| 3.1.5.1. Noncombustible Materials |  |
| (1) | [F02-OS1.2] |
|  | [F02-OP1.2] |
| 3.1.5.5. Combustible Cladding on Exterior Walls |  |
| (2) | [F03,F02-OP3.1] |
| 3.1.5.21. Wires and Cables |  |
| (2) | [F02-OS1.2] |
|  | [F02-OP1.2] |
| (3) | [F02-OS1.2] |
|  | [F02-OP1.2] |
| 3.1.5.23. Non-metallic Raceways |  |
| (1) | [F02-OS1.2] |
|  | [F02-OP1.2] |
| (2) | [F02-OS1.2] |
|  | [F02-OP1.2] |
| 3.1.6.2. Materials Permitted |  |
| (1) | [F02-OS1.2] |
|  | [F02-OP1.2] |
| 3.1.6.3. Structural Mass Timber Elements |  |
| (2) | [F04-OS1.3] |
|  | [F04-OP1.3] |
| (3) | [F02-OS1.2] |
|  | [F02-OP1.2] |
| 3.1.6.4. Encapsulation of Mass Timber Elements |  |
| (1) | [F02-OS1.2] |
|  | [F02-OP1.2] |
| (2) | [F02-OS1.2] |
|  | [F02-OP1.2] |
| 3.1.6.5. Determination of Encapsulation Ratings |  |
| (1) | [F02-OS1.2] |
|  | [F04-OS1.3] |
|  | [F02-OP1.2] |
|  | [F04-OP1.3] |
| 3.1.6.9. Exterior Cladding |  |
| (1) | [F02-OS1.2] |
|  | [F02-OP1.2] |
| (5) | [F02,F03-OP3.1] |
| (7) | [F03-OS1.2] |
|  | [F03-OP1.2] |
| 3.1.6.17. Penetration by Outlet Boxes |  |
| (3) | [F03-OS1.2] |
|  | [F03-OP1.2] |
| 3.1.7.1. Determination of Ratings |  |
| (1) | [F03-OS1.2] [F04-OS1.3] |
|  | [F03-OP1.2] [F04-OP1.3] |
| 3.1.7.5. Rating of Supporting Construction |  |
| (1) | [F04-OS1.3] |
|  | [F04-OP1.3] |
| (3) | [F04-OS1.3] |
|  | [F04-OP1.3] |
| 3.1.8.1. General Requirements |  |
| (1) | (a) [F03-OS1.2] |
|  | (a) [F03-OP1.2] |
| (2) | [F03-OS1.2] Applies to the requirement that openings in fire separations be protected with closures, shafts or other means. |
|  | [F03-OP1.2] Applies to the requirement that openings in fire separations be protected with closures, shafts or other means. |
| 3.1.8.2. Combustible Construction Support |  |
| (1) | [F04-OS1.2] |
|  | [F04-OP1.2] |
| 3.1.8.3. Continuity of Fire Separations |  |
| (1) | [F03-OS1.2] |
|  | [F03-OP1.2] |
| (2) | [F03-OS1.2] |
|  | [F03-OP1.2] |
| (3) | [F03-OS1.2] |
|  | [F03-OP1.2] |
| (4) | [F03-OS1.2] |
|  | [F03-OP1.2] |
| 3.1.8.4. Determination of Ratings and Classifications |  |
| (1) | [F03-OS1.2] |
|  | [F03-OP1.2] |
| (2) | [F03-OS1.2] |
|  | [F03-OP1.2] |
| (3) | [F03-OS1.2] |
|  | [F03-OP1.2] |
| (4) | [F03-OS1.2] |
|  | [F03-OP1.2] |
| 3.1.8.5. Installation of Closures |  |
| (2) | [F03-OS1.2] |
|  | [F03-OP1.2] |
| (3) | [F03-OS1.2] |
|  | [F03-OP1.2] |
| (4) | [F81-OS1.2] |
|  | [F81-OP1.2] |
| (5) | [F81-OP1.2] |
|  | [F81-OS1.2] |
| (6) | [F03-OS1.2] |
|  | [F03-OP1.2] |
| (7) | [F03-OS1.2] |
|  | [F03-OP1.2] |
| 3.1.8.6. Maximum Openings |  |
| (1) | [F03-OS1.2] |
|  | [F03-OP1.2] |
| (2) | [F03-OS1.2] |
|  | [F03-OP1.2] |
| 3.1.8.7. Location of Fire Dampers and Smoke Dampers |  |
| (1) | [F03-OS1.2] |
|  | [F03-OP1.2] |
| (2) | [F03-OS1.2] |
|  | [F03-OP1.2] |
| 3.1.8.10. Installation of Fire Dampers |  |
| (1) | [F04-OS1.2] |
|  | [F04-OP1.2] |
| (2) | [F03-OS1.2] |
|  | [F03-OP1.2] |
| (3) | [F03-OS1.2] |
|  | [F03-OP1.2] |
| (4) | [F03-OS1.2] |
|  | [F03-OP1.2] |
| (5) | [F82-OS1.2] Applies to portion of Code text: “A tightly fitted access door shall be installed for each fire damper to provide access for the inspection of the damper …” |
|  | [F82-OP1.2] Applies to portion of Code text: “A tightly fitted access door shall be installed for each fire damper to provide access for the inspection of the damper …” |
|  | [F82-OH1.2] Applies to portion of Code text: “A tightly fitted access door shall be installed for each fire damper to provide access for … the resetting of the release device.” |
| 3.1.8.11. Installation of Smoke Dampers |  |
| (1) | [F03-OS1.2] |
|  | [F03-OP1.2] |
| (2) | [F03-OS1.2] |
|  | [F03-OP1.2] |
| (3) | [F03-OS1.2] |
|  | [F03-OP1.2] |
| (4) | [F03-OS1.2] |
|  | [F03-OP1.2] |
| (5) | [F82-OS1.2] Applies to portion of Code text: “A tightly fitted access door shall be installed for each smoke damper ... to provide access for ... inspection …” |
|  | [F82-OH1.2] Applies to portion of Code text: “A tightly fitted access door shall be installed for each smoke damper ... to provide access for ... inspection …” |
|  | [F82-OP1.2] Applies to portion of Code text: “A tightly fitted access door shall be installed for each ... fire damper to provide access for … the resetting of the release device.” |
| 3.1.8.12. Twenty-Minute Closures |  |
| (3) | [F03-OS1.2] |
|  | [F03-OP1.2] |
| 3.1.8.13. Self-closing Devices |  |
| (1) | [F03-OS1.2] |
|  | [F03-OP1.2] |
| 3.1.8.14. Hold-Open Devices |  |
| (1) | [F03-OS1.2] |
| (2) | [F03-OS1.2] |
|  | [F03-OP1.2] |
| (3) | [F03-OS1.2] |
|  | [F03-OP1.2] |
| (4) | [F03-OS1.2] |
|  | [F03-OP1.2] |
| (5) | [F03-OS1.2] |
|  | [F03-OP1.2] |
| 3.1.8.15. Door Latches |  |
| (1) | [F03-OS1.2] |
|  | [F03-OP1.2] |
| 3.1.8.16. Wired Glass and Glass Block |  |
| (3) | [F04-OS1.2] Applies to portion of Code text: “Glass blocks permitted by Sentence (1) shall be … reinforced with steel reinforcement in each horizontal joint.” |
|  | [F04-OP1.2] Applies to portion of Code text: “Glass blocks permitted by Sentence (1) shall be … reinforced with steel reinforcement in each horizontal joint.” |
| 3.1.8.17. Temperature Rise Limit for Doors |  |
| (1) | [F03,F31-OS1.2] [F05-OS1.5] |
|  | [F03-OP1.2] |
| 3.1.8.18. Area Limits for Wired Glass, Glass Block and Safety Glazing |  |
| (1) | [F05-OS1.5] [F31-OS1.2] |
|  | [F30-OS3.1] |
| (2) | [F05-OS1.5] [F31-OS1.2] |
| 3.1.9.1. Firestops |  |
| (1) | [F03-OS1.2] [F04-OS1.3] |
|  | [F03-OP1.2] [F04-OP1.3] |
| (2) | [F03-OS1.2] |
|  | [F03-OP3.1] |
|  | [F03-OP1.2] |
| (3) | [F03-OS1.2] |
|  | [F03-OP1.2] |
| (6) | [F03-OS1.2] |
|  | [F03-OP1.2] |
| (7) | [F03-OS1.2] |
|  | [F03-OP1.2] |
| 3.1.9.3. Penetration by Outlet Boxes |  |
| (1) | [F03-OS1.2] |
|  | [F03-OP1.2] |
| (2) | [F03-OS1.2] |
|  | [F03-OP1.2] |
| (4) | [F03-OS1.2] |
|  | [F03-OP1.2] |
| 3.1.9.4. Combustible Piping Penetrations |  |
| (3) | [F03-OS1.2] [F02,F04-OS1.3] |
|  | [F03-OP1.2] [F02,F04-OP1.3] |
| (7) | [F03-OS1.2] [F02-OS1.3] [F04-OS1.3] |
|  | [F03-OP1.2] [F02-OP1.3] [F04-OP1.3] |
| 3.1.9.5. Openings through a Membrane Ceiling |  |
| (1) | [F04-OS1.3] |
|  | [F04-OP1.3] |
| 3.1.10.1. Prevention of Firewall Collapse |  |
| (1) | [F04-OP1.2] |
|  | [F04-OS1.2] |
|  | [F04-OP3.1] |
| (2) | [F03,F04-OP1.2] |
|  | [F03,F04-OS1.2] |
|  | [F03,F04-OP3.1] |
| (4) | [F04-OS1.2] |
|  | [F04-OP1.2] |
|  | [F04-OP3.1] |
| 3.1.10.2. Rating of Firewalls |  |
| (1) | [F03-OS1.2] Applies to portion of Code text: “A firewall that separates a building or buildings with floor areas containing a Group E or a Group F, Division 1 or 2 major occupancy shall be constructed as a fire separation of noncombustible construction having a fire-resistance rating not less than 4 h …” |
|  | [F03-OP1.2] Applies to portion of Code text: “A firewall that separates a building or buildings with floor areas containing a Group E or a Group F, Division 1 or 2 major occupancy shall be constructed as a fire separation of noncombustible construction having a fire-resistance rating not less than 4 h …” |
|  | [F03-OP3.1] Applies to portion of Code text: “A firewall that separates a building or buildings with floor areas containing a Group E or a Group F, Division 1 or 2 major occupancy shall be constructed as a fire separation of noncombustible construction having a fire-resistance rating not less than 4 h …” |
| (2) | [F03-OS1.2] |
|  | [F03-OP1.2] |
|  | [F03-OP3.1] |
| (3) | [F80,F04-OP1.2] |
|  | [F80,F04-OS1.2] |
|  | [F80,F04-OP1.3] |
| (4) | [F80,F04-OP1.2] |
|  | [F80,F04-OS1.2] |
|  | [F80,F04-OP3.1] |
| 3.1.10.3. Continuity of Firewalls |  |
| (1) | [F03-OS1.2] Applies to portion of Code text: “A firewall shall extend from the ground continuously through, or adjacent to, all storeys of a building or buildings so separated …” |
|  | [F03-OP1.2] Applies to portion of Code text: “A firewall shall extend from the ground continuously through, or adjacent to, all storeys of a building or buildings so separated …” |
|  | [F03-OP3.1] Applies to portion of Code text: “A firewall shall extend from the ground continuously through, or adjacent to, all storeys of a building or buildings so separated …” |
| 3.1.10.4. Parapets |  |
| (1) | [F03-OP1.2] |
|  | [F03-OS1.2] |
|  | [F03-OP3.1] |
| 3.1.10.5. Maximum Openings |  |
| (2) | [F03-OP1.2] |
|  | [F03-OS1.2] |
|  | [F03-OP3.1] |
| 3.1.10.7. Combustible Projections |  |
| (1) | [F03-OP1.2] Applies to portion of Code text: “Combustible material shall not extend across the end of a firewall …” |
|  | [F03-OS1.2] Applies to portion of Code text: “Combustible material shall not extend across the end of a firewall …” |
|  | [F03-OP3.1] Applies to portion of Code text: “Combustible material shall not extend across the end of a firewall …” |
| (2) | [F03-OS1.2] |
|  | [F03-OP1.2] |
|  | [F03-OP3.1] |
| 3.1.11.1. Separation of Concealed Spaces |  |
| (1) | [F03-OS1.2] |
|  | [F03-OP1.2] |
| 3.1.11.2. Fire Blocks in Wall Assemblies |  |
| (1) | [F03-OS1.2] |
|  | [F03-OP1.2] |
| 3.1.11.3. Fire Blocks between Nailing and Supporting Elements |  |
| (1) | [F03-OS1.2] |
|  | [F03-OP1.2] |
| (2) | [F03-OS1.2] |
|  | [F03-OP1.2] |
| (3) | [F03-OS1.2] |
|  | [F03-OP1.2] |
| (4) | [F03-OS1.2] |
|  | [F03-OP1.2] |
| 3.1.11.4. Fire Blocks between Vertical and Horizontal Spaces |  |
| (1) | [F03-OS1.2] |
|  | [F03-OP1.2] |
| 3.1.11.5. Fire Blocks in Horizontal Concealed Spaces |  |
| (1) | [F03,F04-OS1.2] |
|  | [F03,F04-OP1.2] |
| (2) | [F03,F04-OS1.2] |
|  | [F03,F04-OP1.2] |
| (3) | [F02,F03-OP1.2] [F04-OP1.3] |
|  | [F02,F03-OS1.2] [F04-OS1.3] |
| (4) | [F02,F03-OS1.2] |
|  | [F04-OS1.3] |
|  | [F02,F03-OP1.2] |
|  | [F04-OP1.3] |
| 3.1.11.6. Fire Blocks in Crawl Spaces |  |
| (1) | [F03,F04-OS1.2] |
|  | [F03,F04-OP1.2] |
| 3.1.11.7. Fire Block Materials |  |
| (1) | [F04-OS1.2] |
|  | [F04-OP1.2] |
| (6) | [F04-OP1.2] |
|  | [F04-OS1.2] |
| (7) | [F03-OP1.2] |
|  | [F03-OS1.2] |
| 3.1.12.1. Determination of Ratings |  |
| (1) | [F02-OS1.2] |
|  | [F02-OP1.2] |
| (2) | [F02-OS1.2] |
|  | [F02-OP1.2] |
| 3.1.13.2. Flame-Spread Rating |  |
| (1) | [F02-OS1.2] |
|  | [F02-OP1.2] |
| 3.1.13.5. Skylights |  |
| (1) | [F02-OS1.5] |
| 3.1.13.6. Corridors |  |
| (1) | [F02-OS1.2,OS1.5] |
|  | [F02-OP1.2] |
| (5) | [F02-OS1.2,OS1.5] |
|  | [F02-OP1.2] |
| (6) | [F02-OS1.2] |
|  | [F02-OP1.2] |
| 3.1.13.7. High Buildings |  |
| (1) | [F02-OS1.2] |
|  | [F02-OP1.2] |
| 3.1.13.9. Underground Walkways |  |
| (1) | [F02-OS1.2] |
|  | [F02-OP3.1] |
| 3.1.13.10. Exterior Exit Passageway |  |
| (1) | [F02-OS1.5] |
| 3.1.13.11. Elevator Cars |  |
| (1) | [F02-OS1.2] |
|  | [F02-OP1.2] |
| (2) | [F02-OS1.2] |
|  | [F02-OP1.2] |
| 3.1.14.1. Fire-Retardant-Treated Wood Roof Systems |  |
| (1) | [F02-OS1.2] |
|  | [F02-OP1.2] |
| (2) | [F02-OS1.3,OS1.2] |
|  | [F02-OP1.3] |
| 3.1.14.2. Metal Roof Deck Assemblies |  |
| (1) | [F02-OS1.2] |
|  | [F02-OP1.2] |
| 3.1.15.1. Roof Covering Classification |  |
| (1) | [F02-OS1.2] |
|  | [F02-OP1.2] |
|  | [F02-OP3.1] |
| 3.1.15.2. Roof Coverings |  |
| (1) | [F02-OS1.2] |
|  | [F02-OP1.2] |
|  | [F02-OP3.1] |
| (3) | [F02-OS1.2] |
|  | [F02-OP1.2] |
|  | [F02-OP3.1] |
| (4) | [F02-OS1.2] |
|  | [F02-OP1.2] |
|  | [F02-OP3.1] |
| 3.1.16.1. Fabric Canopies and Marquees |  |
| (1) | [F02-OS1.2,OS1.5] |
|  | [F02-OP1.2] |
| 3.1.17.1. Occupant Load Determination |  |
| (1) | [F10-OS3.7] |
|  | [F72-OH2.1] [F71-OH2.3] |
| (2) | [F10-OS3.7] |
|  | [F72-OH2.1] [F71-OH2.3] |
| (4) | [F10-OS3.7] |
|  | [F72-OH2.1] [F71-OH2.3] |
| 3.1.18.2. Restrictions |  |
| (1) | [F10,F12,F36-OS3.7] |
|  | [F20-OS2.2] |
| (2) | [F10,F36-OS3.7] Applies to portion of Code text: “An air-supported structure shall not be used for Groups B, C, … major occupancies or for classrooms.” |
|  | [F01,F02,F36-OS1.5] Applies to portion of Code text: “An air-supported structure shall not be used for … Group F, Division 1 major occupancies …” |
| (3) | [F10-OS3.7] |
| 3.1.18.3. Clearance to Other Structures |  |
| (2) | (a) [F03-OS1.2] |
|  | (b) [F10-OS3.7] |
|  | (a) [F03-OP3.1] |
| 3.1.18.4. Clearance to Flammable Material |  |
| (1) | [F01-OS1.1] [F03-OS1.2] |
|  | [F01-OP1.1] [F03-OP1.2] |
| 3.1.18.5. Flame Resistance |  |
| (1) | [F02-OS1.2] |
| 3.1.18.6. Emergency Air Supply |  |
| (1) | [F20-OS3.7] |
| 3.1.18.7. Electrical Systems |  |
| (1) | [F34-OP1.1] |
|  | [F34-OS3.3] |
|  | [F34-OS1.1] |
| (2) | [F81-OP1.1] |
|  | [F81-OS1.1] |
| 3.2.1.2. Storage Garage Considered as a Separate Building |  |
| (1) | [F03-OS1.2] |
|  | [F03-OP1.2] |
| (2) | [F03-OS1.2] |
|  | [F03-OP1.2] |
| (3) | [F03-OS1.2] |
|  | [F03-OP1.2] |
| 3.2.1.4. Floor Assembly over Basement |  |
| (1) | [F03-OS1.2] [F04-OS1.3] |
|  | [F03-OP1.2] [F04-OP1.3] |
| (2) | [F04-OS1.2,OS1.3] |
|  | [F04-OP1.2,OP1.3] |
| 3.2.1.5. Fire Containment in Basements |  |
| (1) | [F02-OS1.2,OS1.3] |
|  | [F02-OP1.2,OP1.3] |
| 3.2.2.2. Special and Unusual Structures |  |
| (1) | [F02,F03,F04-OS1.2,OS1.3] |
|  | [F02,F03,F04-OP1.2,OP1.3] |
| 3.2.2.6. Multiple Major Occupancies |  |
| (1) | [F02,F03,F04-OS1.2,OS1.3] |
|  | [F02,F03,F04-OP1.2,OP1.3] |
| 3.2.2.10. Streets |  |
| (1) | [F12-OS1.2,OS1.5] |
|  | [F12-OP1.2] |
| 3.2.2.15. Storeys below Ground |  |
| (2) | (a) [F02,F04-OS1.2,OS1.3] |
|  | (a) [F02,F04-OP1.2,OP1.3] |
|  | (b),(c) [F03-OS1.2] [F04-OS1.2,OS1.3] |
|  | (b),(c) [F03-OP1.2] [F04-OP1.2,OP1.3] |
| 3.2.2.18. Automatic Sprinkler System Required |  |
| (2) | [F02,F04-OS1.2,OS1.3] |
|  | [F02,F04-OP1.2,OP1.3] |
| 3.2.2.20. Group A, Division 1, Any Height, Any Area, Sprinklered |  |
| (2) | [F02-OS1.2] Applies to portion of Code text: “… the building referred to in Sentence (1) shall be of noncombustible construction …” |
|  | [F02-OP1.2] Applies to portion of Code text: “… the building referred to in Sentence (1) shall be of noncombustible construction …” |
|  | (a) [F02,F04-OS1.2,OS1.3] Applies to portion of Code text: “… the building shall be sprinklered throughout …” |
|  | (a) [F02,F04-OP1.2,OP1.3] Applies to portion of Code text: “… the building shall be sprinklered throughout …” |
|  | (b),(d) [F03-OS1.2] [F04-OS1.2,OS1.3] |
|  | (b),(d) [F03-OP1.2] [F04-OP1.2,OP1.3] |
|  | (c),(d) [F04-OS1.3] |
|  | (c),(d) [F04-OP1.3] |
| 3.2.2.21. Group A, Division 1, One Storey, Limited Area, Sprinklered |  |
| (1) | (a) [F02,F04-OS1.2,OS1.3] Applies to portion of Code text: “… the building is sprinklered throughout …” |
|  | (a) [F02,F04-OP1.2,OP1.3] Applies to portion of Code text: “… the building is sprinklered throughout …” |
| (2) | [F02-OS1.2] Applies to portion of Code text: “The building referred to in Sentence (1) is permitted to be of heavy timber construction or noncombustible construction used singly or in combination …” |
|  | [F02-OP1.2] Applies to portion of Code text: “The building referred to in Sentence (1) is permitted to be of heavy timber construction or noncombustible construction used singly or in combination …” |
|  | [F03-OS1.2] [F04-OS1.2,OS1.3] Applies to portion of Code text: “… (a) floor assemblies shall be fire separations … (a)(i) with a fire-resistance rating not less than 45 min …” and to Clause (b). |
|  | [F03-OP1.2] [F04-OP1.2,OP1.3] Applies to portion of Code text: “… (a) floor assemblies shall be fire separations… (a)(i) with a fire-resistance rating not less than 45 min …” and to Clause (b). |
| 3.2.2.22. Group A, Division 1, One Storey, Sprinklered |  |
| (1) | (a) [F02,F04-OS1.2,OS1.3] Applies to portion of Code text: “… the building is sprinklered throughout …” |
|  | (a) [F02,F04-OP1.2,OP1.3] Applies to portion of Code text: “… the building is sprinklered throughout …” |
| (2) | (a),(d) [F03-OS1.2] [F04-OS1.2,OS1.3] |
|  | (a),(d) [F03-OP1.2] [F04-OP1.2,OP1.3] |
|  | (b),(c) [F04-OS1.3] |
|  | (b),(c) [F04-OP1.3] |
| 3.2.2.23. Group A, Division 2, Any Height, Any Area, Sprinklered |  |
| (2) | [F02-OS1.2] Applies to portion of Code text: “… the building referred to in Sentence (1) shall be of noncombustible construction …” |
|  | [F02-OP1.2] Applies to portion of Code text: “… the building referred to in Sentence (1) shall be of noncombustible construction …” |
|  | (a) [F02,F04-OS1.2,OS1.3] Applies to portion of Code text: “… the building shall be sprinklered throughout …” |
|  | (a) [F02,F04-OP1.2,OP1.3] Applies to portion of Code text: “ … the building shall be sprinklered throughout …” |
|  | (b),(d) [F03-OS1.2] [F04-OS1.2,OS1.3] |
|  | (b),(d) [F03-OP1.2] [F04-OP1.2,OP1.3] |
|  | (c),(d) [F04-OS1.3] |
|  | (c),(d) [F04-OP1.3] |
| 3.2.2.24. Group A, Division 2, up to 6 Storeys, Any Area, Sprinklered |  |
| (1) | (a) [F02,F04-OS1.2,OS1.3] Applies to portion of Code text: “… the building is sprinklered throughout …” |
|  | (a) [F02,F04-OP1.2,OP1.3] Applies to portion of Code text: “… the building is sprinklered throughout …” |
| (2) | [F02-OS1.2] Applies to portion of Code text: “… the building referred to in Sentence (1) shall be of noncombustible construction …” |
|  | [F02-OP1.2] Applies to portion of Code text: “… the building referred to in Sentence (1) shall be of noncombustible construction …” |
|  | (a),(c) [F03-OS1.2] [F04-OS1.2,OS1.3] |
|  | (a),(c) [F03-OP1.2] [F04-OP1.2,OP1.3] |
|  | (b),(c) [F04-OS1.3] |
|  | (b),(c) [F04-OP1.3] |
| 3.2.2.25. Group A, Division 2, up to 2 Storeys |  |
| (2) | [F04-OS1.3] Applies to portion of Code text: “… (c) roof assemblies shall have, if of combustible construction, a fire-resistance rating not less than 45 min, …” and to Clause (d). |
|  | [F04-OP1.3] Applies to portion of Code text: “… (c) roof assemblies shall have, if of combustible construction, a fire-resistance rating not less than 45 min, …” and to Clause (d). |
|  | (a) [F03-OS1.2] Applies to the requirement that noncombustible floor assemblies be fire separations. |
|  | (a) [F03-OP1.2] Applies to the requirement that noncombustible floor assemblies be fire separations. |
|  | (a),(d) [F03-OS1.2] [F04-OS1.2,OS1.3] |
|  | (a),(d) [F03-OP1.2] [F04-OP1.2,OP1.3] |
|  | (b),(d) [F04-OS1.3] |
|  | (b),(d) [F04-OP1.3] |
| 3.2.2.26. Group A, Division 2, up to 2 Storeys, Increased Area, Sprinklered |  |
| (1) | (a) [F02,F04-OS1.2,OS1.3] Applies to portion of Code text: “… the building is sprinklered throughout …” |
|  | (a) [F02,F04-OP1.2,OP1.3] Applies to portion of Code text: “… the building is sprinklered throughout …” |
| (2) | (a) [F03-OS1.2] Applies to the requirement that noncombustible floor assemblies be fire separations. |
|  | (a) [F03-OP1.2] Applies to the requirement that noncombustible floor assemblies be fire separations. |
|  | (a),(c) [F03-OS1.2] [F04-OS1.2,OS1.3] |
|  | (a),(c) [F03-OP1.2] [F04-OP1.2,OP1.3] |
|  | (b),(c) [F04-OS1.3] |
|  | (b),(c) [F04-OP1.3] |
| 3.2.2.27. Group A, Division 2, up to 2 Storeys, Sprinklered |  |
| (1) | (a) [F02,F04-OS1.2,OS1.3] Applies to portion of Code text: “… the building is sprinklered throughout …” |
|  | (a) [F02,F04-OP1.2,OP1.3] Applies to portion of Code text: “… the building is sprinklered throughout …” |
| 3.2.2.28. Group A, Division 2, One Storey |  |
| (2) | [F03-OP1.2] |
|  | [F03-OS1.2] |
| 3.2.2.29. Group A, Division 3, Any Height, Any Area, Sprinklered |  |
| (2) | [F02-OS1.2] Applies to portion of Code text: “… the building referred to in Sentence (1) shall be of noncombustible construction …” |
|  | [F02-OP1.2] Applies to portion of Code text: “… the building referred to in Sentence (1) shall be of noncombustible construction …” |
|  | (a) [F02,F04-OS1.2,OS1.3] Applies to portion of Code text: “… the building shall be sprinklered throughout …” |
|  | (a) [F02,F04-OP1.2,OP1.3] Applies to portion of Code text: “… the building shall be sprinklered throughout …” |
|  | (b),(d) [F03-OS1.2] [F04-OS1.2,OS1.3] |
|  | (b),(d) [F03-OP1.2] [F04-OP1.2,OP1.3] |
|  | (c),(d) [F04-OS1.3] |
|  | (c),(d) [F04-OP1.3] |
| 3.2.2.30. Group A, Division 3, up to 2 Storeys |  |
| (2) | [F02-OS1.2] Applies to portion of Code text: “Except as permitted by Clauses (c) and (d), the building referred to in Sentence (1) shall be of noncombustible construction …” |
|  | [F02-OP1.2] Applies to portion of Code text: “Except as permitted by Clauses (c) and (d), the building referred to in Sentence (1) shall be of noncombustible construction …” |
|  | (a),(d) [F03-OS1.2] [F04-OS1.2,OS1.3] |
|  | (a),(d) [F03-OP1.2] [F04-OP1.2,OP1.3] |
|  | (b),(d) [F04-OS1.3] |
|  | (b),(d) [F04-OP1.3] |
|  | [F04-OS1.3] Applies to portion of Code text: “… (c) roof assemblies shall (c)(i) have a fire-resistance rating not less than 45 min, …” and to Clause (d). |
|  | [F04-OP1.3] Applies to portion of Code text: “… (c) roof assemblies shall (c)(i) have a fire-resistance rating not less than 45 min, …” and to Clause (d). |
| (3) | [F02-OS1.2] [F04-OS1.3] |
|  | [F02-OP1.2] [F04-OP1.3] |
| 3.2.2.31. Group A, Division 3, up to 2 Storeys, Sprinklered |  |
| (1) | (a) [F02,F04-OS1.2,OS1.3] Applies to portion of Code text: “… the building is sprinklered throughout …” |
|  | (a) [F02,F04-OP1.2,OP1.3] Applies to portion of Code text: “… the building is sprinklered throughout …” |
| (2) | [F02-OS1.2] Applies to portion of Code text: “Except as permitted by Clause (c) … the building referred to in Sentence (1) shall be of noncombustible construction …” |
|  | [F02-OP1.2] Applies to portion of Code text: “Except as permitted by Clause (c) … the building referred to in Sentence (1) shall be of noncombustible construction …” |
|  | (a),(c) [F03-OS1.2] [F04-OS1.2,OS1.3] |
|  | (a),(c) [F03-OP1.2] [F04-OP1.2,OP1.3] |
|  | (b),(c) [F04-OS1.3] |
|  | (b),(c) [F04-OP1.3] |
| 3.2.2.32. Group A, Division 3, One Storey, Increased Area |  |
| (2) | (a),(c) [F04-OS1.3] |
|  | (a),(c) [F04-OP1.3] |
|  | [F04-OS1.3] Applies to portion of Code text: “… (b) roof assemblies shall have, if of combustible construction, a fire-resistance rating not less than 45 min, …” and to Clause (c). |
|  | [F04-OP1.3] Applies to portion of Code text: “… (b) roof assemblies shall have, if of combustible construction, a fire-resistance rating not less than 45 min, …” and to Clause (c). |
| (3) | [F02-OS1.2] [F04-OS1.3] |
|  | [F02-OP1.2] [F04-OP1.3] |
| 3.2.2.33. Group A, Division 3, One Storey, Sprinklered |  |
| (1) | (a) [F02,F04-OS1.2,OS1.3] Applies to portion of Code text: “… the building is sprinklered throughout …” |
|  | (a) [F02,F04-OP1.2,OP1.3] Applies to portion of Code text: “… the building is sprinklered throughout …” |
| 3.2.2.35. Group A, Division 4 |  |
| (1) | [F02-OS1.2] Applies to portion of Code text: “… a building classified as Group A, Division 4 shall be of noncombustible construction.” |
|  | [F02-OP1.2] Applies to portion of Code text: “… a building classified as Group A, Division 4 shall be of noncombustible construction.” |
| (4) | [F02,F04-OS1.2,OS1.3] |
|  | [F02,F04-OP1.2,OP1.3] |
| 3.2.2.36. Group B, Division 1, Any Height, Any Area, Sprinklered |  |
| (2) | [F02-OS1.2] Applies to portion of Code text: “… the building referred to in Sentence (1) shall be of noncombustible construction …” |
|  | [F02-OP1.2] Applies to portion of Code text: “… the building referred to in Sentence (1) shall be of noncombustible construction …” |
|  | (a) [F02,F04-OS1.2,OS1.3] Applies to portion of Code text: “… the building shall be sprinklered throughout …” |
|  | (a) [F02,F04-OP1.2,OP1.3] Applies to portion of Code text: “… the building shall be sprinklered throughout …” |
|  | (b),(d) [F03-OS1.2] [F04-OS1.2,OS1.3] |
|  | (b),(d) [F03-OP1.2] [F04-OP1.2,OP1.3] |
|  | (c),(d) [F04-OS1.3] |
|  | (c),(d) [F04-OP1.3] |
| 3.2.2.37. Group B, Division 1, up to 3 Storeys, Sprinklered |  |
| (1) | (a) [F02,F04-OS1.2,OS1.3] Applies to portion of Code text: “… the building is sprinklered throughout …” |
|  | (a) [F02,F04-OP1.2,OP1.3] Applies to portion of Code text: “… the building is sprinklered throughout …” |
| (2) | [F02-OS1.2] Applies to portion of Code text: “… the building referred to in Sentence (1) shall be of noncombustible construction …” |
|  | [F02-OP1.2] Applies to portion of Code text: “… the building referred to in Sentence (1) shall be of noncombustible construction …” |
|  | (a),(c) [F03-OS1.2] [F04-OS1.2,OS1.3] |
|  | (a),(c) [F03-OP1.2] [F04-OP1.2,OP1.3] |
|  | (b),(c) [F04-OS1.3] |
|  | (b),(c) [F04-OP1.3] |
| 3.2.2.38. Group B, Division 2, Any Height, Any Area, Sprinklered |  |
| (2) | [F02-OS1.2] Applies to portion of Code text: “… the building referred to in Sentence (1) shall be of noncombustible construction …” |
|  | [F02-OP1.2] Applies to portion of Code text: “… the building referred to in Sentence (1) shall be of noncombustible construction …” |
|  | (a) [F02,F04-OS1.2,OS1.3] Applies to portion of Code text: “… the building shall be sprinklered throughout …” |
|  | (a) [F02,F04-OP1.2,OP1.3] Applies to portion of Code text: “… the building shall be sprinklered throughout …” |
|  | (b),(d) [F03-OS1.2] [F04-OS1.2,OS1.3] |
|  | (b),(d) [F03-OP1.2] [F04-OP1.2,OP1.3] |
|  | (c),(d) [F04-OS1.3] |
|  | (c),(d) [F04-OP1.3] |
| 3.2.2.39. Group B, Division 2, up to 3 Storeys, Sprinklered |  |
| (1) | (a) [F02,F04-OS1.2,OS1.3] Applies to portion of Code text: “… the building is sprinklered throughout …” |
|  | (a) [F02,F04-OP1.2,OP1.3] Applies to portion of Code text: “… the building is sprinklered throughout …” |
| (2) | [F02-OS1.2] Applies to portion of Code text: “… the building referred to in Sentence (1) shall be of noncombustible construction …” |
|  | [F02-OP1.2] Applies to portion of Code text: “… the building referred to in Sentence (1) shall be of noncombustible construction …” |
|  | (a),(c) [F03-OS1.2] [F04-OS1.2,OS1.3] |
|  | (a),(c) [F03-OP1.2] [F04-OP1.2,OP1.3] |
|  | (b),(c) [F04-OS1.3] |
|  | (b),(c) [F04-OP1.3] |
| 3.2.2.40. Group B, Division 2, up to 2 Storeys, Sprinklered |  |
| (1) | (a) [F02,F04-OS1.2,OS1.3] Applies to portion of Code text: “… the building is sprinklered throughout …” |
|  | (a) [F02,F04-OP1.2,OP1.3] Applies to portion of Code text: “… the building is sprinklered throughout …” |
| (2) | (a),(c) [F03-OS1.2] [F04-OS1.2,OS1.3] |
|  | (a),(c) [F03-OP1.2] [F04-OP1.2,OP1.3] |
|  | (b),(c) [F04-OS1.3] |
|  | (b),(c) [F04-OP1.3] |
| 3.2.2.41. Group B, Division 2, One Storey, Sprinklered |  |
| (1) | (a) [F02,F04-OS1.2,OS1.3] Applies to portion of Code text: “… the building is sprinklered throughout …” |
|  | (a) [F02,F04-OP1.2,OP1.3] Applies to portion of Code text: “… the building is sprinklered throughout …” |
| 3.2.2.42. Group B, Division 3, Any Height, Any Area, Sprinklered |  |
| (2) | [F02-OS1.2] Applies to portion of Code text: “… the building referred to in Sentence (1) shall be of noncombustible construction …” |
|  | [F02-OP1.2] Applies to portion of Code text: “… the building referred to in Sentence (1) shall be of noncombustible construction …” |
|  | (a) [F02,F04-OS1.2,OS1.3] Applies to portion of Code text: “… the building shall be sprinklered throughout …” |
|  | (a) [F02,F04-OP1.2,OP1.3] Applies to portion of Code text: “… the building shall be sprinklered throughout …” |
|  | (b),(d) [F03-OS1.2] [F04-OS1.2,OS1.3] |
|  | (b),(d) [F03-OP1.2] [F04-OP1.2,OP1.3] |
|  | (c),(d) [F04-OS1.3] |
|  | (c),(d) [F04-OP1.3] |
| 3.2.2.43. Group B, Division 3, up to 3 Storeys (Noncombustible), Sprinklered |  |
| (1) | (a) [F02,F04-OS1.2,OS1.3] Applies to portion of Code text: “… the building is sprinklered throughout …” |
|  | (a) [F02,F04-OP1.2,OP1.3] Applies to portion of Code text: “… the building is sprinklered throughout …” |
| (2) | [F02-OS1.2] Applies to portion of Code text: “… the building referred to in Sentence (1) shall be of noncombustible construction …” |
|  | [F02-OP1.2] Applies to portion of Code text: “… the building referred to in Sentence (1) shall be of noncombustible construction …” |
|  | (a),(c) [F03-OS1.2] [F04-OS1.2,OS1.3] |
|  | (a),(c) [F03-OP1.2] [F04-OP1.2,OP1.3] |
|  | (b),(c) [F04-OS1.3] |
|  | (b),(c) [F04-OP1.3] |
| 3.2.2.44. Group B, Division 3, up to 3 Storeys, Sprinklered |  |
| (1) | (a) [F02,F04-OS1.2,OS1.3] Applies to portion of Code text: “… the building is sprinklered throughout …” |
|  | (a) [F02,F04-OP1.2,OP1.3] Applies to portion of Code text: “… the building is sprinklered throughout …” |
| (2) | (a),(c) [F03-OS1.2] [F04-OS1.2,OS1.3] |
|  | (a),(c) [F03-OP1.2] [F04-OP1.2,OP1.3] |
|  | (b),(c) [F04-OS1.3] |
|  | (b),(c) [F04-OP1.3] |
| 3.2.2.45. Group B, Division 3, up to 2 Storeys, Sprinklered |  |
| (1) | (a) [F02,F04-OS1.2,OS1.3] Applies to portion of Code text: “… the building is sprinklered throughout …” |
|  | (a) [F02,F04-OP1.2,OP1.3] Applies to portion of Code text: “… the building is sprinklered throughout …” |
| (2) | (a),(c) [F03-OS1.2] [F04-OS1.2,OS1.3] |
|  | (a),(c) [F03-OP1.2] [F04-OP1.2,OP1.3] |
|  | (b),(c) [F04-OS1.3] |
|  | (b),(c) [F04-OP1.3] |
| 3.2.2.46. Group B, Division 3, One Storey, Sprinklered |  |
| (1) | (a) [F02,F04-OS1.2,OS1.3] Applies to portion of Code text: “… the building is sprinklered throughout …” |
|  | (a) [F02,F04-OP1.2,OP1.3] Applies to portion of Code text: “… the building is sprinklered throughout …” |
| 3.2.2.47. Group C, Any Height, Any Area, Sprinklered |  |
| (2) | [F02-OS1.2] Applies to portion of Code text: “… the building referred to in Sentence (1) shall be of noncombustible construction …” |
|  | [F02-OP1.2] Applies to portion of Code text: “… the building referred to in Sentence (1) shall be of noncombustible construction …” |
|  | (a) [F02,F04-OS1.2,OS1.3] Applies to portion of Code text: “… the building shall be sprinklered throughout …” |
|  | (a) [F02,F04-OP1.2,OP1.3] Applies to portion of Code text: “… the building shall be sprinklered throughout …” |
|  | (b),(d) [F03-OS1.2] [F04-OS1.2,OS1.3] |
|  | (b),(d) [F03-OP1.2] [F04-OP1.2,OP1.3] |
|  | (c),(d) [F04-OS1.3] |
|  | (c),(d) [F04-OP1.3] |
| 3.2.2.48. Group C, up to 12 storeys, Sprinklered |  |
| (2) | (b),(c) [F04-OS1.3] |
|  | (b),(c) [F04-OP1.3] |
|  | (a),(c) [F03-OS1.2] [F04-OS1.2,OS1.3] |
|  | (a),(c) [F03-OP1.2] [F04-OP1.2,OP1.3] |
| 3.2.2.49. Group C, up to 6 Storeys, Sprinklered, Noncombustible Construction |  |
| (1) | (a) [F02,F04-OS1.2,OS1.3] Applies to portion of Code text: “… the building is sprinklered throughout …” |
|  | (a) [F02,F04-OP1.2,OP1.3] Applies to portion of Code text: “… the building is sprinklered throughout …” |
| (2) | [F02-OS1.2] Applies to portion of Code text: “… the building referred to in Sentence (1) shall be of noncombustible construction …” |
|  | [F02-OP1.2] Applies to portion of Code text: “… the building referred to in Sentence (1) shall be of noncombustible construction …” |
|  | (a),(c) [F03-OS1.2] [F04-OS1.2,OS1.3] |
|  | (a),(c) [F03-OP1.2] [F04-OP1.2,OP1.3] |
|  | (b),(c) [F04-OS1.3] |
|  | (b),(c) [F04-OP1.3] |
| 3.2.2.50. Group C, up to 3 Storeys, Noncombustible Construction |  |
| (2) | [F02-OS1.2] Applies to portion of Code text: “The building referred to in Sentence (1) shall be of noncombustible construction …” |
|  | [F02-OP1.2] Applies to portion of Code text: “The building referred to in Sentence (1) shall be of noncombustible construction …” |
|  | [F03-OS1.2] [F04-OS1.2,OS1.3] Applies to portion of Code text: “... (a) ... floor assemblies shall be fire separation with a fire-resistance rating not less than 1 h, …” and to Clause (d). |
|  | [F03-OP1.2] [F04-OP1.2,OP1.3] Applies to portion of Code text: “… (a) … floor assemblies shall be fire separations with a fire-resistance rating not less than 1 h, …” and to Clause (d). |
|  | (b),(d) [F04-OS1.3] |
|  | (b),(d) [F04-OP1.3] |
|  | (c),(d) [F04-OS1.3] |
|  | (c),(d) [F04-OP1.3] |
| 3.2.2.51. Group C, up to 6 Storeys, Sprinklered |  |
| (1) | (a) [F02,F04-OS1.2,OS1.3] |
|  | (a) [F02,F04-OP1.2,OP1.3] |
| (2) | [F03-OS1.2] [F04-OS1.2,OS1.3] Applies to portion of Code text: “... (a) ... floor assemblies shall be fire separations with a fire-resistance rating not less than 1 h, …” and to Clause (e). |
|  | [F03-OP1.2] [F04-OP1.2,OP1.3] Applies to portion of Code text: “… (a) … floor assemblies shall be fire separations with a fire-resistance rating not less than 1 h, …” and to Clause (e). |
|  | (b),(d),(e) [F04-OS1.3] |
|  | (b),(d),(e) [F04-OP1.3] |
|  | (c) [F04-OS1.3] Applies to portion of Code text: “... the roof assembly shall be constructed of noncombustible construction or fire-retardant-treated wood conforming to Article 3.1.4.5., ...” |
|  | (c) [F04-OP1.3] Applies to portion of Code text: “... the roof assembly shall be constructed of noncombustible construction or fire-retardant-treated wood conforming to Article 3.1.4.5., ...” |
| 3.2.2.52. Group C, up to 4 Storeys, Sprinklered |  |
| (1) | (a) [F02,F04-OS1.2,OS1.3] Applies to portion of Code text: “… the building is sprinklered throughout …” |
|  | (a) [F02,F04-OP1.2,OP1.3] Applies to portion of Code text: “… the building is sprinklered throughout …” |
| (2) | [F03-OS1.2] [F04-OS1.2,OS1.3] Applies to portion of Code text: “... (a) ... floor assemblies shall be fire separations with a fire-resistance rating not less than 1 h, ...” and to Clause (c). |
|  | [F03-OP1.2] [F04-OP1.2,OP1.3] Applies to portion of Code text: “... (a) ... floor assemblies shall be fire separations with a fire-resistance rating not less than 1 h, ...” and to Clause (c). |
|  | (b),(c) [F04-OS1.3] |
|  | (b),(c) [F04-OP1.3] |
| 3.2.2.53. Group C, up to 3 Storeys, Increased Area |  |
| (2) | [F03-OS1.2] [F04-OS1.2,OS1.3] Applies to portion of Code text: “... (a) ... floor assemblies shall be fire separations with a fire-resistance rating not less than 1 h, ...” and to Clause (d). |
|  | [F03-OP1.2] [F04-OP1.2,OP1.3] Applies to portion of Code text: “... (a) ... floor assemblies shall be fire separations with a fire-resistance rating not less than 1 h, ...” and to Clause (d). |
|  | (b),(d) [F04-OS1.3] |
|  | (b),(d) [F04-OP1.3] |
|  | (c),(d) [F04-OS1.3] |
|  | (c),(d) [F04-OP1.3] |
| 3.2.2.54. Group C, up to 3 Storeys |  |
| (2) | [F03-OS1.2] [F04-OS1.2,OS1.3] Applies to portion of Code text: “... (a) ... floor assemblies shall be fire separations with a fire-resistance rating not less than 45 min, ...” and to Clause (c). |
|  | [F03-OP1.2] [F04-OP1.2,OP1.3] Applies to portion of Code text: “... (a) ... floor assemblies shall be fire separations with a fire-resistance rating not less than 45 min, …” and to Clause (c). |
|  | (b),(c) [F04-OS1.3] |
|  | (b),(c) [F04-OP1.3] |
| 3.2.2.55. Group C, up to 3 Storeys, Sprinklered |  |
| (1) | (a) [F02,F04-OS1.2,OS1.3] Applies to portion of Code text: “… the building is sprinklered throughout …” |
|  | (a) [F02,F04-OP1.2,OP1.3] Applies to portion of Code text: “ … the building is sprinklered throughout …” |
| (2) | [F03-OS1.2] [F04-OS1.2,OS1.3] Applies to portion of Code text: “... (a) ... floor assemblies shall be fire separations with a fire-resistance rating not less than 45 min, …” and to Clause (c). |
|  | [F03-OP1.2] [F04-OP1.2,OP1.3] Applies to portion of Code text: “… (a) … floor assemblies shall be fire separations with a fire-resistance rating not less than 45 min, …” and to Clause (c). |
|  | (b),(c) [F04-OS1.3] |
|  | (b),(c) [F04-OP1.3] |
| 3.2.2.56. Group D, Any Height, Any Area, Sprinklered |  |
| (2) | [F02-OS1.2] Applies to portion of Code text: “… the building referred to in Sentence (1) shall be of noncombustible construction …” |
|  | [F02-OP1.2] Applies to portion of Code text: “… the building referred to in Sentence (1) shall be of noncombustible construction …” |
|  | (a) [F02,F04-OS1.2,OS1.3] Applies to portion of Code text: “… the building shall be sprinklered throughout …” |
|  | (a) [F02,F04-OP1.2,OP1.3] Applies to portion of Code text: “… the building shall be sprinklered throughout …” |
|  | (b),(d) [F03-OS1.2] [F04-OS1.2,OS1.3] |
|  | (b),(d) [F03-OP1.2] [F04-OP1.2,OP1.3] |
|  | (c),(d) [F04-OS1.3] |
|  | (c),(d) [F04-OP1.3] |
| 3.2.2.57. Group D, up to 12 storeys, Sprinklered |  |
| (2) | (b),(c) [F04-OS1.3] |
|  | (b),(c) [F04-OP1.3] |
|  | (a),(c) [F03-OS1.2] [F04-OS1.2,OS1.3] |
|  | (a),(c) [F03-OP1.2] [F04-OP1.2,OP1.3] |
| 3.2.2.58. Group D, up to 6 Storeys |  |
| (2) | [F02-OS1.2] Applies to portion of Code text: “The building referred to in Sentence (1) shall be of noncombustible construction …” |
|  | [F02-OP1.2] Applies to portion of Code text: “The building referred to in Sentence (1) shall be of noncombustible construction …” |
|  | (a),(d) [F03-OS1.2] [F04-OS1.2,OS1.3] |
|  | (a),(d) [F03-OP1.2] [F04-OP1.2,OP1.3] |
|  | (b),(d) [F04-OS1.3] |
|  | (b),(d) [F04-OP1.3] |
|  | [F04-OS1.3] Applies to portion of Code text: “… (c) roof assemblies shall have a fire-resistance rating not less than 1 h …” and to Clause (d). |
|  | [F04-OP1.3] Applies to portion of Code text: “… (c) roof assemblies shall have a fire-resistance rating not less than 1 h, …” and to Clause (d). |
| 3.2.2.59. Group D, up to 6 Storeys, Sprinklered, Noncombustible Construction |  |
| (1) | (a) [F02,F04-OS1.2,OS1.3] Applies to portion of Code text: “… the building is sprinklered throughout …” |
|  | (a) [F02,F04-OP1.2,OP1.3] Applies to portion of Code text: “… the building is sprinklered throughout …” |
| (2) | [F02-OS1.2] Applies to portion of Code text: “… the building referred to in Sentence (1) shall be of noncombustible construction …” |
|  | [F02-OP1.2] Applies to portion of Code text: “… the building referred to in Sentence (1) shall be of noncombustible construction …” |
|  | (a),(c) [F03-OS1.2] [F04-OS1.2,OS1.3] |
|  | (a),(c) [F03-OP1.2] [F04-OP1.2,OP1.3] |
|  | (b),(c) [F04-OS1.3] |
|  | (b),(c) [F04-OP1.3] |
| 3.2.2.60. Group D, up to 6 Storeys, Sprinklered |  |
| (1) | (a) [F02,F04-OS1.2,OS1.3] |
|  | (a) [F02,F04-OP1.2,OP1.3] |
| (2) | (a),(e) [F03-OS1.2] [F04-OS1.3,OS1.2] |
|  | (a),(e) [F03-OP1.2] [F04-OP1.2,OP1.3] |
|  | (b),(d),(e) [F04-OS1.3] |
|  | (b),(d),(e) [F04-OP1.3] |
|  | (c) [F04-OS1.3] Applies to portion of Code text: “... the roof assembly shall be constructed of noncombustible construction or fire-retardant-treated wood conforming to Article 3.1.4.5., ...” |
|  | (c) [F04-OP1.3] Applies to portion of Code text: “.... the roof assembly shall be constructed of noncombustible construction or fire-retardant-treated wood conforming to Article 3.1.4.5., ...” |
| 3.2.2.61. Group D, up to 4 Storeys, Sprinklered |  |
| (1) | (a) [F02,F04-OS1.2,OS1.3] Applies to portion of Code text: “… the building is sprinklered throughout …” |
|  | (a) [F02,F04-OP1.2,OP1.3] Applies to portion of Code text: “… the building is sprinklered throughout …” |
| (2) | (a),(c) [F03-OS1.2] [F04-OS1.2,OS1.3] |
|  | (a),(c) [F03-OP1.2] [F04-OP1.2,OP1.3] |
|  | (b),(c) [F04-OS1.3] |
|  | (b),(c) [F04-OP1.3] |
| 3.2.2.62. Group D, up to 3 Storeys |  |
| (2) | [F04-OS1.3] Applies to portion of Code text: “… (c) roof assemblies shall have, if of combustible construction, a fire-resistance rating not less than 45 min, …” and to Clause (d). |
|  | [F04-OP1.3] Applies to portion of Code text: “… (c) roof assemblies shall have, if of combustible construction, a fire-resistance rating not less than 45 min, …” and to Clause (d). |
|  | (a) [F03-OS1.2] Applies to the requirement that noncombustible floor assemblies be fire separations. |
|  | (a) [F03-OP1.2] Applies to the requirement that noncombustible floor assemblies be fire separations. |
|  | (a),(d) [F03-OS1.2] [F04-OS1.2,OS1.3] |
|  | (a),(d) [F03-OP1.2] [F04-OP1.2,OP1.3] |
|  | (b),(d) [F04-OS1.3] |
|  | (b),(d) [F04-OP1.3] |
| 3.2.2.63. Group D, up to 3 Storeys, Sprinklered |  |
| (1) | (a) [F02,F04-OS1.2,OS1.3] Applies to portion of Code text: “… the building is sprinklered throughout …” |
|  | (a) [F02,F04-OP1.2,OP1.3] Applies to portion of Code text: “ … the building is sprinklered throughout …” |
| (2) | (a) [F03-OS1.2] Applies to the requirement that noncombustible floor assemblies be fire separations. |
|  | (a) [F03-OP1.2] Applies to the requirement that noncombustible floor assemblies be fire separations. |
|  | (a),(c) [F03-OS1.2] [F04-OS1.2,OS1.3] |
|  | (a),(c) [F03-OP1.2] [F04-OP1.2,OP1.3] |
|  | (b),(c) [F04-OS1.3] |
|  | (b),(c) [F04-OP1.3] |
| 3.2.2.64. Group D, up to 2 Storeys |  |
| (2) | (a) [F03-OS1.2] Applies to the requirement that noncombustible floor assemblies be fire separations. |
|  | (a) [F03-OP1.2] Applies to the requirement that noncombustible floor assemblies be fire separations. |
|  | [F03-OS1.2] [F04-OS1.2,OS1.3] |
|  | [F03-OP1.2] [F04-OP1.2,OP1.3] |
| 3.2.2.65. Group D, up to 2 Storeys, Sprinklered |  |
| (1) | (a) [F02,F04-OS1.2,OS1.3] Applies to portion of Code text: “… the building is sprinklered throughout …” |
|  | (a) [F02,F04-OP1.2,OP1.3] Applies to portion of Code text: “… the building is sprinklered throughout …” |
| (2) | (a) [F03-OS1.2] Applies to the requirement that noncombustible floor assemblies be fire separations. |
|  | (a) [F03-OP1.2] Applies to the requirement that noncombustible floor assemblies be fire separations. |
|  | [F03-OS1.2] [F04-OS1.2,OS1.3] |
|  | [F03-OP1.2] [F04-OP1.2,OP1.3] |
| 3.2.2.66. Group E, Any Height, Any Area, Sprinklered |  |
| (2) | [F02-OS1.2] Applies to portion of Code text: “… the building referred to in Sentence (1) shall be of noncombustible construction …” |
|  | [F02-OP1.2] Applies to portion of Code text: “… the building referred to in Sentence (1) shall be of noncombustible construction …” |
|  | (a) [F02,F04-OS1.2,OS1.3] Applies to portion of Code text: “… the building shall be sprinklered throughout …” |
|  | (a) [F02,F04-OP1.2,OP1.3] Applies to portion of Code text: “… the building shall be sprinklered throughout …” |
|  | (b),(d) [F03-OS1.2] [F04-OS1.2,OS1.3] |
|  | (b),(d) [F03-OP1.2] [F04-OP1.2,OP1.3] |
|  | (c),(d) [F04-OS1.3] |
|  | (c),(d) [F04-OP1.3] |
| 3.2.2.67. Group E, up to 4 Storeys, Sprinklered |  |
| (1) | (a) [F02,F04-OS1.2,OS1.3] Applies to portion of Code text: “… the building is sprinklered throughout …” |
|  | (a) [F02,F04-OP1.2,OP1.3] Applies to portion of Code text: “… the building is sprinklered throughout …” |
| (2) | (a),(c) [F03-OS1.2] [F04-OS1.2,OS1.3] |
|  | (a),(c) [F03-OP1.2] [F04-OP1.2,OP1.3] |
|  | (b),(c) [F04-OS1.3] |
|  | (b),(c) [F04-OP1.3] |
| 3.2.2.68. Group E, up to 3 Storeys |  |
| (2) | (a),(e) [F03-OS1.2] [F04-OS1.2,OS1.3] |
|  | (a),(e) [F03-OP1.2] [F04-OP1.2,OP1.3] |
|  | (b),(d) [F04-OS1.3] |
|  | (b),(d) [F04-OP1.3] |
|  | (c),(d) [F04-OS1.3] |
|  | (c),(d) [F04-OP1.3] |
| 3.2.2.69. Group E, up to 3 Storeys, Sprinklered |  |
| (1) | (a) [F02,F04-OS1.2,OS1.3] Applies to portion of Code text: “… the building is sprinklered throughout …” |
|  | (a) [F02,F04-OP1.2,OP1.3] Applies to portion of Code text: “… the building is sprinklered throughout …” |
| (2) | (a),(d) [F03-OS1.2] [F04-OS1.2,OS1.3] |
|  | (a),(d) [F03-OP1.2] [F04-OP1.2,OP1.3] |
|  | (b),(c) [F04-OS1.3] |
|  | (b),(c) [F04-OP1.3] |
| 3.2.2.70. Group E, up to 2 Storeys |  |
| (2) | [F03-OS1.2] [F04-OS1.2,OS1.3] |
|  | (a),(b) [F03-OP1.2] [F04-OP1.2,OP1.3] |
| 3.2.2.71. Group E, up to 2 Storeys, Sprinklered |  |
| (1) | (a) [F02,F04-OS1.2,OS1.3] Applies to portion of Code text: “… the building is sprinklered throughout …” |
|  | (a) [F02,F04-OP1.2,OP1.3] Applies to portion of Code text: “… the building is sprinklered throughout …” |
| (2) | [F03-OS1.2] [F04-OS1.2,OS1.3] |
|  | (a),(b) [F03-OP1.2] [F04-OP1.2,OP1.3] |
| 3.2.2.72. Group F, Division 1, up to 4 Storeys, Sprinklered |  |
| (2) | (c),(d) [F04-OP1.3] |
|  | [F02-OS1.2] Applies to portion of Code text: “… the building referred to in Sentence (1) shall be of noncombustible construction …” |
|  | [F02-OP1.2] Applies to portion of Code text: “… the building referred to in Sentence (1) shall be of noncombustible construction …” |
|  | (a) [F02,F04-OS1.2,OS1.3] Applies to portion of Code text: “… the building shall be sprinklered throughout …” |
|  | (a) [F02,F04-OP1.2,OP1.3] Applies to portion of Code text: “… the building shall be sprinklered throughout …” |
|  | (b),(d) [F03-OS1.2] [F04-OS1.2,OS1.3] |
|  | (b),(d) [F03-OP1.2] [F04-OP1.2,OP1.3] |
|  | (c),(d) [F04-OS1.3] |
| 3.2.2.73. Group F, Division 1, up to 3 Storeys, Sprinklered |  |
| (1) | (a) [F02,F04-OS1.2,OS1.3] Applies to portion of Code text: “… the building is sprinklered throughout …” |
|  | (a) [F02,F04-OP1.2,OP1.3] Applies to portion of Code text: “… the building is sprinklered throughout …” |
| (2) | [F02-OS1.2] Applies to portion of Code text: “The building referred to in Sentence (1) is permitted to be of heavy timber construction or noncombustible construction used singly or in combination …” |
|  | [F02-OP1.2] Applies to portion of Code text: “The building referred to in Sentence (1) is permitted to be of heavy timber construction or noncombustible construction used singly or in combination …” |
|  | [F03-OS1.2] [F04-OS1.2,OS1.3] |
|  | [F03-OP1.2] [F04-OP1.2,OP1.3] |
| 3.2.2.74. Group F, Division 1, up to 2 Storeys, Sprinklered |  |
| (1) | (a) [F02,F04-OS1.2,OS1.3] Applies to portion of Code text: “… the building is sprinklered throughout …” |
|  | (a) [F02,F04-OP1.2,OP1.3] Applies to portion of Code text: “… the building is sprinklered throughout …” |
| (2) | (a) [F03-OS1.2] Applies to portion of Code text: “... [noncombustible] floor assemblies shall be fire separations …” |
|  | (a) [F03-OP1.2] Applies to portion of Code text: “... [noncombustible] floor assemblies shall be fire separations …” |
|  | [F03-OS1.2] [F04-OS1.2,OS1.3] |
|  | [F03-OP1.2] [F04-OP1.2,OP1.3] |
| 3.2.2.76. Group F, Division 2, Any Height, Any Area, Sprinklered |  |
| (2) | [F02-OS1.2] Applies to portion of Code text: “… the building referred to in Sentence (1) shall be of noncombustible construction …” |
|  | [F02-OP1.2] Applies to portion of Code text: “… the building referred to in Sentence (1) shall be of noncombustible construction …” |
|  | (a) [F02,F04-OS1.2,OS1.3] Applies to portion of Code text: “… the building shall be sprinklered throughout …” |
|  | (a) [F02,F04-OP1.2,OP1.3] Applies to portion of Code text: “… the building shall be sprinklered throughout …” |
|  | (b),(d) [F03-OS1.2] [F04-OS1.2,OS1.3] |
|  | (b),(d) [F03-OP1.2] [F04-OP1.2,OP1.3] |
|  | (c),(d) [F04-OS1.3] |
|  | (c),(d) [F04-OP1.3] |
| 3.2.2.77. Group F, Division 2, up to 4 Storeys, Increased Area, Sprinklered |  |
| (1) | (a) [F02,F04-OS1.2,OS1.3] Applies to portion of Code text: “… the building is sprinklered throughout …” |
|  | (a) [F02,F04-OP1.2,OP1.3] Applies to portion of Code text: “… the building is sprinklered throughout …” |
| (2) | [F02-OS1.2] Applies to portion of Code text: “… the building referred to in Sentence (1) shall be of noncombustible construction …” |
|  | [F02-OP1.2] Applies to portion of Code text: “… the building referred to in Sentence (1) shall be of noncombustible construction …” |
|  | (a),(c) [F03-OS1.2] [F04-OS1.2,OS1.3] |
|  | (a),(c) [F03-OP1.2] [F04-OP1.2,OP1.3] |
|  | (b),(c) [F04-OS1.3] |
|  | (b),(c) [F04-OP1.3] |
| 3.2.2.78. Group F, Division 2, up to 3 Storeys |  |
| (2) | (a),(e) [F03-OS1.2] [F04-OS1.2,OS1.3] |
|  | (a),(e) [F03-OP1.2] [F04-OP1.2,OP1.3] |
|  | (b),(d) [F04-OS1.3] |
|  | (b),(d) [F04-OP1.3] |
|  | [F04-OS1.3] Applies to portion of Code text: “… (c) roof assemblies shall have, if of combustible construction, a fire-resistance rating not less than 45 min …” and to Clause (d). |
|  | [F04-OP1.3] Applies to portion of Code text: “… (c) roof assemblies shall have, if of combustible construction, a fire-resistance rating not less than 45 min, …” and to Clause (d). |
| 3.2.2.79. Group F, Division 2, up to 4 Storeys, Sprinklered |  |
| (1) | (a) [F02,F04-OS1.2,OS1.3] Applies to portion of Code text: “… the building is sprinklered throughout …” |
|  | (a) [F02,F04-OP1.2,OP1.3] Applies to portion of Code text: “… the building is sprinklered throughout …” |
| (2) | (a),(d) [F03-OS1.2] [F04-OS1.2,OS1.3] |
|  | (a),(d) [F03-OP1.2] [F04-OP1.2,OP1.3] |
|  | (b),(c) [F04-OS1.3] |
|  | (b),(c) [F04-OP1.3] |
| 3.2.2.80. Group F, Division 2, up to 2 Storeys |  |
| (2) | (a) [F03-OS1.2] Applies to the requirement that noncombustible floor assemblies be fire separations. |
|  | (a) [F03-OP1.2] Applies to the requirement that noncombustible floor assemblies be fire separations. |
|  | [F03-OS1.2] [F04-OS1.2,OS1.3] |
|  | [F03-OP1.2] [F04-OP1.2,OP1.3] |
| 3.2.2.81. Group F, Division 2, up to 2 Storeys, Sprinklered |  |
| (1) | (a) [F02,F04-OS1.2,OS1.3] Applies to portion of Code text: “… the building is sprinklered throughout …” |
|  | (a) [F02,F04-OP1.2,OP1.3] Applies to portion of Code text: “… the building is sprinklered throughout …” |
| (2) | (a) [F03-OS1.2] Applies to the requirement that noncombustible floor assemblies be fire separations. |
|  | (a) [F03-OP1.2] Applies to the requirement that noncombustible floor assemblies be fire separations. |
|  | [F03-OS1.2] [F04-OS1.2,OS1.3] |
|  | [F03-OP1.2] [F04-OP1.2,OP1.3] |
| 3.2.2.82. Group F, Division 3, Any Height, Any Area, Sprinklered |  |
| (2) | [F02-OS1.2] Applies to portion of Code text: “… the building referred to in Sentence (1) shall be of noncombustible construction …” |
|  | [F02-OP1.2] Applies to portion of Code text: “… the building referred to in Sentence (1) shall be of noncombustible construction …” |
|  | (a) [F02,F04-OS1.2,OS1.3] Applies to portion of Code text: “… the building shall be sprinklered throughout …” |
|  | (a) [F02,F04-OP1.2,OP1.3] Applies to portion of Code text: “… the building shall be sprinklered throughout …” |
|  | (b),(d) [F03-OS1.2] [F04-OS1.2,OS1.3] |
|  | (b),(d) [F03-OP1.2] [F04-OP1.2,OP1.3] |
|  | (c),(d) [F04-OS1.3] |
|  | (c),(d) [F04-OP1.3] |
| 3.2.2.83. Group F, Division 3, up to 6 Storeys |  |
| (2) | [F02-OS1.2] Applies to portion of Code text: “The building referred to in Sentence (1) shall be of noncombustible construction…” |
|  | [F02-OP1.2] Applies to portion of Code text: “The building referred to in Sentence (1) shall be of noncombustible construction …” |
|  | (a),(d) [F03-OS1.2] [F04-OS1.2,OS1.3] |
|  | (a),(d) [F03-OP1.2] [F04-OP1.2,OP1.3] |
|  | (b),(d) [F04-OS1.3] |
|  | (b),(d) [F04-OP1.3] |
|  | (c),(d) [F04-OS1.3] |
|  | (c),(d) [F04-OP1.3] |
| 3.2.2.84. Group F, Division 3, up to 6 Storeys, Sprinklered |  |
| (1) | (a) [F02,F04-OS1.2,OS1.3] Applies to portion of Code text: “… the building is sprinklered throughout …” |
|  | (a) [F02,F04-OP1.2,OP1.3] Applies to portion of Code text: “… the building is sprinklered throughout …” |
| (2) | [F02-OS1.2] Applies to portion of Code text: “… the building referred to in Sentence (1) shall be of noncombustible construction …” |
|  | [F02-OP1.2] Applies to portion of Code text: “… the building referred to in Sentence (1) shall be of noncombustible construction …” |
|  | (a),(c) [F03-OS1.2] [F04-OS1.2,OS1.3] |
|  | (a),(c) [F03-OP1.2] [F04-OP1.2,OP1.3] |
|  | (b),(c) [F04-OS1.3] |
|  | (b),(c) [F04-OP1.3] |
| 3.2.2.85. Group F, Division 3, up to 4 Storeys |  |
| (2) | [F04-OS1.3] Applies to portion of Code text: “… (c) roof assemblies shall have, if of combustible construction, a fire-resistance rating not less than 45 min …” and to Clause (d). |
|  | [F04-OP1.3] Applies to portion of Code text: “… (c) roof assemblies shall have, if of combustible construction, a fire-resistance rating not less than 45 min, …” and to Clause (d). |
|  | (a) [F03-OS1.2] Applies to the requirement that noncombustible floor assemblies be fire separations. |
|  | (a) [F03-OP1.2] Applies to the requirement that noncombustible floor assemblies be fire separations. |
|  | (a),(d) [F03-OS1.2] [F04-OS1.2,OS1.3] |
|  | (a),(d) [F03-OP1.2] [F04-OP1.2,OP1.3] |
|  | (b),(d) [F04-OS1.3] |
|  | (b),(d) [F04-OP1.3] |
| 3.2.2.86. Group F, Division 3, up to 4 Storeys, Sprinklered |  |
| (1) | (a) [F02,F04-OS1.2,OS1.3] Applies to portion of Code text: “… the building is sprinklered throughout …” |
|  | (a) [F02,F04-OP1.2,OP1.3] Applies to portion of Code text: “… the building is sprinklered throughout …” |
| (2) | (a) [F03-OS1.2] Applies to the requirement that noncombustible floor assemblies be fire separations. |
|  | (a) [F03-OP1.2] Applies to the requirement that noncombustible floor assemblies be fire separations. |
|  | (a),(c) [F03-OS1.2] [F04-OS1.2,OS1.3] |
|  | (a),(c) [F03-OP1.2] [F04-OP1.2,OP1.3] |
|  | (b),(c) [F04-OS1.3] |
|  | (b),(c) [F04-OP1.3] |
| 3.2.2.87. Group F, Division 3, up to 2 Storeys |  |
| (2) | (a) [F03-OS1.2] Applies to the requirement that noncombustible floor assemblies be fire separations. |
|  | (a) [F03-OP1.2] Applies to the requirement that noncombustible floor assemblies be fire separations. |
|  | [F03-OS1.2] [F04-OS1.2,OS1.3] |
|  | [F03-OP1.2] [F04-OP1.2,OP1.3] |
| 3.2.2.88. Group F, Division 3, up to 2 Storeys, Sprinklered |  |
| (1) | (a) [F02,F04-OS1.2,OS1.3] Applies to portion of Code text: “… the building is sprinklered throughout …” |
|  | (a) [F02,F04-OP1.2,OP1.3] Applies to portion of Code text: “… the building is sprinklered throughout …” |
| (2) | (a) [F03-OS1.2] Applies to the requirement that noncombustible floor assemblies be fire separations. |
|  | (a) [F03-OP1.2] Applies to the requirement that noncombustible floor assemblies be fire separations. |
|  | [F03-OS1.2] [F04-OS1.2,OS1.3] |
|  | [F03-OP1.2] [F04-OP1.2,OP1.3] |
| 3.2.2.89. Group F, Division 3, One Storey |  |
| (1) | [F02-OS1.2] Applies to portion of Code text: “A building classified as Group F, Division 3 is permitted to be of heavy timber construction or noncombustible construction used singly or in combination …” |
|  | [F02-OP1.2] Applies to portion of Code text: “A building classified as Group F, Division 3 is permitted to be of heavy timber construction or noncombustible construction used singly or in combination …” |
| 3.2.2.90. Group F, Division 3, One Storey, Sprinklered |  |
| (1) | [F02-OS1.2] Applies to portion of Code text: “A building classified as Group F, Division 3 is permitted to be of heavy timber construction or noncombustible construction used singly or in combination …” |
|  | [F02-OP1.2] Applies to portion of Code text: “A building classified as Group F, Division 3 is permitted to be of heavy timber construction or noncombustible construction used singly or in combination …” |
|  | (a) [F02,F04-OS1.2,OS1.3] Applies to portion of Code text: “… the building is sprinklered throughout …” |
|  | (a) [F02,F04-OP1.2,OP1.3] Applies to portion of Code text: “… the building is sprinklered throughout …” |
| 3.2.2.91. Group F, Division 3, One Storey, Any Area, Low Fire Load Occupancy |  |
| (2) | [F02-OS1.2] |
|  | [F02-OP1.2] |
| 3.2.2.92. Group F, Division 3, Storage Garages up to 22 m High |  |
| (1) | [F02-OS1.2] Applies to portion of Code text: “A building used as a storage garage with all storeys constructed as open-air storeys and having no other occupancy above it is permitted to have its floor, wall, ceiling and roof assemblies constructed without a fire-resistance rating provided it is (a) of noncombustible construction …” |
|  | [F02-OP1.2] Applies to portion of Code text: “A building used as a storage garage with all storeys constructed as open-air storeys and having no other occupancy above it is permitted to have its floor, wall, ceiling and roof assemblies constructed without a fire-resistance rating provided it is (a) of noncombustible construction …” |
| 3.2.3.1. Limiting Distance and Area of Unprotected Openings |  |
| (1) | [F03-OP3.1] |
| (5) | [F03-OP3.1] |
| (6) | [F03-OP3.1] |
| (8) | [F03-OP3.1] |
| (9) | [F03-OP3.1] |
| (10) | [F03-OP3.1] |
| 3.2.3.4. Party Wall |  |
| (1) | [F03-OP3.1] |
| 3.2.3.5. Wall with Limiting Distance Less Than 1.2 m |  |
| (1) | [F03-OP3.1] |
| (2) | [F03-OP3.1] |
| 3.2.3.6. Combustible Projections |  |
| (1) | [F03-OP3.1] |
| (2) | [F03-OP3.1] |
| (3) | [F03-OP3.1] |
| (5) | [F03-OP3.1] |
| 3.2.3.7. Construction of Exposing Building Face |  |
| (1) | [F03,F02-OP3.1] |
| (2) | [F03,F02-OP3.1] |
| (3) | [F02,F03-OP3.1] |
| (4) | [F03,F02-OP3.1] |
| 3.2.3.8. Protection of Exterior Building Face |  |
| (1) | [F03,F02-OP3.1] |
| 3.2.3.9. Protection of Structural Members |  |
| (1) | [F04-OS1.3] |
|  | [F04-OP1.3] |
| 3.2.3.10. Unlimited Unprotected Openings |  |
| (1) | [F03-OP3.1] |
| (2) | [F03-OP3.1] |
| 3.2.3.11. Low Fire Load, One Storey Building |  |
| (1) | (b) [F03-OP3.1] |
|  | (a) [F04-OP3.1] |
| 3.2.3.12. Area Increase for Unprotected Openings |  |
| (1) | [F03-OP3.1] |
| 3.2.3.13. Protection of Exit Facilities |  |
| (4) | [F06-OS1.2] [F05-OS1.5] |
|  | [F06-OP1.2] |
| 3.2.3.14. Wall Exposed to Another Wall |  |
| (1) | [F03-OS1.2] |
|  | [F03-OP1.2] |
|  | [F03-OP3.1] |
| (2) | [F03-OS1.2] |
|  | [F03-OP1.2] |
|  | [F03-OP3.1] |
| 3.2.3.15. Wall Exposed to Adjoining Roof |  |
| (1) | [F03-OS1.2] |
|  | [F03-OP1.2] |
| 3.2.3.16. Protection of Soffits |  |
| (1) | [F03-OS1.2] |
|  | [F03-OP1.2] |
| (2) | [F03-OS1.2] |
|  | [F03-OP1.2] |
| (3) | [F03-OS1.2] |
|  | [F03-OP1.2] |
| (4) | [F02-OS1.2] |
|  | [F02-OP1.2] |
| 3.2.3.17. Canopy Protection for Vertically Separated Openings |  |
| (1) | [F03-OS1.2] |
|  | [F03-OP1.2] |
| (2) | [F03-OS1.2] |
|  | [F03-OP1.2] |
| (3) | [F02-OS1.2] |
|  | [F02-OP1.2] |
| 3.2.3.18. Covered Vehicular Passageway |  |
| (1) | [F03-OP3.1] |
| (2) | [F02-OP3.1] |
| 3.2.3.19. Walkway between Buildings |  |
| (1) | [F03-OP3.1] |
| (2) | [F02-OP3.1] |
| (3) | [F02-OP3.1] |
| (4) | [F02,F12-OP3.1] |
| 3.2.3.20. Underground Walkway |  |
| (1) | [F01,F02-OP3.1] |
| (2) | [F03-OP3.1] |
| (3) | [F02-OP3.1] Applies to portion of Code text: “An underground walkway shall be of noncombustible construction …” |
|  | [F80-OP2.3] Applies to portion of Code text: “An underground walkway shall be … suitable for an underground location.” |
| (4) | (a) [F05-OS1.5] [F06-OS1.2] |
|  | (b) [F10-OS1.5] [F12-OS1.2] |
| 3.2.3.22. Installation of Service Lines Under Buildings |  |
| (1) | [F01-OS1.1] |
|  | [F01-OP1.1] |
| 3.2.4.1. Determination of Requirement for a Fire Alarm System |  |
| (1) | [F11-OS1.5] [F13-OS1.5,OS1.2] |
|  | [F13-OP1.2] |
| (4) | [F11-OS1.5] |
| 3.2.4.2. Continuity of Fire Alarm System |  |
| (1) | [F11-OS1.5] |
| (2) | [F11-OS1.5] |
| (3) | [F11-OS1.5] |
| (4) | [F10-OS1.5] [F03-OS1.2] |
| (5) | [F11,F13-OS1.2] |
| (6) | [F11-OS1.5] |
| 3.2.4.3. Types of Fire Alarm Systems |  |
| (1) | (a) [F11-OS1.5] |
|  | (b) [F11-OS1.4] [F13-OS1.5] |
|  | (c),(d) [F11-OS1.5] |
| 3.2.4.4. Description of Fire Alarm Systems |  |
| (1) | [F11-OS1.5] |
| (2) | (a) [F11-OS1.4] [F13-OS1.5] |
|  | (b),(c) [F11-OS1.5] |
| (3) | [F13-OS1.5] |
| (4) | [F13-OS1.5] |
| 3.2.4.5. Installation and Verification of Fire Alarm Systems |  |
| (1) | [F11,F81-OS1.5] [F13,F12,F81-OS1.5,OS1.2] |
|  | [F12,F11-OS3.7] Applies to voice communication systems. |
| (2) | [F82-OS1.5] |
| 3.2.4.6. Silencing of Alarm Signals |  |
| (1) | [F11-OS1.5] |
| (2) | [F81,F34-OS1.5] |
| 3.2.4.7. Signals to Fire Department |  |
| (1) | [F13-OS1.5,OS1.2] |
|  | [F13-OP1.2] |
| (2) | [F13-OS1.5,OS1.2] |
|  | [F13-OP1.2] |
| (3) | [F13-OS1.5,OS1.2] |
|  | [F13-OP1.2] |
| (4) | [F81,F13-OS1.5,OS1.2] |
|  | [F81,F13-OP1.2] |
| (5) | [F13-OS1.5,OS1.2] |
|  | [F13-OP1.2] |
| (6) | [F13-OP1.2] |
|  | [F13-OS1.2] |
| 3.2.4.8. Annunciator and Zone Indication |  |
| (1) | [F12-OS1.5,OS1.2] |
| (2) | [F12-OS1.5,OS1.2] |
| (4) | [F12-OS1.2,OS1.5] |
| (7) | [F12-OS1.5,OS1.2] |
| 3.2.4.9. Electrical Supervision |  |
| (1) | [F82-OS1.5,OS1.2] |
| (2) | [F82-OS1.2] |
|  | [F82-OP1.2] |
| (3) | (a),(d),(e),(f),(g) [F82-OS1.2] |
|  | (a),(d),(e),(f),(g) [F82-OP1.2] |
|  | (b),(c) [F82-OS1.5] |
| (4) | [F81-OP1.2] |
|  | [F82-OS1.2] |
| (5) | [F81-OP1.2] |
|  | [F82-OS1.2] |
| (6) | [F82-OS1.2] |
|  | [F82-OP1.2] |
| 3.2.4.10. Fire Detectors |  |
| (1) | [F11-OS1.5] |
| (2) | [F11-OS1.5] |
| (3) | [F02-OS1.2] [F11-OS1.5] |
| (4) | [F11-OS1.5] |
| 3.2.4.11. Smoke Detectors |  |
| (1) | [F11-OS1.5] |
| (3) | [F12-OS1.5] |
| (4) | [F10-OS1.5] |
| (5) | [F11-OS1.5] |
| (7) | [F11-OS1.4,OS1.5] |
| 3.2.4.12. Prevention of Smoke Circulation |  |
| (1) | [F03-OS1.2] |
| 3.2.4.13. Vacuum Cleaning System Shutdown |  |
| (1) | [F03-OS1.2] |
| 3.2.4.14. Elevator Emergency Return |  |
| (1) | [F10-OS1.5] |
| (2) | [F11-OS1.5] |
| (3) | [F02-OS1.2] |
| 3.2.4.15. System Monitoring |  |
| (1) | [F11-OS1.5] [F12-OS1.5,OS1.2] |
|  | [F12-OP1.2] |
| (2) | [F11-OS1.5] [F13-OS1.5,OS1.2] |
|  | [F13-OP1.2] |
| (3) | [F12-OS1.2,OS1.5] |
|  | [F12-OP1.2] |
| 3.2.4.16. Manual Stations |  |
| (1) | [F11-OS1.5] |
| (2) | [F02-OS1.2] [F12-OS1.2,OS1.5] [F10-OS1.5] |
| (3) | [F02-OS1.2] [F12-OS1.2,OS1.5] [F10-OS1.5] |
| (4) | [F11-OS1.5] |
| (5) | [F11-OS1.5] |
| 3.2.4.17. Alert and Alarm Signals |  |
| (2) | [F11-OS1.5] |
| (3) | [F11-OS1.5] |
| 3.2.4.18. Audibility of Alarm Systems |  |
| (1) | [F11-OS1.5] |
| (2) | [F11-OS1.5] |
| (3) | [F11-OS1.5] |
| (4) | [F33-OS3.5] |
| (5) | [F11-OS1.5] |
| (6) | [F11-OS1.5] |
| (7) | [F11-OS1.5] |
| (8) | [F11,F81-OS1.5] |
| (9) | [F11,F81-OS1.5] |
| (10) | [F11,F81-OS1.5] |
| (11) | [F11-OS1.5] |
| (13) | [F11-OS1.5] |
| 3.2.4.19. Visible Signals |  |
| (1) | [F11-OS1.5] |
| (3) | [F11-OS1.5] |
| 3.2.4.20. Smoke Alarms |  |
| (2) | [F81,F11-OS1.5] |
| (3) | [F11-OS1.5] |
| (4) | [F11-OS1.5] |
| (5) | [F11-OS1.5] |
| (6) | [F11-OS1.5] |
| (7) | [F11-OS1.5] |
| (8) | [F11-OS1.5] |
| (9) | [F11,F81-OS1.5] |
| (10) | [F11,F81-OS1.5] |
| (12) | [F11-OS1.5] |
| (13) | [F81,F11-OS1.5] |
| (14) | [F11,F81-OS1.5] |
| (16) | [F11-OS1.5] |
| 3.2.4.21. Residential Fire Warning Systems |  |
| (1) | [F11,F81-OS1.5] |
| 3.2.4.22. Voice Communication Systems for High Buildings |  |
| (1) | [F12,F11-OS3.7] |
| (2) | [F11-OS1.5] |
| (3) | [F11-OS1.5] [F13-OS1.4,OS1.5] |
| (4) | [F11-OS1.5] |
| (5) | [F12-OS3.7] |
| (6) | [F11-OS1.5] |
| (7) | [F11-OS1.5] |
| 3.2.4.23. One-Way Voice Communication Systems |  |
| (1) | [F11-OS1.5] |
| (2) | [F11-OS1.5] |
| (3) | [F11-OS1.5] |
| 3.2.5.1. Access to Above-Grade Storeys |  |
| (1) | [F12-OS1.5,OS1.2] |
|  | [F12-OP1.2] |
| (2) | [F12-OS1.5,OS1.2] |
|  | [F12-OP1.2] |
| (3) | [F12-OS1.5,OS1.2] |
|  | [F12-OP1.2] |
| 3.2.5.2. Access to Basements |  |
| (1) | [F12-OS1.5,OS1.2] |
|  | [F12-OP1.2] |
| (2) | [F12-OS1.5,OS1.2] |
|  | [F12-OP1.2] |
| 3.2.5.3. Roof Access |  |
| (1) | [F12-OS1.2] |
|  | [F12-OP1.2] |
| 3.2.5.4. Access Routes |  |
| (1) | [F12-OS1.5,OS1.2] |
|  | [F12-OP1.2] |
| 3.2.5.5. Location of Access Routes |  |
| (1) | [F12-OS1.5,OS1.2] [F06-OS1.1] |
|  | [F12-OP1.2] |
| (2) | [F12-OS1.2] |
|  | [F12-OP1.2] |
| (4) | [F12-OS1.2] |
|  | [F12-OP1.2] |
| 3.2.5.6. Access Route Design |  |
| (1) | [F12-OS1.2] |
|  | [F12-OP1.2] |
| (2) | [F02,F12-OS1.2] |
|  | [F02,F12,F03-OP1.2] |
|  | [F02,F12,F03-OP3.1] |
| 3.2.5.7. Water Supply |  |
| (1) | [F02-OS1.2] |
|  | [F02-OP1.2] |
|  | [F02-OP3.1] |
| 3.2.5.8. Standpipe Systems |  |
| (1) | [F02-OS1.2] |
|  | [F02-OP1.2] |
| 3.2.5.9. Standpipe System Design |  |
| (1) | [F02-OS1.2] |
|  | [F02-OP1.2] |
| (2) | [F12-OS1.2] |
|  | [F12-OP1.2] |
| (4) | [F02-OS1.2] |
|  | [F02-OP1.2] |
| (5) | [F12-OS1.2] |
|  | [F12-OP1.2] |
| 3.2.5.10. Hose Connections |  |
| (1) | [F03-OS1.2] [F05,F06-OS1.5,OS1.2] |
|  | [F03,F06-OP1.2] |
| (3) | [F12-OS1.2] |
|  | [F12-OP1.2] |
| (4) | [F02-OS1.2] |
|  | [F02-OP1.2] |
| 3.2.5.11. Hose Stations |  |
| (1) | [F02-OS1.2] |
|  | [F02-OP1.2] |
| (2) | [F02-OS1.2] |
|  | [F02-OP1.2] |
| (3) | [F02,F12-OS1.2] |
|  | [F02,F12-OP1.2] |
| (4) | [F03-OS1.2] |
|  | [F03-OP1.2] |
| (5) | [F10-OS1.5] |
| (6) | [F02-OS1.2] |
|  | [F02-OP1.2] |
| (7) | [F01-OS1.1] |
| 3.2.5.12. Automatic Sprinkler Systems |  |
| (1) | [F02,F81,F82-OS1.2] |
|  | [F02,F81,F82-OP1.2] |
| (2) | [F02,F81-OS1.2] |
|  | [F02,F81-OP1.2] |
| (3) | [F02,F81-OS1.2] |
|  | [F02,F81-OP1.2] |
| (4) | [F02-OS1.2] |
|  | [F02-OP1.2] |
| (5) | [F81-OS1.2] |
|  | [F81-OP1.2] |
| (6) | [F02-OS1.2] |
|  | [F02-OP1.2] |
| (7) | [F03-OS1.2] |
|  | [F03-OP1.2] |
|  | [F03-OP3.1] |
| (8) | [F81-OS3.3,OS3.6] |
| 3.2.5.13. Combustible Sprinkler Piping |  |
| (2) | [F02,F81-OS1.2] |
|  | [F02,F81-OP1.2] |
| (3) | [F06-OS1.2] |
|  | [F06-OP1.2] |
| (4) | [F06-OS1.2] |
|  | [F06-OP1.2] |
| 3.2.5.14. Sprinklered Service Space |  |
| (1) | [F02-OS1.2] |
|  | [F02-OP1.2] |
| (2) | [F12-OS1.2] |
|  | [F12-OP1.2] |
| (3) | [F11-OS1.5] [F12-OS1.5,OS1.2] |
|  | [F12-OP1.2] |
| 3.2.5.15. Fire Department Connections |  |
| (1) | [F12-OS1.2] |
|  | [F12-OP1.2] |
| (2) | [F12-OS1.2] |
|  | [F12-OP1.2] |
| 3.2.5.16. Portable Fire Extinguishers |  |
| (1) | [F02,F12,F81-OS1.2] |
|  | [F02,F12,F81-OP1.2] |
| (2) | [F12-OS1.2] |
|  | [F12-OP1.2] |
| 3.2.5.17. Protection from Freezing |  |
| (1) | [F81-OS1.2] |
|  | [F81-OP1.2] |
| 3.2.5.18. Fire Pumps |  |
| (1) | [F02,F81-OS1.2] [F81-OS1.4] |
|  | [F02,F81-OP1.2] [F81-OP1.4] |
| 3.2.6.2. Limits to Smoke Movement |  |
| (1) | [F02-OS1.2,OS1.5] |
|  | [F02-OP1.2] |
| (2) | [F06-OS1.2,OS1.5] [F05-OS1.5] |
|  | [F06-OP1.2] |
| (3) | [F06-OS1.5,OS1.2] [F05-OS1.5] |
|  | [F06-OP1.2] |
| (4) | [F03-OS1.2,OS1.5] |
|  | [F03-OP1.2] |
| (5) | [F03-OS1.2,OS1.5] |
|  | [F03-OP1.2] |
| (6) | [F03,F12-OS1.2,OS1.5] |
|  | [F03,F12-OP1.2] |
| 3.2.6.3. Connected Buildings |  |
| (1) | [F03-OS1.2,OS1.5] |
|  | [F03-OP1.2] |
|  | [F03-OP3.1] |
| 3.2.6.4. Emergency Operation of Elevators |  |
| (1) | [F12-OS1.2,OS1.5] |
|  | [F12-OP1.2] |
| (2) | [F12-OS1.2,OS1.5] |
|  | [F12-OP1.2] |
| (3) | [F12-OS1.2,OS1.5] |
|  | [F12-OP1.2] |
| (4) | [F12-OS1.2,OS1.5] |
|  | [F12-OP1.2] |
| 3.2.6.5. Elevator for Use by Firefighters |  |
| (1) | [F12,F06-OS1.2,OS1.5] |
|  | [F12,F06-OP1.2] |
| (2) | [F12-OS1.2,OS1.5] |
|  | [F12-OP1.2] |
| (3) | [F06-OS1.2,OS1.5] |
|  | [F06-OP1.2] |
| (4) | [F12-OS1.2,OS1.5] |
|  | [F12-OP1.2] |
| (5) | [F12-OS1.2,OS1.5] |
|  | [F12-OP1.2] |
| (6) | [F06-OS1.2,OS1.5] |
|  | [F06-OP1.2] |
| 3.2.6.6. Venting to Aid Firefighting |  |
| (1) | [F06-OS1.2,OS1.5] |
|  | [F06-OP1.2] |
| (2) | [F30-OS3.1] |
| (3) | [F12-OS1.2,OS1.5] |
|  | [F12-OP1.2] |
| (4) | [F03-OS1.2] [F12-OS1.2,OS1.5] |
| 3.2.6.7. Central Alarm and Control Facility |  |
| (1) | [F12-OS1.2,OS1.5] |
|  | [F12-OP1.2] |
| (2) | [F12-OS1.2,OS1.5] [F11-OS1.5] |
|  | [F12-OP1.2] |
| 3.2.6.8. Voice Communication System |  |
| (1) | [F12,F11-OS3.7] |
| 3.2.6.9. Testing |  |
| (1) | [F82-OS1.2,OS1.5] |
|  | [F82-OP1.2] |
| 3.2.7.1. Minimum Lighting Requirements |  |
| (1) | [F30-OS3.1] [F10-OS3.7] |
| (2) | [F30-OS3.1] [F10-OS3.7] |
| (4) | [F30-OS3.1] |
| (5) | [F74-OA2] |
| (6) | [F74-OA2] |
| (7) | [F10-OS3.7] |
|  | [F74-OA2] |
|  | [F30-OS3.1] |
| 3.2.7.2. Recessed Lighting Fixtures |  |
| (1) | [F01-OS1.1,OS1.2] |
|  | [F01-OP1.1,OP1.2] |
| 3.2.7.3. Emergency Lighting |  |
| (1) | [F30-OS3.1] [F10-OS3.7] |
| (2) | [F30-OS3.1] [F10-OS3.7] |
| (3) | [F30-OS3.1] [F10-OS3.7] |
| (4) | [F30-OS3.1] [F10-OS3.7] |
| 3.2.7.4. Emergency Power for Lighting |  |
| (1) | [F30-OS3.1] [F10-OS3.7] |
| (2) | [F30,F81-OS3.1] [F10,F81-OS3.7] |
| 3.2.7.5. Emergency Power Supply Installation |  |
| (1) | [F81,F06,F11,F02,F03,F10,F12-OS1.2,OS1.5] |
|  | [F81,F06,F02,F03-OP1.2] |
|  | [F81,F06,F02-OP3.1] |
|  | [F81,F30-OS3.1] [F81,F11,F10,F12-OS3.7] |
| 3.2.7.6. Emergency Power for Treatment Occupancies |  |
| (1) | [F81,F06,F11,F02,F03,F10,F12-OS1.2,OS1.5] |
|  | [F81,F06,F02,F03-OP1.2] |
|  | [F81,F06,F02-OP3.1] |
|  | [F81,F30-OS3.1] [F81,F11,F10,F12-OS3.7] |
| 3.2.7.7. Fuel Supply Shut-off Valves |  |
| (1) | [F12-OS1.1,OS1.2] Applies to the requirement for a suitably identified shut-off valve outside the building. |
|  | [F12-OP1.2] Applies to the requirement for a suitably identified shut-off valve outside the building. |
|  | [F12-OH5] Applies to the requirement for a suitably identified shut-off valve outside the building. |
|  | [F81-OS1.2,OS1.5] Applies to the requirement for a suitably identified separate shut-off valve. |
|  | [F81-OS3.1,OS3.7] Applies to the requirement for a suitably identified separate shut-off valve. |
| 3.2.7.8. Emergency Power for Fire Alarm Systems |  |
| (1) | [F11-OS1.5] [F13-OS1.5,OS1.2] |
|  | [F13-OP1.2] Applies to the requirement for fire alarm systems, including those with a voice communication system, to be provided with an emergency power supply. |
| (2) | [F11-OS1.5] [F13-OS1.2,OS1.5] |
|  | [F13-OP1.2] |
| (3) | [F11-OS1.5] [F13-OS1.5,OS1.2] |
|  | [F13-OP1.2] |
| (4) | [F13-OP1.2] |
|  | [F11-OS1.5] [F13-OS1.2,OS1.5] |
| 3.2.7.9. Emergency Power for Building Services |  |
| (1) | [F12,F02,F03-OS1.5,OS1.2] |
|  | [F12,F02,F03-OP1.2] |
|  | (b) [F02-OP3.1] |
|  | (a) [F36-OS3.6] [F12,F10-OS3.7] |
| (2) | [F12-OS1.5,OS1.2] |
|  | [F12-OP1.2] |
|  | [F36-OS3.6] [F12-OS3.7] |
| 3.2.7.10. Protection of Electrical Conductors |  |
| (2) | [F06-OS1.2,OS1.5] |
|  | [F06-OP1.2] |
| (3) | [F06-OS1.2,OS1.5] |
|  | [F06-OP1.2] |
| (4) | [F06-OS1.2,OS1.5] |
|  | [F06-OP1.2] |
| (6) | [F06-OS1.2,OS1.5] |
|  | [F06-OP1.2] |
| (8) | [F06-OS1.2,OS1.5] |
|  | [F06-OP1.2] |
| (10) | [F06-OS1.4] |
|  | [F06-OP1.2] |
|  | [F10-OS3.7] |
| 3.2.8.1. Application |  |
| (1) | [F03,F06-OS1.2] [F05-OS1.5] |
|  | [F03,F06-OP1.2] |
| 3.2.8.2. Exceptions to Special Protection |  |
| (3) | [F03-OS1.2] |
|  | [F03-OP1.2] |
| (5) | [F02,F03-OS1.2] |
|  | [F02,F03-OP1.2] |
| 3.2.8.3. Sprinklers |  |
| (1) | [F02-OS1.2] |
|  | [F02-OP1.2] |
| (2) | [F02-OS1.2] [F11-OS1.5] [F13-OS1.5,OS1.2] |
|  | [F02,F13-OP1.2] |
| 3.2.8.4. Vestibules |  |
| (1) | [F06-OS1.2] [F05-OS1.5] |
|  | [F06,F03-OP1.2] |
| 3.2.8.5. Protected Floor Space |  |
| (1) | [F05-OS1.2] [F06-OS1.5] |
| 3.2.8.6. Draft Stops |  |
| (1) | [F02-OS1.2] [F11-OS1.5] [F13-OS1.5,OS1.2] |
|  | [F02,F13-OP1.2] |
| 3.2.8.7. Mechanical Exhaust System |  |
| (1) | [F03-OS1.5,OS1.2] |
|  | [F03-OP1.2] |
| (2) | [F12-OS1.5,OS1.2] |
|  | [F12-OP1.2] |
| 3.2.8.8. Combustible Content Limits |  |
| (1) | [F02-OS1.2] |
|  | [F02-OP1.2] |
| 3.2.9.1. Testing |  |
| (1) | [F02,F81,F82-OS1.2,OS1.5] |
|  | [F02,F81,F82-OP1.2] |
| 3.3.1.1. Separation of Suites |  |
| (1) | [F03-OS1.2] |
|  | [F03-OP1.2] |
| (3) | [F02-OS1.2] |
|  | [F02-OP1.2] |
| 3.3.1.2. Hazardous Substances, Equipment and Processes |  |
| (1) | [F01,F02,F03-OS1.1,OS1.2] |
|  | [F01,F02,F03-OP1.1,OP1.2] |
|  | [F43-OS3.4] |
| (3) | [F43-OS3.7] |
|  | [F05-OS1.5] |
| 3.3.1.3. Means of Egress |  |
| (3) | [F10-OS3.7] |
| (4) | [F10,F12,F05,F06-OS3.7] |
| (5) | [F10,F12-OS3.7] |
| (6) | [F10,F12,F05,F06-OS3.7] |
| (7) | [F10,F12,F05,F06-OS3.7] |
| (8) | [F05-OS1.5] |
| (9) | [F10,F12,F05,F06-OS3.7] |
| 3.3.1.4. Public Corridor Separations |  |
| (1) | [F03,F05-OS1.5] [F06-OS1.5,OS1.2] |
|  | [F03,F06-OP1.2] |
| (2) | [F03,F05-OS1.5] [F06-OS1.5,OS1.2] |
|  | [F03,F06-OP1.2] |
| (3) | [F03,F05-OS1.5] [F06-OS1.2,OS1.5] |
|  | [F03,F06-OP1.2] |
| (4) | (a),(b) [F03,F05,F10-OS1.5] [F06,F12-OS1.2,OS1.5] (c) [F03,F05-OS1.5] [F03,F06-OS1.5,OS1.2] |
|  | (a),(b) [F03,F06,F12-OP1.2] (c) [F03,F06-OP1.2] |
| 3.3.1.5. Egress Doorways |  |
| (1) | [F10,F05-OS1.5] |
| (2) | [F05,F10-OS1.5] |
| 3.3.1.6. Travel Distance |  |
| (1) | [F10-OS1.5] |
| 3.3.1.7. Protection on Floor Areas with a Barrier-Free Path of Travel |  |
| (1) | [F10,F05-OS1.5] |
|  | (a) [F06-OS1.5] |
| (2) | [F03-OS1.2] [F06-OS1.5] |
| (4) | (a) [F10,F73-OS1.5] |
|  | (b),(c) [F10-OS1.5] |
| 3.3.1.8. Headroom and Protruding Objects |  |
| (2) | [F30,F73-OS3.1] |
| 3.3.1.9. Corridors |  |
| (1) | [F10,F12-OS3.7] |
| (2) | [F10,F12-OS3.7] |
| (3) | [F10,F12-OS3.7] |
| (4) | (a) [F10,F12-OS3.7] |
|  | (b) [F05-OS1.5] [F06-OS1.5,OS1.2] |
| 3.3.1.11. Door Swing |  |
| (1) | [F10-OS3.7] |
| (2) | [F10-OS3.7] |
| (3) | [F10-OS3.7] |
| (4) | [F10-OS3.7] |
| 3.3.1.12. Sliding Doors |  |
| (1) | (b) [F10-OS3.7] |
| 3.3.1.13. Doors and Door Hardware |  |
| (1) | (a),(b) [F10,F12-OS3.7] [F30-OS3.1] |
|  | (c) [F10-OS3.7] [F30-OS3.1] |
|  | (d) [F10-OS3.7] |
| (2) | [F10-OS3.7] |
| (3) | [F10-OS3.7] |
| (4) | [F10-OS3.7] |
| (5) | [F10-OS3.7] |
|  | [F73-OA1] |
| (8) | [F12-OS3.7] |
| (9) | [F12-OS3.7] |
| (10) | [F12-OS3.7] |
| 3.3.1.16. Tapered Treads in a Curved Flight |  |
| (2) | [F30-OS3.1] [F10-OS3.7] |
| (3) | [F30-OS3.1] [F10-OS3.7] |
| (4) | [F30-OS3.1] [F10-OS3.7] |
| 3.3.1.17. Capacity of Access to Exits |  |
| (2) | [F10-OS3.7] |
| (3) | [F10-OS3.7] |
| (4) | [F10-OS3.7] |
| (6) | [F10-OS3.7] |
| 3.3.1.18. Guards |  |
| (1) | [F30-OS3.1] |
| (2) | [F30-OS3.1] |
| (3) | [F30-OS3.1] |
| (4) | [F30-OS3.1] |
| 3.3.1.19. Tactile Walking Surface Indicators |  |
| (1) | [F30-OS3.1] |
| 3.3.1.20. Transparent Doors and Panels |  |
| (1) | [F30-OS3.1] [F10-OS3.7] |
| (2) | [F30-OS3.1] [F10-OS3.7] |
| (3) | [F20-OS3.1] |
| (4) | [F30-OS3.1] [F10-OS3.7] |
| (6) | [F30-OS3.1] [F10-OS3.7] |
| (8) | [F30-OS3.1] |
| 3.3.1.21. Exhaust Ventilation and Explosion Venting |  |
| (1) | [F01-OS1.1] |
| (2) | (a) [F02-OS1.2] |
|  | (a) [F02-OP1.2] |
| (3) | [F02-OS1.3] Applies to the requirement for explosion-relief devices and vents. |
|  | [F02-OP1.3] Applies to the requirement for explosion-relief devices and vents. |
| 3.3.1.22. Janitors' Rooms |  |
| (1) | [F03-OS1.2] |
|  | [F03-OP1.2] |
| (3) | [F02-OS1.2] |
|  | [F02-OP1.2] |
| 3.3.1.23. Common Laundry Rooms |  |
| (1) | [F03-OS1.2] |
|  | [F03-OP1.2] |
| (3) | [F02-OS1.2] |
|  | [F02-OP1.2] |
| 3.3.1.24. Obstructions |  |
| (1) | [F10-OS3.7] |
| 3.3.1.25. Signs in Service Spaces |  |
| (1) | [F10-OS3.7] |
| 3.3.1.26. Welding and Cutting |  |
| (1) | [F03,F02-OS1.2] |
|  | [F03,F02-OP1.2] |
| 3.3.2.1. Scope |  |
| (2) | [F30-OS3.1] [F10-OS3.7] |
| (3) | [F30-OS3.1] [F10-OS3.7] |
| 3.3.2.2. Fire Separations |  |
| (1) | [F03-OS1.2] |
| (3) | [F03-OS1.2] Applies where space under tiers of seats is not sprinklered. |
|  | [F03-OS1.2] Applies where space under tiers of seats is sprinklered. |
| 3.3.2.4. Fixed Seats |  |
| (1) | [F30-OS3.1] [F10-OS3.7] |
| (3) | [F10-OS3.7] |
| 3.3.2.5. Aisles |  |
| (2) | [F10-OS3.7] |
| (4) | [F10-OS3.7] |
| (5) | [F10-OS3.7] |
| (6) | [F10-OS3.7] |
| (7) | [F10-OS3.7] |
| (8) | [F10-OS3.7] [F30-OS3.1] |
| (9) | [F10-OS3.7] [F30-OS3.1] |
| (10) | [F10-OS3.7] [F30-OS3.1] |
| (11) | [F10-OS3.7] [F30-OS3.1] |
| (12) | [F10-OS3.7] [F30-OS3.1] |
| (13) | [F10-OS3.7] [F30-OS3.1] |
| (14) | [F10-OS3.7] [F30-OS3.1] |
| (15) | [F10-OS3.7] [F30-OS3.1] |
| (16) | [F10-OS3.7] [F30-OS3.1] |
| 3.3.2.6. Corridors |  |
| (1) | [F03,F05-OS1.5] [F06-OS1.5,OS1.2] |
|  | [F03,F06-OP1.2] |
| (3) | [F03,F05-OS1.5] [F06-OS1.5,OS1.2] |
|  | [F03,F06-OP1.2] |
| (4) | [F10-OS3.7] |
| 3.3.2.7. Doors |  |
| (1) | [F10-OS3.7] |
| 3.3.2.8. Fixed Bench-Type Seats without Arms |  |
| (1) | [F10-OS3.7] |
|  | [F10-OS3.7] |
| 3.3.2.10. Handrails in Aisles with Steps |  |
| (1) | [F30-OS3.1] [F10-OS3.7] |
| (2) | [F30-OS3.1] [F10-OS3.7] |
| 3.3.2.11. Outdoor Places of Assembly |  |
| (1) | [F10-OS3.7] |
| (2) | [F10-OS3.7] |
| (3) | [F10-OS3.7] |
| (5) | [F10-OS3.7] |
| 3.3.2.12. Bleachers |  |
| (1) | [F10-OS3.7] [F30-OS3.1] |
| (2) | [F10-OS3.7] [F30-OS3.1] |
| (4) | [F10-OS3.7] [F30-OS3.1] |
| (5) | [F30-OS3.1] |
| 3.3.2.13. Libraries |  |
| (1) | [F03-OS1.2] |
|  | [F03-OP1.2] |
| (2) | [F02-OS1.2] |
|  | [F02-OP1.2] |
| 3.3.2.14. Stages for Theatrical Performances |  |
| (1) | [F02-OS1.2] |
|  | [F02-OP1.2] |
| (2) | [F03-OS1.2] |
|  | [F03-OP1.2] |
| (3) | [F03-OS1.2] |
|  | [F03-OP1.2] |
| (4) | [F03-OS1.2] |
|  | [F03-OP1.2] |
| (5) | [F02-OS1.2] [F06-OS1.2,OS1.5] |
|  | [F02,F06-OP1.2] |
| (6) | [F03-OS1.2,OS1.5] |
|  | [F03-OP1.2] |
| 3.3.2.15. Risers for Stairs |  |
| (1) | [F30-OS3.1] |
| 3.3.2.16. Storage Rooms |  |
| (1) | [F12-OS1.2] |
|  | [F12-OP1.2] |
| 3.3.2.17. Safety Glazing |  |
| (1) | [F20,F30-OS3.1] |
| (2) | [F20,F30-OS3.1] |
| 3.3.2.18. Daycare Facilities with Children under 30 Months |  |
| (1) | (a) [F02,F03,F05-OS1.2,OS1.3] |
|  | (b) [F10-OS1.5] |
| (2) | [F11-OS1.5] |
| (3) | [F11-OS1.5] |
| (4) | [F11-OS1.5] |
|  | [F81-OS1.4] |
| (5) | [F11-OS1.5] |
|  | [F81-OS1.4] |
| 3.3.3.2. Separations between Care, Treatment or Detention Occupancies and Repair Garages |  |
| (1) | [F44-OS3.4] |
|  | [F03-OS1.2] |
| 3.3.3.3. Corridors |  |
| (1) | [F10-OS3.7] |
| (2) | [F10-OS3.7] |
| (3) | [F10,F12-OS3.7] |
| (4) | (a) [F10-OS3.7] |
|  | (b) [F10,F12-OS3.7] |
| 3.3.3.4. Doorway Width |  |
| (1) | [F10,F12-OS3.7] |
| (2) | [F10,F12-OS3.7] |
| 3.3.3.5. Compartments and Fire Separations |  |
| (2) | [F05-OS1.5] [F06-OS1.5,OS1.2] |
|  | [F06-OP1.2] |
| (4) | [F05-OS1.2] [F06-OS1.2,OS1.5] |
|  | [F03,F06-OP1.2] |
| (6) | [F10-OS1.5] |
| (7) | [F10-OS1.5] |
| (8) | [F03,F05-OS1.2] [F06-OS1.5] |
| (12) | [F03,F05-OS1.2] [F06-OS1.5] |
| (16) | [F02,F03-OS1.2] [F44-OS1.1] |
|  | [F02,F03-OP1.2] |
| 3.3.3.6. Areas of Refuge |  |
| (1) | [F03-OS1.2] |
| 3.3.3.7. Contained Use Areas |  |
| (2) | [F03-OS1.2] [F06-OS1.5,OS1.2] |
|  | [F03,F06-OP1.2] |
| (3) | [F02-OS1.2] [F06-OS1.5,OS1.2] |
|  | [F02,F06-OP1.2] |
| (4) | [F02-OS1.2] [F06-OS1.5,OS1.2] |
|  | [F02,F06-OP1.2] |
| (5) | [F10-OS3.7] |
| 3.3.4.2. Fire Separations |  |
| (1) | [F03-OS1.2] [F05-OS1.5] [F06-OS1.5,OS1.2] |
|  | [F03,F06-OP1.2] |
| (4) | [F02,F03-OS1.2] [F44-OS1.1] |
|  | (a),(b) [F02,F03-OP1.2] |
| (5) | [F03-OS1.2] [F01-OS1.1] |
|  | (a) [F03-OP1.2] |
|  | [F44-OS3.4] |
| 3.3.4.3. Storage Rooms |  |
| (1) | [F02-OS1.2] |
|  | [F02-OP1.2] |
| (2) | [F03-OS1.2] |
|  | [F03-OP1.2] |
| (4) | [F12-OS1.2] |
|  | [F12-OP1.2] |
| 3.3.4.4. Egress from Dwelling Units |  |
| (2) | [F10,F05-OS3.7] |
| (3) | [F10-OS3.7] |
| (4) | [F05-OS1.2,OS1.5] |
| (5) | [F10,F05-OS3.7] |
| (6) | [F10,F05-OS3.7] |
| 3.3.4.5. Automatic Locking Prohibition |  |
| (1) | [F10-OS3.7] |
| 3.3.4.8. Protection of Openable Windows |  |
| (1) | [F30-OS3.1] |
| 3.3.5.2. Fire Extinguishing Systems |  |
| (1) | [F03-OS1.2] |
|  | [F03-OP1.2] |
| 3.3.5.3. Basements |  |
| (1) | [F12-OS1.2,OS1.5] [F01-OS1.1] |
|  | [F12-OP1.2] |
| (2) | [F06-OS1.5,OS1.2] Applies to the separation of entrances to basements and to rooms containing building services from the remainder of the building. |
|  | [F06-OP1.2] Applies to the separation of entrances from the remainder of the building. |
|  | [F05-OS1.5] [F06-OS1.2,OS1.5] Applies to the separation of exits from the remainder of the building. |
|  | [F06-OP1.2] Applies to the separation of exits from the remainder of the building. |
| (3) | [F44-OS1.1] |
| 3.3.5.4. Repair and Storage Garages |  |
| (2) | [F30-OS3.1] [F10,F12-OS3.7] |
| (5) | [F30-OS3.1] |
| (6) | [F30-OS3.1] |
| (8) | [F02-OS1.2] |
|  | [F02-OP1.2] |
| 3.3.5.5. Repair Garage Separation |  |
| (1) | [F03-OS1.2] |
|  | [F03-OP1.2] |
| 3.3.5.6. Storage Garage Separation |  |
| (1) | [F03-OS1.2] |
|  | [F03-OP1.2] |
| 3.3.5.7. Vestibules |  |
| (4) | [F44-OS3.4] |
|  | [F44-OS1.1] |
| 3.3.5.8. Dispensing of Fuel |  |
| (1) | [F01-OS1.1] |
| (2) | [F01-OS1.1] |
| 3.3.5.9. Multiple-Tenant Self-Storage Warehouses |  |
| (1) | [F03-OS1.2] |
|  | [F03-OP1.2] |
| 3.3.6.2. Storage of Dangerous Goods |  |
| (1) | [F03-OP1.2] |
|  | [F03-OS1.2] |
| (2) | [F03-OS1.2] |
|  | [F03-OP1.2] |
| (3) | [F01,F02,F03,F81-OS1.1,OS1.2] |
|  | [F01,F02,F03,F81-OP1.1,OP1.2] |
| (4) | [F01-OS1.1] |
|  | [F01-OP1.1] |
| 3.3.6.3. Indoor Storage of Anhydrous Ammonia and Flammable, Toxic and Oxidizing Gases |  |
| (1) | (a) [F03-OS1.2] [F44-OS1.1] |
|  | (a) [F03-OP1.2] |
|  | (a) [F44-OS1.2,OS1.5,OS1.1] Applies to gas-tight fire separations. |
|  | (b) [F12-OS1.2] [F01-OS1.1] [F02-OS1.3] |
|  | (b) [F02-OP1.3] |
|  | (c) [F12-OS1.1] |
|  | (d) [F44-OS1.1] |
| (2) | (a) [F03-OP1.2] |
|  | (a) [F03-OS1.2] [F44-OS1.1] |
|  | (a) [F44-OS1.2,OS1.5,OS1.1] Applies to gas-tight fire separations. |
|  | (b) [F12-OS1.2] [F01-OS1.1] |
|  | (c) [F12-OS1.1] |
|  | (d) [F44-OS1.1] |
| 3.3.6.4. Storage and Dispensing Rooms for Flammable Liquids and Combustible Liquids |  |
| (1) | [F03-OS1.2] |
|  | [F03-OP1.2] |
| (2) | [F02-OS1.3] |
|  | [F02-OP1.3] |
| 3.3.6.5. Tire Storage |  |
| (1) | [F03-OS1.2] |
|  | [F03-OP1.2] |
| 3.3.6.6. Ammonium Nitrate Storage |  |
| (2) | [F01-OS1.1] [F02,F12-OS1.2] |
|  | [F01-OP1.1] [F02,F12-OP1.2] |
| (3) | [F03-OS1.2] [F01-OS1.1] |
|  | [F03-OP1.2] [F01-OP1.1] |
| (4) | [F12,F02-OS1.1] |
|  | [F12,F02-OP1.2] |
| (5) | [F44-OH5] |
|  | [F01-OS1.1] [F02-OS1.2] |
|  | [F43-OS3.4] |
| (6) | [F01,F81-OS1.1] |
| 3.3.6.7. Flooring Materials |  |
| (1) | [F43-OS3.4] |
|  | [F44-OH5] |
|  | [F01-OS1.1] |
| 3.3.6.8. Fire Separations in Process Plants |  |
| (1) | [F03-OP1.2] |
|  | [F03-OS1.2] |
| 3.3.6.9. Basements and Pits |  |
| (1) | [F01-OS1.1] |
|  | [F01-OP1.1] |
| 3.4.1.2. Separation of Exits |  |
| (1) | [F10,F12,F05,F06-OS3.7] |
|  | [F12,F06-OP1.2] |
|  | [F12,F06-OS1.5,OS1.2] |
| (2) | [F10-OS3.7] |
| 3.4.1.5. Exterior Exit Passageways |  |
| (1) | [F10-OS3.7] |
| 3.4.1.6. Restricted Use of Horizontal Exits |  |
| (1) | [F10-OS3.7] |
| (2) | [F10,F05-OS3.7] |
| 3.4.1.7. Slide Escapes |  |
| (1) | [F10-OS3.7] |
| 3.4.1.9. Mirrors near Exits |  |
| (1) | [F10-OS3.7] [F30-OS3.1] |
| 3.4.1.10. Combustible Glazing in Exits |  |
| (1) | [F05-OS1.2] [F06-OS1.2,OS1.5] |
|  | [F03,F06-OP1.2] |
| 3.4.2.1. Minimum Number of Exits |  |
| (1) | [F10,F12,F05,F06-OS3.7] |
|  | [F12,F06-OS1.2] |
|  | [F12,F06-OP1.2] |
| (3) | [F10-OS3.7] |
| 3.4.2.2. Means of Egress from Mezzanines |  |
| (1) | [F05-OS1.5] |
| 3.4.2.3. Distance between Exits |  |
| (1) | [F10,F05-OS1.5] |
| (4) | [F10-OS3.7] |
| 3.4.2.4. Travel Distance |  |
| (3) | [F10-OS3.7] |
| 3.4.2.5. Location of Exits |  |
| (1) | [F10-OS3.7] |
| (3) | [F10-OS3.7] |
| 3.4.2.6. Principal Entrances |  |
| (1) | [F10-OS3.7] |
| (2) | [F10-OS3.7] |
| 3.4.3.1. Exit Width Based on Occupant Load |  |
| (2) | [F10-OS3.7] |
| 3.4.3.2. Exit Width |  |
| (1) | [F10-OS3.7] |
| (2) | [F10-OS3.7] |
| (3) | [F10-OS3.7] |
| (6) | [F10-OS3.7] |
| (7) | [F10-OS3.7] |
| (8) | [F12,F10-OS3.7] [F30-OS3.1] |
|  | [F12-OP1.2] |
|  | [F12-OS1.2] |
| 3.4.3.3. Exit Width Reduction |  |
| (1) | [F10,F12-OS3.7] [F30-OS3.1] |
|  | [F12-OP1.2] |
|  | [F12-OS1.2] |
| (2) | [F10,F12-OS3.7] |
|  | [F12-OP1.2] |
|  | [F12-OS1.2] |
| (3) | [F10,F12-OS3.7] |
|  | [F12-OP1.2] |
|  | [F12-OS1.2] |
| (4) | [F10,F12-OS3.7] |
|  | [F12-OP1.2] |
|  | [F12-OS1.2] |
| 3.4.3.4. Headroom Clearance |  |
| (1) | [F30-OS3.1] [F10,F12-OS3.7] |
|  | [F12-OP1.2] |
|  | [F12-OS1.2] |
| (4) | [F30-OS3.1] [F10,F12-OS3.7] |
|  | [F12-OP1.2] |
|  | [F12-OS1.2] |
| (5) | [F30-OS3.1] [F10,F12-OS3.7] |
|  | [F12-OP1.2] |
|  | [F12-OS1.2] |
| 3.4.4.1. Fire-Resistance Rating of Exit Separations |  |
| (1) | [F05-OS1.5] [F06-OS1.5,OS1.2] [F03-OS1.2] |
|  | [F06,F03-OP1.2] |
| 3.4.4.2. Exits through Lobbies |  |
| (1) | [F05,F06-OS1.5] |
| (2) | [F12,F10,F05,F06-OS1.5] |
| 3.4.4.3. Exterior Passageway Exceptions |  |
| (1) | [F05,F06,F10-OS1.5] |
| 3.4.4.4. Integrity of Exits |  |
| (1) | [F05-OS1.5] [F06-OS1.5,OS1.2] [F03-OS1.2] |
|  | [F06,F03-OP1.2] |
| (2) | [F05-OS1.5] [F06-OS1.5,OS1.2] |
|  | [F06-OP1.2] |
| (3) | [F05-OS1.5] [F06-OS1.5,OS1.2] |
|  | [F06-OP1.2] |
| (4) | [F05-OS1.5] [F06-OS1.5,OS1.2] |
|  | [F06-OP1.2] |
|  | [F43-OS3.7] |
| (5) | [F05-OS1.5] [F06-OS1.5,OS1.2] [F03-OS1.2] |
|  | [F03,F06-OP1.2] |
| (6) | [F10,F12-OS3.7] [F30-OS3.1] [F31-OS3.2] [F32-OS3.3] [F43-OS3.4] |
|  | [F10,F05-OS1.5] [F12-OS1.5,OS1.2] |
|  | [F12-OP1.2] |
| (7) | [F05-OS1.5] [F06-OS1.5,OS1.2] |
|  | [F06-OP1.2] |
|  | [F43-OS3.7] |
| (8) | [F05-OS1.5] [F06-OS1.5,OS1.2] |
|  | [F06-OP1.2] |
| (9) | [F05-OS1.5] [F06-OS1.5,OS1.2] |
|  | [F06-OP1.2] |
| 3.4.5.1. Exit Signs |  |
| (1) | [F10-OS3.7] |
| (2) | [F10-OS3.7] |
| (3) | [F10,F81-OS3.7] |
| (4) | [F10,F81-OS3.7] |
| (5) | [F10-OS3.7] |
| (6) | [F10-OS3.7] |
| (7) | [F10-OS3.7] |
| 3.4.5.2. Exit Signs with Tactile Information |  |
| (1) | [F10-OS3.7] |
| 3.4.5.3. Signs for Stairs and Ramps at Exit Level |  |
| (1) | [F10-OS3.7] |
| 3.4.6.1. Slip Resistance of Ramps and Stairs |  |
| (1) | (a) [F10-OS3.7] [F30-OS3.1] |
|  | (b) [F10-OS3.7] [F30-OS3.1] |
| (2) | [F10,F12-OS3.7] [F30-OS3.1] |
|  | [F12-OP1.2] |
|  | [F12-OS1.2,OS1.5] |
| 3.4.6.2. Minimum Number of Risers |  |
| (1) | [F30-OS3.1] |
| 3.4.6.3. Maximum Vertical Rise of Stair Flights and Required Landings |  |
| (1) | [F10-OS3.7] |
| (2) | [F10-OS3.7] [F30-OS3.1] |
| (3) | [F10,F12-OS3.7] [F30-OS3.1] |
| 3.4.6.4. Dimensions of Landings |  |
| (1) | [F10,F12-OS3.7] [F30-OS3.1] |
|  | [F12-OP1.2] |
|  | [F12-OS1.2,OS1.5] |
| (2) | [F10,F12-OS3.7] [F30-OS3.1] |
|  | [F12-OP1.2] |
|  | [F12-OS1.2,OS1.5] |
| (4) | [F10,F12-OS3.7] [F30-OS3.1] |
| (5) | [F10,F12-OS3.7] [F30-OS3.1] |
| 3.4.6.5. Handrails |  |
| (1) | [F10-OS3.7] [F30-OS3.1] |
| (2) | [F10-OS3.7] [F30-OS3.1] |
| (3) | [F10-OS3.7] [F30-OS3.1] |
| (4) | [F10-OS3.7] [F30-OS3.1] |
| (5) | [F30-OS3.1] [F10-OS3.7] |
| (7) | [F30-OS3.1] [F10-OS3.7] |
| (9) | [F10-OS3.7] [F30-OS3.1] |
| (10) | [F30-OS3.1] [F10-OS3.7] |
|  | [F73-OA1] |
| (11) | [F30-OS3.1] [F10-OS3.7] |
| (12) | [F30-OS3.1] [F10-OS3.7] |
|  | [F73-OA1] |
| (13) | [F30-OS3.1] [F10-OS3.7] |
| (15) | [F30-OS3.1] [F10-OS3.7] |
| 3.4.6.6. Guards |  |
| (1) | [F30-OS3.1] [F10-OS3.7] |
| (2) | [F30-OS3.1] [F10-OS3.7] |
| (4) | [F30-OS3.1] [F10-OS3.7] |
| (5) | [F30-OS3.1] |
| (6) | [F30-OS3.1] |
| (7) | [F30-OS3.1] |
| 3.4.6.7. Ramp Slope |  |
| (1) | [F10-OS3.7] [F30-OS3.1] |
| (2) | [F10-OS3.7] [F30-OS3.1] |
| 3.4.6.8. Treads and Risers |  |
| (1) | [F10-OS3.7] [F30-OS3.1] |
| (2) | [F10-OS3.7] [F30-OS3.1] |
| (3) | [F10-OS3.7] [F30-OS3.1] |
|  | [F73-OA1] |
| (4) | [F10-OS3.7] [F30-OS3.1] |
| (5) | [F30-OS3.1] [F10-OS3.7] |
| (6) | [F30-OS3.1] [F10-OS3.7] |
| (7) | [F30-OS3.1] [F10-OS3.7] |
| (8) | [F30-OS3.1] |
| (9) | [F10-OS3.7] [F30-OS3.1] |
| (10) | [F30-OS3.1] |
| 3.4.6.9. Curved Flights in Exits |  |
| (1) | [F10-OS3.7] [F30-OS3.1] |
| (2) | [F10-OS3.7] [F30-OS3.1] |
| (3) | [F10-OS3.7] [F30-OS3.1] |
| (4) | [F30-OS3.1] [F10-OS3.7] |
| 3.4.6.10. Horizontal Exits |  |
| (1) | [F10-OS3.7] |
| (2) | [F10-OS3.7] |
| (4) | [F10,F73-OS3.7] |
| (5) | [F10-OS3.7] |
| 3.4.6.11. Doors |  |
| (1) | [F30-OS3.1] [F10-OS3.7] |
| (2) | [F10-OS3.7] [F30-OS3.1] |
| (3) | [F30-OS3.1] [F10-OS3.7] |
|  | [F81,F10-OS3.7] Applies where there is a danger of blockage from ice or snow. |
| (4) | [F10-OS3.7] |
| (5) | [F10,F12-OS3.7] |
| (6) | [F10-OS3.7] |
| 3.4.6.12. Direction of Door Swing |  |
| (1) | [F10-OS3.7] |
| 3.4.6.13. Self-closing Devices |  |
| (1) | [F05-OS1.5] [F06-OS1.5,OS1.2] |
|  | [F06,F03-OP1.2] |
| 3.4.6.14. Sliding Doors |  |
| (2) | [F12-OS3.7] |
| 3.4.6.15. Revolving Doors |  |
| (1) | (a) [F30-OS3.1] [F10-OS3.7] |
|  | (b) [F10,F12-OS3.7] |
|  | (c) [F10-OS3.7] |
|  | (d) [F30-OS3.1] [F10-OS3.7] |
|  | (e) [F20-OS3.1] |
| (2) | [F10-OS3.7] |
| (3) | (a),(b),(d),(e) [F10,F81-OS3.7] [F20,F30-OS3.1] |
| 3.4.6.16. Door Release Hardware |  |
| (1) | [F10-OS3.7] |
| (2) | [F10-OS3.7] |
| (3) | [F10-OS3.7] |
| (4) | [F10-OS3.7] |
| (5) | [F10,F81-OS3.7] |
| (6) | [F10,F81-OS3.7] |
| (7) | [F10-OS3.7] |
|  | [F73-OA1] |
| 3.4.6.17. Security for Banks and Mercantile Floor Areas |  |
| (1) | [F02-OS1.2] Applies to sprinklered buildings. |
|  | [F10,F81-OS3.7] Applies to exit and egress doors that comply with the stated Sentences. |
| (2) | [F10-OS3.7] |
| (3) | [F81-OS3.7] |
| (5) | [F10-OS1.5] |
| (6) | [F10-OS3.7] |
| (9) | [F10,F81-OS3.7] |
| 3.4.6.18. Emergency Crossover Access to Floor Areas |  |
| (1) | [F10-OS3.7] |
| (3) | [F10-OS3.7] |
| (4) | [F10-OS3.7] |
|  | [F12-OS3.7] |
|  | [F12-OP1.2] |
|  | [F12-OS1.2,OS1.5] |
| (5) | [F10-OS3.7] |
| 3.4.6.19. Floor Numbering and Identification of Stair Shafts |  |
| (1) | [F10,F12,F73-OS3.7] |
|  | [F73-OA1] |
|  | [F12-OP1.2] |
|  | [F12-OS1.2] |
| (2) | [F10,F12,F73-OS3.7] |
|  | [F12-OP1.2] |
|  | [F12-OS1.2] |
| 3.4.7.1. Scope |  |
| (1) | [F10,F12-OS3.7] |
| (2) | [F10-OS3.7] [F30-OS3.1] |
|  | [F10-OS1.5] [F12-OS1.2] |
| 3.4.7.2. Fire Escape Construction |  |
| (1) | [F05-OS1.5] [F06-OS1.2] Applies to the combustibility of materials used in the construction of fire escapes. |
|  | [F10,F12-OS3.7] [F20-OS3.1] Applies to the type and construction of fire escapes. |
|  | [F20-OS2.1] Applies to the type and construction of fire escapes. |
| 3.4.7.3. Access to Fire Escapes |  |
| (1) | [F10-OS3.7] Applies to portion of Code text: “Access to fire escapes shall be from corridors through doors at floor level …” |
| (2) | [F30-OS3.1] [F10-OS3.7] |
| 3.4.7.4. Protection of Fire Escapes |  |
| (1) | [F05,F06-OS1.5] |
| 3.4.7.5. Stairs |  |
| (1) | [F10-OS3.7] |
| (2) | [F10-OS3.7] |
| (3) | [F10-OS3.7] Applies to the reduction in width permitted under certain conditions. |
| (4) | [F10-OS3.7] [F30-OS3.1] |
| 3.4.7.6. Guards and Railings |  |
| (1) | [F10-OS3.7] [F30-OS3.1] |
| (2) | [F10-OS3.7] [F30-OS3.1] |
| (3) | [F10-OS3.7] [F30-OS3.1] |
| (4) | [F30-OS3.1] |
| (5) | [F30-OS3.1] |
| 3.5.2.1. Elevators, Escalators and Dumbwaiters |  |
| (1) | [F30,F81-OS3.1] [F32,F81-OS3.3] [F36,F81-OS3.6] |
| (2) | [F82-OS3.1,OS3.3,OS3.6] |
| (3) | [F73-OA1] |
| 3.5.3.1. Fire Separations for Elevator Hoistways |  |
| (1) | [F03-OS1.2] |
|  | [F03-OP1.2] |
| 3.5.3.2. Vertical Service Spaces for Dumbwaiters |  |
| (1) | [F03-OS1.2] |
|  | [F03-OP1.2] |
| 3.5.3.3. Fire Separations for Elevator Machine Rooms |  |
| (1) | [F03-OS1.2] |
|  | [F03-OP1.2] |
| (2) | [F03-OS1.2] |
|  | [F03-OP1.2] |
| 3.5.4.1. Elevator Car Dimensions |  |
| (1) | [F12-OS3.7] |
| (3) | [F12-OS3.7] |
| 3.5.4.2. Floor Numbering |  |
| (1) | [F73-OA1] |
| 3.6.1.2. Electrical Wiring and Equipment |  |
| (1) | [F01-OS1.1] [F02,F03-OS1.2] [F81-OS1.4] |
|  | [F01-OP1.1] [F02,F03-OP1.2] [F81-OP1.4] |
|  | [F32-OS3.3] |
| 3.6.1.3. Lightning Protection Systems |  |
| (1) | [F01,F81-OS1.1] |
|  | [F01,F81-OP1.1] |
| 3.6.1.4. Storage Use Prohibition |  |
| (1) | [F01-OS1.1] [F02-OS1.2] |
| 3.6.1.5. Appliances Installed outside a Building |  |
| (1) | [F03-OS1.2] |
|  | (b) [F03-OP1.2] |
|  | (a) [F03-OP3.1] |
| 3.6.2.1. Fire Separations around Service Rooms |  |
| (1) | [F03-OS1.2,OS1.4] |
|  | [F03-OP1.2,OP1.4] |
| (3) | [F01-OS1.1] [F03-OS1.2] |
|  | [F01-OP1.1] [F03-OP1.2] |
| (4) | [F03-OS1.2,OS1.4] |
|  | [F03-OP1.2,OP1.4] |
| (5) | [F03-OS1.2,OS1.4] |
|  | [F03-OP1.2,OP1.4] |
| (6) | [F03-OS1.2,OS1.4] |
|  | [F03-OP1.2,OP1.4] |
| (7) | [F03-OS1.2,OS1.4] |
|  | [F03-OP1.2,OP1.4] |
| 3.6.2.2. Service Rooms under Exits |  |
| (1) | [F06,F05-OS3.7] |
|  | [F02-OS1.2] |
| 3.6.2.4. Incinerator Rooms |  |
| (1) | [F02-OS1.2] |
| 3.6.2.5. Storage of Combustible Refuse and Recycling |  |
| (1) | [F03-OS1.2] |
|  | [F03-OP1.2] |
| 3.6.2.6. Door Swing for Service Rooms |  |
| (1) | [F10-OS1.5] Applies to portion of Code text: “A swing-type door from a service room containing a boiler or incinerator shall swing outward from the room …” |
|  | [F30-OS3.1] Applies to portion of Code text: “A swing-type door from a service room containing a boiler or incinerator shall swing … inward if the door opens onto a corridor or any room used for an assembly occupancy.” |
| 3.6.2.7. Electrical Equipment Vaults |  |
| (2) | [F03-OS1.2,OS1.4] |
|  | [F03-OP1.2,OP1.4] |
| (3) | [F02-OS1.2] [F11-OS1.5] [F03-OS1.4] |
|  | [F02-OP1.2] [F03-OP1.4] |
| (4) | [F03-OS1.2,OS1.4] |
|  | [F03-OP1.2,OP1.4] |
| (6) | [F81-OS1.1] |
| (7) | [F03-OS1.2] |
| (8) | [F44-OS1.1] [F03-OS1.2] |
| (9) | [F34-OS1.1] |
|  | [F34-OS3.3] |
|  | [F34-OP1.1] |
| 3.6.2.8. Emergency Power Installations |  |
| (1) | [F03-OS1.2,OS1.4] [F06-OS1.2,OS1.5] |
|  | [F03-OP1.2,OP1.4] [F06-OP1.2] |
| 3.6.3.1. Fire Separations for Vertical Service Spaces |  |
| (1) | [F03-OS1.2] |
|  | [F03-OP1.2] |
| (2) | [F03-OS1.2] |
|  | [F03-OP1.2] |
| (3) | [F03-OS1.2] |
|  | [F03-OP1.2] |
| (4) | [F03-OS1.2] |
|  | [F03-OP1.2] |
| (5) | [F03-OS1.2] |
|  | [F03-OP1.2] |
| 3.6.3.2. Foamed Plastic Protection |  |
| (1) | [F02-OS1.2] |
| 3.6.3.3. Linen and Refuse Chutes |  |
| (1) | (d),(e) [F02-OS1.2] |
|  | (a),(b),(c) [F41-OH2.4,OH2.5] |
| (2) | [F03-OS1.2] |
|  | [F03-OP1.2] |
| (3) | [F03-OS1.2] |
| (4) | (b) [F03-OS1.2] |
|  | (a) [F41-OH2.4,OH2.5] |
| (5) | (a) [F81,F03-OS1.2] |
|  | (a) [F81,F41-OH2.4,OH2.5] |
|  | (a) [F81,F03-OP1.2] |
|  | (b) [F03-OS1.2] |
|  | (b) [F03-OP1.2] |
|  | (c) [F01,F02-OS1.2] |
|  | (c) [F01,F02-OP1.2] |
|  | (d) [F05-OS1.5] [F06-OS1.5,OS1.2] |
|  | (d) [F06-OP1.2] |
| (6) | [F02-OS1.2] |
|  | [F02-OP1.2] |
| (7) | [F03-OS1.2] |
|  | [F03-OP1.2] |
| (8) | [F02-OS1.2] |
|  | [F41-OH2.4,OH2.5] |
| (9) | [F03-OS1.2] |
|  | [F03-OP1.2] |
| (10) | [F81,F03-OS1.2] Applies to portion of Code text: “The room or bin into which a refuse chute discharges shall be of sufficient size to contain the refuse between normal intervals of emptying …” |
|  | [F81,F41-OH2.4,OH2.5] Applies to portion of Code text: “The room or bin into which a refuse chute discharges shall be of sufficient size to contain the refuse between normal intervals of emptying …” |
|  | [F41-OH2.4,OH2.5] Applies to portion of Code text: “The room or bin into which a refuse chute discharges shall be … impervious to moisture and be equipped with a water connection and floor drain for washing-down purposes.” |
| (11) | [F01,F02-OS1.2] |
| 3.6.3.4. Exhaust Duct Negative Pressure |  |
| (1) | [F03-OS1.2] |
| 3.6.3.5. Grease Duct Enclosures |  |
| (1) | [F02,F03-OS1.2] |
|  | [F02,F03-OP1.2] |
| (2) | [F02,F03-OS1.2] |
|  | [F02,F03-OP1.2] |
| 3.6.4.2. Fire Separations for Horizontal Service Spaces |  |
| (2) | [F03-OS1.2] |
|  | [F03-OP1.2] |
| 3.6.4.3. Plenum Requirements |  |
| (1) | [F02-OS1.2] |
| (2) | [F03-OS1.2,OS1.3] |
|  | [F03-OP1.2,OP1.3] |
| 3.6.4.4. Attic or Roof Space Access |  |
| (1) | [F01,F02,F12-OS1.2] |
|  | [F01,F02,F12-OP1.2] |
| 3.6.4.5. Horizontal Service Space Access |  |
| (1) | [F01,F02,F12-OS1.2] |
|  | [F01,F02,F12-OP1.2] |
| 3.6.4.6. Crawl Space Access |  |
| (1) | [F01,F02,F12-OS1.2] |
|  | [F01,F02,F12-OP1.2] |
| 3.6.5.1. Duct Materials |  |
| (1) | [F01,F02-OS1.2] |
| (2) | [F02-OS1.2] |
| (4) | [F02-OS1.2] |
| (5) | [F02-OS1.2] |
| 3.6.5.2. Vibration Isolation Connectors |  |
| (1) | [F01,F02-OS1.2] |
| (2) | [F02-OS1.2] |
| 3.6.5.3. Tape |  |
| (1) | [F02-OS1.2] |
| 3.6.5.4. Coverings, Linings, Adhesives and Insulation |  |
| (1) | [F02-OS1.2] |
| (2) | [F02-OS1.2] |
| (3) | [F02-OS1.2] |
| (4) | [F02-OS1.2] |
| (5) | [F02-OS1.2] |
| (6) | [F02-OS1.2] |
| (7) | [F01,F02-OS1.2] |
| 3.6.5.5. Insulation and Coverings |  |
| (1) | [F01,F02-OS1.2] |
| (2) | [F02-OS1.2] |
| (3) | [F02-OS1.2] |
| (4) | [F02-OS1.2] |
| 3.6.5.6. Clearance of Ducts and Plenums |  |
| (2) | [F01-OS1.2] |
| (3) | [F01-OS1.2] |
| (4) | [F01-OS1.2] |
| (5) | [F01-OS1.2] |
| 3.6.5.7. Supply, Return, Intake and Exhaust-Air Openings |  |
| (1) | [F02-OS1.2] |
| 3.6.5.8. Return-Air System |  |
| (1) | [F02-OS1.2] |
| (2) | [F01,F02-OS1.2] |
| (3) | [F01,F02-OS1.2] |
| (4) | [F01,F02-OS1.2] |
| 3.7.1.1. Room and Space Height |  |
| (1) | [F30-OS3.1] |
| 3.7.2.1. Plumbing and Drainage Systems |  |
| (3) | [F72-OH2.1] |
| (4) | [F72-OH2.1] |
| 3.7.2.2. Water Closets |  |
| (1) | [F72-OH2.1] Applies to portion of Code text: “... water closets shall be provided ...” |
| (4) | [F72-OH2.1] |
| (5) | [F72-OH2.1] |
| (6) | [F72-OH2.1] |
| (7) | [F72-OH2.1] |
| (8) | [F72-OH2.1] |
| (9) | [F72-OH2.1] |
| (10) | [F72-OH2.1] |
| (11) | [F72-OH2.1] |
| (12) | [F72-OH2.1] |
| (13) | [F72-OH2.1] |
| (14) | [F72-OH2.1] |
| 3.7.2.3. Lavatories |  |
| (1) | [F71-OH2.3] |
| (3) | [F30-OS3.1] |
| (4) | [F71-OH2.3] |
| 3.7.2.4. Safety Glazing |  |
| (1) | [F20-OS3.1] |
| 3.7.2.5. Surface Protection |  |
| (1) | [F72-OH2.1] [F40-OH2.4] |
| (2) | [F72-OH2.1] [F40-OH2.4] |
| 3.7.2.6. Floor Drain |  |
| (1) | [F40-OH2.4] |
|  | [F30-OS3.1] |
| 3.7.2.7. Grab Bars |  |
| (1) | [F20-OS3.1] |
| 3.7.2.8. Bathtubs |  |
| (1) | [F74-OA2] |
|  | (b) [F31-OS3.2] |
|  | (d) [F30-OS3.1] |
| 3.7.3.1. Medical Gas Piping |  |
| (1) | [F43,F81,F82-OS3.4] |
|  | (b) [F01,F02-OS1.1] |
|  | (b) [F01,F02-OP1.1] |
| 3.8.2.2. Entrances |  |
| (1) | [F73-OA1] |
| (4) | [F73-OA1] |
| 3.8.2.3. Areas Requiring a Barrier-Free Path of Travel |  |
| (1) | [F73-OA1] |
| (3) | [F74-OA2] |
| (4) | [F74-OA2] |
| (5) | [F74-OA2] |
|  | [F10-OS3.7] Applies to portion of Code text: “... each row of seats served by two aisles shall have one adaptable seat conforming to Subsection 3.8.3. located adjacent to one of the aisles.” |
| (6) | [F74-OA2] |
| 3.8.2.4. Access to Storeys Served by Escalators and Moving Walks |  |
| (1) | [F73-OA1] |
| (2) | [F73-OA1] |
| 3.8.2.5. Exterior Barrier-Free Paths of Travel to Building Entrances and Exterior Passenger-Loading Zones |  |
| (1) | [F73-OA1] |
| (2) | [F73-OA1] |
| 3.8.2.7. Power Door Operators |  |
| (1) | [F73-OA1] |
| 3.8.2.8. Plumbing Facilities |  |
| (1) | [F74-OA2] |
|  | [F72-OH2.1] [F71-OH2.3] |
| (2) | [F74-OA2] |
|  | [F72-OH2.1] [F71-OH2.3] |
| (4) | [F72-OH2.1] |
|  | [F73-OA1] |
| (13) | [F74-OA2] |
| (15) | [F74-OA2] |
| 3.8.2.9. Assistive Listening Systems |  |
| (2) | [F74-OA2] |
| 3.8.2.10. Signs and Indicators |  |
| (1) | [F74-OA2] |
| (2) | [F74-OA2] |
| (3) | [F74-OA2] |
| (4) | [F74-OA2] |
| 3.8.2.11. Counters |  |
| (1) | [F74-OA2] |
| 3.8.2.12. Telephones |  |
| (1) | [F74-OA2] |
| 3.8.3.2. Barrier-Free Path of Travel |  |
| (1) | [F73-OA1] |
| (3) | (a),(b) [F30-OS3.1] |
|  | (a),(b) [F73-OA1] |
|  | (c),(d) [F73-OA1] |
|  | (e),(f) [F73-OA1] |
|  | (e),(f) [F30-OS3.1] |
|  | (c),(d) [F30-OS3.1] |
| (5) | [F73-OA1] |
| (6) | [F73-OA1] |
| 3.8.3.3. Exterior Walks |  |
| (1) | (a) [F73-OA1] |
|  | (a) [F30-OS3.1] |
|  | (b) [F73-OA1] |
|  | (d) [F30-OS3.1] |
| 3.8.3.4. Exterior Passenger-Loading Zones |  |
| (1) | (a) [F74-OA2] |
|  | (b) [F73-OA1] |
|  | (c) [F74-OA2] |
| 3.8.3.5. Ramps |  |
| (1) | (b),(e) [F73-OA1] |
|  | (d) [F30-OS3.1] |
|  | (c) [F73-OA1] |
|  | (d) [F73-OA1] |
|  | (b),(e) [F30-OS3.1] |
|  | (c) [F30-OS3.1] |
| (4) | (a) [F73-OA1] |
|  | (b),(c) [F30-OS3.1] |
| (5) | [F30-OS3.1] |
| 3.8.3.6. Doorways and Doors |  |
| (2) | [F73-OA1] |
| (3) | [F74-OA2] |
|  | [F30-OS3.1] |
| (4) | [F74-OA2] |
|  | [F10-OS3.7] |
| (5) | [F74-OA2] |
|  | [F10-OS3.7] |
| (6) | [F73-OA1] |
| (7) | [F30-OS3.1] |
| (8) | [F73-OA1] |
| (10) | [F30-OS3.1] |
|  | [F73-OA1] |
| (11) | [F73-OA1] |
| (12) | [F30-OS3.1] |
|  | [F73-OA1] |
| (14) | [F73-OA1] |
| (15) | [F73-OA1] |
| (17) | [F74-OA2] |
|  | [F10-OS3.7] |
| 3.8.3.7. Passenger-Elevating Devices |  |
| (1) | [F73-OA1] |
|  | [F74-OA2] |
|  | [F30-OS3.1] [F10-OS3.7] |
| 3.8.3.8. Controls |  |
| (1) | [F74-OA2] |
|  | [F10-OS3.7] |
| 3.8.3.9. Accessible Signs |  |
| (1) | [F74-OA2] |
|  | [F73-OA1] |
| (2) | [F74-OA2] |
|  | [F73-OA1] |
| (3) | [F74-OA2] |
|  | [F73-OA1] |
| 3.8.3.10. Drinking Fountains |  |
| (1) | [F74-OA2] |
| (2) | [F74-OA2] |
| 3.8.3.11. Water-Bottle Filling Stations |  |
| (1) | [F74-OA2] |
| (2) | [F74-OA2] |
| 3.8.3.12. Accessible Water-Closet Stalls |  |
| (1) | [F74-OA2] |
|  | [F72-OH2.1] |
|  | (d)(i) [F74-OA2] |
|  | (f),(g) [F30,F20-OS3.1] |
|  | (h) [F30-OS3.1] Applies to portion of Code text: “… be equipped with a coat hook … projecting not more than 50 mm from the wall …” |
| 3.8.3.13. Universal Washrooms |  |
| (1) | [F74-OA2] |
|  | (b) [F10-OS3.7] |
|  | (g) [F30-OS3.1] Applies to the requirement for a coat hook. |
|  | (i) [F74-OA2] Applies to the requirement for a shelf. |
|  | [F72-OH2.1] [F71-OH2.3] |
|  | (b) [F74-OA2] Applies to portion of Code text: “… a door ... capable of being locked from the inside …” |
| (2) | [F72-OH2.1] [F71-OH2.3] |
| 3.8.3.14. Water Closets |  |
| (1) | [F74-OA2] |
|  | [F72-OH2.1] |
| 3.8.3.15. Water-Closet Stalls and Urinals for Persons with Limited Mobility |  |
| (1) | [F74-OA2] |
|  | (d) [F30-OS3.1] |
| (2) | [F74-OA2] |
|  | (f) [F30-OS3.1] |
| 3.8.3.16. Lavatories and Mirrors |  |
| (1) | [F74-OA2] |
|  | [F71-OH2.3] |
|  | (f) [F31-OS3.2] |
| (2) | [F74-OA2] |
| 3.8.3.17. Showers |  |
| (1) | [F74-OA2] |
|  | (d),(e) [F30-OS3.1] |
|  | (f) [F30-OS3.1] |
|  | (h) [F31-OS3.2] |
| (2) | [F74-OA2] |
|  | [F71-OH2.3] |
|  | (a) [F73-OA1] |
|  | (b) [F10-OS3.7] |
|  | (b) [F74-OA2] |
|  | (g) [F74-OA2] |
| 3.8.3.18. Accessible Bathtubs |  |
| (1) | [F74-OA2] |
| 3.8.3.19. Assistive Listening Systems |  |
| (1) | [F74-OA2] |
|  | [F11-OS3.7] |
| (2) | [F74-OA2] |
| 3.8.3.20. Counters |  |
| (1) | [F74-OA2] |
| 3.8.3.21. Telephones |  |
| (1) | [F74-OA2] |
| (2) | [F74-OA2] |
| 3.8.3.22. Spaces in Seating Area |  |
| (1) | [F74-OA2] |
|  | [F30-OS3.1] Applies to portion of Code text: “… level ... level and have removable seats, …” |
|  | (d) [F10-OS3.7] Applies to portion of Code text: “… without infringing on egress from any row of seating or any aisle requirements …” |
| (2) | [F74-OA2] |
|  | [F30-OS3.1] Applies to portion of Code text: “… level, ...” |
| (3) | (a) [F10-OS3.7] Applies to portion of Code text: “… without infringing on egress from any row of seating or any aisle requirements …” |
|  | [F74-OA2] |
| (4) | [F10-OS3.7] |
| 3.9.1.2. Application |  |
| (1) | (d) [F02-OS1.1] |
| 3.9.2.2. Spatial Separation |  |
| (2) | [F12-OP3.1] |
| (3) | [F56-OH3.1] |
| 3.9.3.1. Safety Requirements Within Floor Areas |  |
| (2) | [F02-OS1.2] |
| (3) | [F03-OS1.2] |
|  | [F03-OP1.2] |
| (6) | [F02-OP1.2] |
| 3.9.3.2. Sanitary Facilities |  |
| (1) | [F72-OH2.1] |
|  | [F71-OH2.3] |

Notes to Table 3.10.1.1.:

(1) See Parts 2 and 3 of Division A.

Notes to Part 3

Fire Protection, Occupant Safety and Accessibility

A-3   Application of Part 3. In applying the requirements of this Part, it is intended that they be applied with discretion to buildings of unusual configuration that do not clearly conform to the specific requirements, or to buildings in which processes are carried out which make compliance with particular requirements in this Part impracticable. The definition of “building” as it applies to this Code is general and encompasses most structures, including those which would not normally be considered as buildings in the layman's sense. This occurs more often in industrial uses, particularly those involving manufacturing facilities and equipment that require specialized design that may make it impracticable to follow the specific requirements of this Part. Steel mills, aluminum plants, refining, power generation and liquid storage facilities are examples. A water tank or an oil refinery, for example, has no floor area, so it is obvious that requirements for exits from floor areas would not apply. Requirements for structural fire protection in large steel mills and pulp and paper mills, particularly in certain portions, may not be practicable to achieve in terms of the construction normally used and the operations for which the space is to be used. In other portions of the same building, however, it may be quite reasonable to require that the provisions of this Part be applied (e.g., the office portions). Similarly, areas of industrial occupancy which may be occupied only periodically by service staff, such as equipment penthouses, normally would not need to have the same type of exit facility as floor areas occupied on a continuing basis. It is expected that judgment will be exercised in evaluating the application of a requirement in those cases when extenuating circumstances require special consideration, provided the occupants' safety is not endangered.

The provisions in this Part for fire protection features installed in buildings are intended to provide a minimum acceptable level of public safety. It is intended that all fire protection features of a building, whether required or not, will be designed in conformance with good fire protection engineering practice and will meet the appropriate installation requirements in relevant standards. Good design is necessary to ensure that the level of public safety established by the Code requirements will not be reduced by a voluntary installation.

Firefighting Assumptions

The requirements of this Part are based on the assumption that firefighting capabilities are available in the event of a fire emergency. These firefighting capabilities may take the form of a paid or volunteer public fire department or in some cases a private fire brigade. If these firefighting capabilities are not available, additional fire safety measures may be required.

Firefighting capability can vary from municipality to municipality. Generally, larger municipalities have greater firefighting capability than smaller ones. Similarly, older, well established municipalities may have better firefighting facilities than newly formed or rapidly growing ones. The level of municipal fire protection considered to be adequate will normally depend on both the size of the municipality (i.e., the number of buildings to be protected) and the size of buildings within that municipality. Since larger buildings tend to be located in larger municipalities, they are generally, but not always, favoured with a higher level of municipal protection.

Although it is reasonable to consider that some level of municipal firefighting capability was assumed in developing the fire safety provisions in Part 3, this was not done on a consistent or defined basis. The requirements in the Code, while developed in the light of commonly prevailing municipal fire protection levels, do not attempt to relate the size of building to the level of municipal protection. The responsibility for controlling the maximum size of building to be permitted in a municipality in relation to local firefighting capability rests with the municipality. If a proposed building is too large, either in terms of floor area or building height, to receive reasonable protection from the municipal fire department, fire protection requirements in addition to those prescribed in this Code, may be necessary to compensate for this deficiency. Automatic sprinkler protection may be one option to be considered.

Alternatively, the municipality may, in light of its firefighting capability, elect to introduce zoning restrictions to ensure that the maximum building size is related to available municipal fire protection facilities. This is, by necessity, a somewhat arbitrary decision and should be made in consultation with the local firefighting service, who should have an appreciation of their capability to fight fires.

The requirements of Subsection 3.2.3. are intended to prevent fire spread from thermal radiation assuming there is adequate firefighting available. It has been found that periods of from 10 to 30 minutes usually elapse between the outbreak of fire in a building that is not protected with an automatic sprinkler system and the attainment of high radiation levels. During this period, the specified spatial separations should prove adequate to inhibit ignition of an exposed building face or the interior of an adjacent building by radiation. Subsequently, however, reduction of the fire intensity by firefighting and the protective wetting of the exposed building face will often be necessary as supplementary measures to inhibit fire spread.

In the case of a building that is sprinklered throughout, the automatic sprinkler system should control the fire to an extent that radiation to neighbouring buildings should be minimal. Although there will be some radiation effect on a sprinklered building from a fire in a neighbouring building, the internal sprinkler system should control any fires that might be ignited in the building and thereby minimize the possibility of the fire spreading into the exposed building. NFPA 80A, “Recommended Practice for Protection of Buildings from Exterior Fire Exposures,” provides additional information on the possibility of fire spread at building exteriors.

The water supply requirements for fire protection installations depend on the requirements of any automatic sprinkler installations and also on the number of fire streams that may be needed at any fire, having regard to the length of time the streams will have to be used. Both these factors are largely influenced by the conditions at the building to be equipped, and the quantity and pressure of water needed for the protection of both the interior and exterior of the building must be ascertained before the water supply is decided upon. Acceptable water supplies may be a public waterworks system that has adequate pressure and discharge capacity, automatic fire pumps, pressure tanks, manually controlled fire pumps in combination with pressure tanks, gravity tanks, and manually controlled fire pumps operated by remote control devices at each hose station.

A-3.1.2.   Use Classification. The purpose of classification is to determine which requirements apply. This Code requires classification in accordance with every major occupancy for which the building is used or intended to be used. Where necessary, an application clause has been inserted in this Part to explain how to choose between the alternative requirements which multiple occupancy classification may present.

A-3.1.2.1.(1)   Major Occupancy Classification. The following are examples of the major occupancy classifications described in Table 3.1.2.1.:

Group A, Division 1

Motion picture theatres

Opera houses

Television studios admitting a viewing audience

Theatres, including experimental theatres

Group A, Division 2

Art galleries

Auditoria

Bowling alleys

Churches and similar places of worship

Clubs, nonresidential

Community halls

Courtrooms

Dance halls

Daycare Facilities for Children

Exhibition halls (other than classified in Group E)

Gymnasia

Lecture halls

Libraries

Licensed beverage establishments

Museums

Passenger stations and depots

Recreational piers

Restaurants

Schools and colleges, nonresidential

Undertaking premises

Group A, Division 3

Arenas

Indoor swimming pools, with or without spectator seating

Rinks

Group A, Division 4

Amusement park structures (not elsewhere classified)

Bleachers

Grandstands

Reviewing stands

Stadia

Group B, Division 1

Jails

Penitentiaries

Police stations with detention quarters

Prisons

Psychiatric hospitals with detention quarters

Reformatories with detention quarters

Group B, Division 2

Care facilities with treatment

Convalescent /recovery/rehabilitation centres with treatment

Hospices with treatment

Hospitals

Infirmaries

Nursing homes with treatment

Psychiatric hospitals without detention quarters

Respite centres with treatment

Group B, Division 3

Assisted/supportive living facilities

Care facilities without treatment

Children's custodial homes

Convalescent/recovery/rehabilitation centres without treatment

Group homes

Hospices without treatment

Nursing homes without treatment

Reformatories without detention quarters

Respite centres without treatment

Group C

Apartments

Boarding houses

Clubs, residential

Colleges, residential

Convents

Dormitories

Hotels

Houses

Lodging houses

Monasteries

Motels

Schools, residential

Group D

Banks

Barber and hairdressing shops

Beauty parlours

Dental offices

Dry cleaning establishments, self-service, not using flammable or explosive solvents or cleaners

Laundries, self-service

Medical offices

Offices

Police stations without detention quarters

Radio stations

Small tool and appliance rental and service establishments

Group E

Department stores

Exhibition halls

Markets

Shops

Stores

Supermarkets

Group F, Division 1

Bulk plants for flammable liquids

Bulk storage warehouses for hazardous substances

Cereal mills

Chemical manufacturing or processing plants

Distilleries

Dry cleaning plants

Feed mills

Flour mills

Grain elevators

Lacquer factories

Mattress factories

Paint, varnish and pyroxylin product factories

Rubber processing plants

Spray painting operations

Waste paper processing plants

Group F, Division 2

Aircraft hangars

Box factories

Candy plants

Cold storage plants

Dry cleaning establishments not using flammable or explosive solvents or cleaners

Electrical substations

Factories

Freight depots

Helicopter landing areas on roofs

Laboratories

Laundries, except self-service

Mattress factories

Planing mills

Printing plants

Repair garages

Salesrooms

Service stations

Storage rooms

Television studios not admitting a viewing audience

Warehouses

Wholesale rooms

Woodworking factories

Workshops

Group F, Division 3

Creameries

Factories

Laboratories

Light-aircraft hangars (storage only)

Power plants

Salesrooms

Sample display rooms

Storage garages, including open air parking garages

Storage rooms

Warehouses

Workshops

A-3.1.2.3.(1)   Arena Regulation. The use of an arena is regulated in the British Columbia Fire Code.

A-3.1.2.7. Group A, Division 2, Low Occupant Load. A suite of Group A, Division 2 assembly is permitted to be classified as a Group D business and personal services occupancy provided the requirements of Article 3.1.2.6. are complied with. This re-classification will permit the suite to be located in a building to which Part 9 of the Code is applicable, or when the suite is located in a building where the adjoining occupancy is a Group F, Division 1 high hazard occupancy.

A-3.1.2.8. Daycare Facilities for Children. A daycare facility for children is typically occupied for a period of less than 24 hours each day (i.e., is not a residential facility). The term “daycare” is not meant to exclude facilities that provide short term care during the night for a period of less than 24 hours each day. (See also A-3.3.2.18.)

A-3.1.4.1.(1)   Combustible Construction and Materials Permitted. The permission to use combustible construction or combustible materials stated in Articles 3.1.4.1., 3.1.5.5., 3.1.5.14. and 3.1.5.15. does not waive the requirements regarding construction type and cladding stated in Article 3.2.3.7.

A-3.1.4.2.   Protection of Penetrations. Where foamed plastics are required to be protected from adjacent spaces within a building, the protection should be continuous so as to cover the foamed plastics so they are not exposed to the interior of the building. However, minor penetrations of the protective covering by small electrical and mechanical components, such as electrical outlets and fixtures, sprinkler piping, and mechanical vents, are acceptable because the penetrant and associated fittings and seals will prevent the small amount of foamed plastic surrounding the penetration from being exposed to the interior of the building.

Foamed plastics that are penetrated by larger components or assemblies, such as windows, are unlikely to be exposed to the interior of the building as they are protected by associated framing and finishes and/or the installation of a closure.

Small amounts of foamed plastics, such as air sealants used between major components of exterior wall construction, are not required to be protected (see Sentence 3.1.5.2.(1)).

Penetrations of a fire separation or of a membrane forming part of an assembly required to have a fire-resistance rating are nevertheless required to be provided with a firestop in accordance with Subsection 3.1.9.

A-3.1.4.2.(1)   Concealed Space. The term “concealed space” includes any space that is not visibly apparent and that is provided with an opening to allow access for repair and periodic inspections.

A-3.1.4.2.(1)(c)   Thermal Barrier in Combustible Construction. Any thermal barrier that is accepted under the requirements of Sentence 3.1.5.15.(2) for noncombustible construction is also acceptable for combustible construction.

A-3.1.4.2.(2) and 3.1.5.7.(3)   Walk-in Coolers and Freezers. Sentences 3.1.4.2.(2) and 3.1.5.7.(3) are intended to apply to walk-in coolers and freezers that are constructed as stand-alone structures within a building.

A-3.1.4.3.(1)(b)(i)   Raceway Definition. The term raceway is defined in CSA C22.1, “Canadian Electrical Code, Part I,” and includes both rigid and flexible conduit.

A-3.1.4.3.(1)   Wire and Cable Equivalence. Electrical wires and cables that conform to the requirements of Sentence 3.1.5.21.(1) are deemed to satisfy the requirements of Sentence 3.1.4.3.(1).

A-3.1.4.8.(1)   Exterior Cladding.  The requirements in Sentence 3.1.4.8.(1) are intended to limit the potential for fire spread on the exterior cladding of buildings of combustible construction through the use of noncombustible finishes on the exterior of the wall assembly or the use of a cladding/wall assembly that has been assessed with regard to its ability to resist flame propagation up the outside of a building. These cladding and wall assembly combinations can be used as infill or panel-type walls between structural elements, or attached directly to a loadbearing structural system. Note that these requirements apply independently of the provisions contained in Subsection 3.2.3. regarding spatial separation and exposure protection.

A-3.1.5.4.(1)   Skylight Spacing. The minimum spacing dimensions for skylight assemblies are based on the distance that flame must travel along a flat ceiling surface. If ceilings have projecting beams or other features that would increase the distance the flame would have to travel along the surface, the distances specified may be measured accordingly.

A-3.1.5.5.(1)(b)   Combustible Cladding on Exterior Walls. The performance of the wall assembly is assessed with regard to its ability to resist flame propagation up the outside of a building.

A-3.1.5.5.(1)(b)(i)   Flame-Spread Distance. The maximum flame-spread distance referred to in Subclause 3.1.5.5.(1)(b)(i) means the distance between the top of the opening and the highest observable instance of flaming along the wall assembly; thus, intermittent flaming to a height of 5 m above the opening is acceptable.

A-3.1.5.5.(1)(b)(ii)   Heat Flux Measurement. The heat flux to the assembly referred to in Subclause 3.1.5.5.(1)(b)(ii) is the maximum one-minute averaged heat flux measured by transducers located 3.5 m above the top of the opening. The intent of this criterion is to limit the spread of fire on the wall assembly to a height of 3.5 m above the opening.

Fire tests have shown that flame does not spread on the exterior surface of a wall assembly where the heat flux is less than 35 kW/m2 above the opening.

A-3.1.5.14.(5)(d)   Foamed Plastic Insulation Protection. The standard fire exposure temperature in CAN/ULC-S101, “Standard Method of Fire Endurance Tests of Building Construction and Materials,” is the same as in CAN/ULC-S124, “Standard Method of Test for the Evaluation of Protective Coverings for Foamed Plastic.” A thermal barrier that, when tested in conformance with CAN/ULC-S101, does not exceed an average temperature rise of 140°C on its unexposed face after a period of 10 min satisfies this requirement.

A-3.1.5.21.(1)   Wire and Cable Flammability. In regulating the flammability characteristics of electrical wires and cables installed in a building, it is intended that the requirements of this Sentence and of other similar Sentences in the Code apply to wires and cables that are essentially a part of the distribution systems for power or communications. These distribution systems will normally include branch circuits that terminate at an outlet box in the space to be served and at that location cable terminators or plugs for individual items of equipment will be plugged in.

A-3.1.6.   Encapsulated Mass Timber Construction and Materials Permitted. The permission to use encapsulated mass timber construction and other combustible materials stated in Articles 3.1.6.2., 3.1.6.3., 3.1.6.9. and 3.1.6.10. does not waive the requirements regarding types of construction and cladding stated in Article 3.2.3.7.

A-3.1.6.3.   Structural Mass Timber Elements. Structural timber elements may consist of any number of large cross-section timber products, such as solid-sawn timber, glued-laminated timber (glulam), structural composite lumber (SCL), cross-laminated timber (CLT), and nail-laminated timber (NLT).

The minimum dimensions required for structural timber elements in encapsulated mass timber construction were established so that such elements will exhibit the fire performance characteristics of mass timber rather than those of lightweight, small-dimensioned wood elements (e.g., lumber), including reduced-ignition propensity and reduced average rate of fuel contribution. Note that the dimensions stated in Table 3.1.6.3. do not reflect a specific fire-resistance rating; larger dimensions may be required to satisfy fire-resistance rating requirements.

The reference to Article 3.2.2.16. means that heavy timber construction is permitted to be used for the roof assembly (and its supports) in buildings of encapsulated mass timber construction that are sprinklered and not more than 2 storeys in building height. It follows that the minimum dimensions stated in Table 3.1.4.7. would apply to those elements rather than the ones stated in Table 3.1.6.3. Furthermore, the roof elements and supports made of heavy timber construction do not need to conform to the encapsulation requirements of Article 3.1.6.4., nor are they limited by the flame-spread rating or maximum thickness or cut-through requirements of Article 3.1.6.14.

A-3.1.6.4.(1)   Encapsulation of Mass Timber Elements. The general intent of Sentence 3.1.6.4.(1) is that all exposed surfaces of the mass timber elements be encapsulated, including the upper surface of a mass timber floor assembly. However, the exposed surfaces in certain concealed spaces formed by or contained within mass timber elements are exempted from complying with this Sentence (see Sentences 3.1.6.3.(4),  3.1.6.16.(2) and 3.1.6.17.(2), and Articles 3.1.6.7. and 3.1.6.12.). Moreover, the upper surface of a mass timber roof assembly need not be encapsulated where there is no concealed space above it. As well, the exterior side of a mass timber exterior wall assembly need not be encapsulated; however, the provisions of Article 3.1.6.9. and Subsection 3.2.3. for exterior walls still need to be considered.

A-3.1.6.4.(3) to (6)   Fire-Resistance Rating of Mass Timber with Exposed Surfaces. Portions of mass timber elements required to have a fire-resistance rating are permitted to be exposed in accordance with the permissions stated in Sentences 3.1.6.4.(3) to (6); however, it is important to note that applying those permissions does not waive the requirement for these elements to have a fire-resistance rating.

A-3.1.6.4.(4)   Exposed Surfaces of Mass Timber Walls. The primary objective of encapsulating mass timber elements is to limit the probability that these elements will significantly contribute to fire spread and fire duration in the event of a fire. Since thick wood members require a source of imposed heat flux to burn, the stipulation in Clause 3.1.6.4.(4)(a) that the exposed surfaces of mass timber walls face the same direction within a suite is intended to reduce the potential of re-radiation between burning mass timber surfaces that face each other, which could sustain flaming combustion into the decay phase of a fire if the sprinkler system failed to operate or to control the fire. Additionally, the maximum percentage of exposed surface area stated in Article 3.1.6.4. is low so that it is not sufficient to sustain a ventilation-controlled fire that might provide the radiation required to sustain flaming combustion into the decay phase of a fire if the sprinkler system failed to operate or to control the fire.

A-3.1.6.6.   Encapsulation Materials. Research has been conducted on different types of encapsulation materials, such as gypsum board, gypsum concrete and cement board. The results of tests using an intermediate-scale furnace and of cone calorimeter tests indicate that a combustible timber element protected with a 38 mm thick layer of gypsum-concrete topping or with two layers of 12.7 mm Type X gypsum board will not ignite or contribute significant heat to a fire until average temperatures of 325–380°C are attained at the interface between the encapsulation material or assembly of materials and the combustible substrate. These temperatures are consistent with the ignition temperatures of wood-based materials.

A-3.1.6.6.(2)   Protection of Gypsum Board from Foot Traffic. Where gypsum board is used as the encapsulation material on the top of a mass timber floor assembly, it should be protected from physical impact arising from normal pedestrian traffic that could damage it and possibly compromise its encapsulation rating.

A-3.1.6.9.(1) and (2)   Exterior Cladding. The requirements in Sentences 3.1.6.9.(1) and (2) are intended to reduce the potential for fire spread on the exterior cladding of buildings of encapsulated mass timber construction through the use of noncombustible finishes on the exterior of the wall assembly or the use of a cladding/wall assembly that has been proven to resist flame propagation. These cladding/wall assembly combinations can be used as infill or panel-type walls between structural elements, or attached directly to a loadbearing structural system. Note that the requirements in Article 3.1.6.9. do not supersede the provisions in Subsection 3.2.3. regarding spatial separation and exposure protection.

A-3.1.8.1.(1)(b)   Barrier to Control Smoke Spread. Although a fire separation is not always required to have a fire-resistance rating, the fire separation should act as a barrier to the spread of smoke and fire until some response is initiated.

When choosing products for firestopping, the physical characteristics of the material used at the joints as well as the nature of the assembly and its potential movement should be taken into consideration.

If the fire-resistance rating of a fire separation is waived on the basis of the presence of an automatic sprinkler system, it is intended that the fire separation will be constructed so that it will remain in place and act as a barrier against the spread of smoke for a period of time until the sprinklers have actuated and controlled the fire.

A-3.1.8.1.(2)   Installation of Closures.  Although there is no explicit performance statement in the British Columbia Building Code that means of egress should be free of smoke, it is the intent that during the period when occupants are using a means of egress to evacuate from a floor area, the smoke contamination should not reach levels that would inhibit movement to the exit. This is particularly critical for persons with disabilities, who may not move at the same rate as other persons and who could be more susceptible to the effects of smoke contamination. NFPA 80, “Standard for Fire Doors and Other Opening Protectives,” requires that a fire door protecting a means of egress be designed to minimize the possibility of smoke passing through the opening.

Although self-closing devices are not required for all doors in a fire separation (see Article 3.1.8.13.), it is assumed that in a fire situation every door in a fire separation is closed. Article 3.3.3.5. prohibits grilles and similar openings for certain doors in hospitals and nursing homes with treatment.

Although fire dampers that release on the fusion of a fusible link will help to control the spread of fire, a substantial quantity of smoke could have passed through the opening before that event. They are frequently located below the upper levels of a room and so the release of the fusible link of the fire damper that protects an opening will be delayed until the temperature at the level of the opening becomes high enough to fuse the link.

Similar concern has to be considered for other closure devices that are permitted to remain open on fusible links, and their location should be restricted in accordance with NFPA 80 and the British Columbia Building Code, except where their installation in another location will not allow the products of combustion to spread into means of egress.

A-3.1.8.3.(2)   Fire Separation Continuity. The continuity of a fire separation with a fire-resistance rating is maintained by installing a firestop system at the juncture where it abuts against another fire separation, a floor, a ceiling or a roof assembly. The continuity of a fire separation without a fire-resistance rating that abuts another fire separation is maintained by filling all openings at the juncture of the assemblies with a fire-resistance-rated joint firestop system that will ensure the integrity of the fire separation at that location.

Test methods for the evaluation of joint systems are described in CAN/ULC-S115, “Standard Method of Fire Tests of Firestop Systems,” which covers joint systems between adjacent fire-resistance-rated assemblies and between a fire-resistance-rated floor and a non-fire-resistance-rated exterior wall. ASTM E2307, “Standard Test Method for Determining Fire Resistance of Perimeter Fire Barriers Using Intermediate-Scale, Multi-storey Test Apparatus,” is a test method applicable to joint systems between a fire-resistance-rated floor and a non-fire-resistance-rated exterior wall.

Fire-resistance-rated joint firestop systems can be tested and listed as either static or dynamic. Dynamic joint firestop systems are subjected to movement cycling prior to undergoing fire testing at maximum joint extension. This approach ensures that the fire-resistance rating of the joint firestop system will be maintained even after the joint has cycled through its anticipated range of movement over the service life of the building. Most joints between fire-resistance-rated assemblies, other than those between loadbearing elements, experience some movement over the service life of the building.

A-3.1.8.3.(5)   Joints. Firestops need not be installed between joints of interior finish materials that are arranged so as to create a smoke-tight joint.

A-3.1.8.10.(1)   Combination Smoke/Fire Dampers. A combination smoke/fire damper may be used in lieu of a fire damper to meet the requirement of Sentence 3.1.8.10.(1).

A-3.1.8.10.(5)   Damper Access. It is intended that an access door be provided in the duct and, if the duct is enclosed with an architectural finish, that a second access door be provided through that finish.

A-3.1.8.18.(1)   Wired Glass and Glass Block. The permission to include wired glass and glass block in doors and fire separations between an exit and the adjacent floor area does not permit the inclusion of those items in fire separations between exits and other parts of the building that are not included in the floor area. Examples include other exit facilities and vertical service spaces, including those used for building services and elevator hoistways.

A-3.1.8.19.(1)   Fire-Protection Rating for Doors. The provisions in Articles 3.1.8.17., 3.1.8.18. and 3.1.8.19. do not waive a requirement for a door to have a fire-protection rating. To achieve this rating in a door test, it may be necessary to limit the area of glass in the door. If this area is less than the area limits of Article 3.1.8.18., it is the governing criterion. Conversely, if the area limits of Article 3.1.8.18. are less than the area required to achieve a fire-protection rating, then the area limits of this Article govern.

A-3.1.9.   Penetrations. In the application of Subsection 3.1.9., a building service or structural element is considered to penetrate an assembly if it passes into or through the assembly. In some situations a service item enters an assembly through a membrane at one location, runs within the assembly, and then leaves the assembly through a membrane at another location.

The term “membrane penetration” usually designates an opening made through one side (wall, floor or ceiling membrane) of an assembly, whereas the term “through-penetration” designates an opening that passes through an entire assembly. Firestopping of membrane penetrations and through-penetrations involves installing an assemblage of specific materials or products that are designed, tested and fire-resistance-rated to resist for a prescribed period of time the spread of fire through the penetrations.

Products for firestopping within a barrier are required to address movement of the assembly and to control smoke spread; as such, the flexibility of the material used at the flexible joints as well as the nature of the assembly and its potential movement must be taken into consideration.

A-3.1.9.1.(1)(b)   Penetration. The intention behind the use of the term “cast in place” is to reinforce that there are to be no gaps between the building service or penetrating item and the membrane or assembly it penetrates. The term ”cast in place” describes a typical means of firestopping for a service penetration through a concrete slab or wall.

A-3.1.9.2.(1)   Service Equipment Penetrations. The provisions dealing with outlet boxes assume size, quantities and concentrations of partial depth penetrations that would not significantly affect the fire resistance of the assembly, including the temperature rise on the unexposed side of a wall. Sentence 3.1.9.2.(1) is not intended to allow large electrical distribution and control boxes to be recessed into an assembly required to have a fire-resistance rating unless they are firestopped as described in Sentence 3.1.9.3.(1).

The installation of fire dampers, smoke dampers or combination smoke/fire dampers is intended to comply with Subsection 3.1.8. and Sentence 3.1.9.1.(5), and the conditions of their listing and labeling, which may or may not permit the installation of firestopping around the duct.

A-3.1.9.3.   Outlet Boxes. For the purposes of Article 3.1.9.3., outlet boxes include, but are not limited to, electrical boxes, junction boxes, high and low voltage outlets, switches, enclosures for electrical equipment, laundry boxes, and shower diverters.

A-3.1.9.4.(8)   Combustible Branches.  Combustible branches for drain, waste and vent piping are permitted to be used to connect to a plumbing fixture within a fire compartment. The integrity of the fire separation is maintained through the use of a firestop system where the vertical stack piping penetrates the fire separation.

A-3.1.10.2.(4)   Firewall Construction. Inherent in the use of a firewall is the intent that this specialized wall construction provide the required fire-resistance rating while also being designed to resist physical damage—arising out of normal use—that would compromise the rating of the assembly. Traditionally, this has been accomplished by prescribing the use of noncombustible materials, which was in fact restricted to concrete or masonry. Sentences 3.1.10.2.(3) and (4) are intended to retain both of the characteristics of firewalls, while permitting greater flexibility in the use of materials and designs. The fire-resistance rating and damage protection attributes of a firewall may be provided by a single fire- and damage-resistant material such as concrete or masonry, by a fire- and damage-resistant membrane on a structural frame, or by separate components—one that provides the fire-resistance rating and another one that protects the firewall against damage.

If the firewall is composed of separate components, the fire-resistance rating of the fire-resistive component needs to be determined for this assembly on its own. In addition, if the damage protection component is physically attached to the fire-resistive component (for example, as a sacrificial layer), then for the purposes of determining the overall performance of the assembly, it is also necessary to determine through testing whether failure of the damage protection component during a fire affects the performance of the fire-resistive component.

A-3.1.11.3.(3)   Fire Blocks between Nailing and Supporting Elements. Sentence 3.1.11.3.(3) applies to the portion of the combustible ceiling finish that is attached using nailing elements and constructed in accordance with Sentence 3.1.6.14.(3), which permits 10% of the ceiling finish within a fire compartment to have a flame-spread rating not more than 150. Where this portion of ceiling finish creates a concealed space above it, exposed combustible elements within that space require fire blocks to limit the spread of fire.

A-3.1.11.5.(1)   Fire Blocks in Combustible Construction. Combustible construction referred to in Sentence 3.1.11.5.(1) includes all types of construction that do not comply with the requirements for noncombustible construction or encapsulated mass timber construction. All the elements within the concealed space can be combustible, unless required to be of noncombustible materials (e.g., certain categories of pipework and ducts), but the value of the flame-spread rating of the combustible materials determines the permitted extent of the concealed space between fire blocks. The materials to be considered include all construction materials regulated by this Code, including the framing and building services that are located in the concealed space. When designing fire blocking, consideration should be given to avoid restricting venting capabilities within concealed spaces. (See also Note A-5.6.2.1.)

A-3.1.11.5.(3) and (4)   Fire Blocks in Concealed Spaces.  To reduce the risk of fire spread in combustible concealed spaces within the types of buildings referred to in Sentences 3.1.11.5.(3) and (4), fire blocking is required regardless of whether the horizontal concealed space is protected by sprinklers or not, unless the space is filled with noncombustible insulation so that any air gap at the top of the insulation is very small. (See also Note A-3.1.11.5.(1) for roof venting.)

A 5- or 6-storey building constructed in accordance with Article 3.2.2.51. and buildings constructed in accordance with Article 3.2.2.48., 3.2.2.57. or 3.2.2.60. are required to be sprinklered in accordance with NFPA 13, “Standard for the Installation of Sprinkler Systems” (see Article 3.2.5.12.). NFPA 13 generally requires sprinklering of any concealed spaces of combustible construction or where large amounts of combustibles are present. However, NFPA 13 allows combustible concealed spaces not to be sprinklered in certain cases, including where concealed spaces are filled almost entirely with noncombustible insulation, where spaces contain only materials with a low flame-spread rating, and where limited access or the size of the space makes it impractical to install sprinklers. For certain types of construction in combustible concealed spaces that are not sprinklered, NFPA 13 mandates fire blocking beyond the minimum specified in Sentence 3.1.11.5.(3).

A-3.1.11.7.(7)   Integrity of Fire Blocks. Sentence 3.1.11.7.(7), together with Article 3.1.9.1., is intended to ensure that the integrity of fire blocks is maintained at areas where they are penetrated. This requirement is satisfied by the use of generic firestops such as mineral wool, gypsum plaster or Portland cement mortar, or by the use of sealants that form part of a firestop tested in accordance with CAN/ULC-S115, “Standard Method of Fire Tests of Firestop Systems.”

A-3.1.11.7.(8)   Fire Blocks. Figure A-3.1.11.7.(8) shows the location of the semi-rigid fibre insulation board at the intersection between walls and floors in wood-frame construction. The figure is intended to illustrate the fire block detail and not a design of a fire separation.

Figure A-3.1.11.7.(8)

Fire block

A-3.1.13.2.(2)   Folding Partition. Folding partitions used to divide a space into separate rooms are not considered as doors for the purposes of this Sentence.

A-3.1.18.   Tents and Air-Supported Structures. The requirements in this Subsection are intended to be limited to certain types of structure. For instance, the word “tent” as used in the Code is intended to refer to a temporary shelter which is used at an open air event such as a fair or an exhibition. A tent will normally be constructed of a fabric held up by poles and attached to the ground by ties. The requirements for tents, however, are not intended to be applied to fabric structures located on buildings.

The term “air-supported structure,” as used in the Code, refers to an envelope which is held up by air pressure alone and which is erected on the ground or above a basement. The structure will usually require ballast or a positive ground anchorage system around the entire perimeter to secure it to the ground or basement. To reinforce this intent, the Code prohibits the location of an air-supported structure above the first storey of any building.

The requirements of Subsection 3.1.18. are not intended to apply to air-supported roof assemblies on buildings, such as domed stadia, or to other types of air-supported structures, such as those over swimming pools situated on the roofs of buildings, which would not be anchored at or near ground level. These assemblies or structures are normally designed and evaluated on the basis of alternative solutions as permitted by Article 1.2.1.1. of Division A.

A-3.2.1.1.(3)(a)   Mezzanine Area. The permitted area of the mezzanine for the purposes of determining the allowable percentage is to be based on the open area of the floor of the space in which the mezzanine is located. The Code does not restrict the enclosing of space below the mezzanine but the enclosed area must be deducted from the area of the overall space before applying the percentage allowance.

A-3.2.1.1.(8)   Accessible Service Space. These service spaces are often referred to as interstitial spaces and are designed to allow service personnel to enter and undertake maintenance or installation within the space. Catwalks or flooring are usually included to provide a walking or access surface. Even when flooring is included, it is not intended that the interstitial space should be considered as a storey for the purposes of the Code unless the space is used for purposes other than servicing or the storage of materials and equipment to be used for building services within that space.

A-3.2.2.2.(1)   Special and Unusual Structures. Examples of structures which cannot be identified with the descriptions of buildings in Articles 3.2.2.20. to 3.2.2.92. include grain elevators, refineries and towers. Publications that may be consulted to establish good engineering practice for the purposes of Article 3.2.2.2. include the NFPA “Fire Protection Handbook,” Factory Mutual Data Sheets, and publications of the Society for Fire Protection Engineering.

A-3.2.2.17.(1)   Roof Assemblies in Gymnasiums, Swimming Pools, Arenas and Rinks. The permission to waive the fire-resistance rating requirements for roof assemblies over gymnasiums, swimming pools, arenas and rinks that meet the conditions of Sentence 3.2.2.17.(1) includes the permission to waive the requirements relating to minimum size and construction details stated in Article 3.1.4.7. for wood elements in roof assemblies of heavy timber construction on buildings conforming to Articles 3.2.2.25. and 3.2.2.32. However, wood elements in roof assemblies of heavy timber construction on buildings conforming to Article 3.2.2.30. must nevertheless meet the requirements of Article 3.1.4.7.

A-3.2.2.18.(2)   Sprinkler Extent. A literal interpretation of Article 3.2.2.6. and Sentences 3.2.2.4.(1) and (2) could require installation of an automatic sprinkler system throughout all storeys of a building regardless of options in Articles 3.2.2.20. to 3.2.2.92. to construct one or more storeys without installation of sprinklers. It is the intent of the Code that all storeys below a storey in which an automatic sprinkler system is installed should also be protected by an automatic sprinkler system to ensure that a fire in a lower storey does not incapacitate the automatic sprinkler system or overwhelm an automatic sprinkler system in an upper storey. Persons in an upper storey in which waivers or reductions of other fire safety systems are permitted would be exposed to an increased risk from a fire on a lower storey. This concept also applies to situations in which an automatic sprinkler system has been installed within a floor area in order to modify other safety requirements applying within the floor area. If the uppermost storey or storeys of a building can be constructed without the installation of an automatic sprinkler system it is not necessary that an automatic sprinkler system required in a lower storey be extended into the upper storey or storeys.

A-3.2.2.35.(4)   Sprinkler Requirements.  Spaces in a building of Group A, Division 4 occupancy that are intended to be equipped with sprinklers include, but are not limited to, dressing and changing rooms, concession stands and areas, toilet rooms, locker rooms, storage areas, service rooms, offices and other spaces that provide service to the building. The enclosure of seating areas with glazing needs special consideration in determining the requirements for sprinklers. For example, if the enclosed area is used for the consumption of food and beverages, it should be classified as Group A, Division 2 and the appropriate requirements of that classification applied. Enclosure of limited spaces above seating areas for press and media purposes is not considered to require the installation of sprinklers.

A-3.2.2.48.(4) and 3.2.2.57.(3)   Occupancy Combinations in Buildings of Mixed Construction. Buildings conforming to the building height and area limits and the other fire protection requirements of Article 3.2.2.48. or 3.2.2.57. may be entirely constructed of encapsulated mass timber construction and incorporate the occupancies specifically permitted by Sentence 3.2.2.48.(4) or 3.2.2.57.(3)., for example, Group A, Division 2 major occupancies on the first to third storeys, Group E major occupancies on the first and second storeys, and a parking garage on the first to fourth storeys.

Alternatively, the requirements of Articles 3.2.2.4. to 3.2.2.8. for superimposed major occupancies can be applied, resulting in buildings of mixed construction conforming to the building height and area limits for encapsulated mass timber construction and in which the lower storeys are of noncombustible construction and the upper storeys are of combustible construction. For example, a Group A, Division 2 or Group B, Division 3 major occupancy could be located on the first 4 storeys of a 12‐storey Group C building constructed in accordance with Article 3.2.2.48., as long as these first 4 storeys were constructed of noncombustible construction in accordance with Article 3.2.2.23. or 3.2.2.42., as applicable. (See also Articles 3.2.2.6. and 3.2.2.7.)

A-3.2.2.51.(5) and 3.2.2.60.(4)   Occupancy Combinations in Buildings of Mixed Construction. Buildings conforming to the building height and area limits and the other fire protection requirements of Article 3.2.2.51. or 3.2.2.60. are permitted to be entirely constructed of combustible construction and incorporate the occupancies specifically permitted by Sentence 3.2.2.51.(5) or 3.2.2.60.(4): for example, Group A, Division 2 and Group E major occupancies on the first and second storeys, and a parking garage on the first to third storeys.

Alternatively, the requirements of Articles 3.2.2.4. to 3.2.2.8. for superimposed major occupancies can be applied, resulting in buildings of mixed construction conforming to the building height and area limits of Article 3.2.2.51. or 3.2.2.60. and in which the lower storeys are of noncombustible construction and the upper storeys are of combustible construction. For example, a Group A, Division 2 or Group B, Division 3 major occupancy could be located on the first 4 storeys of a 6‐storey Group C building constructed in accordance with Article 3.2.2.51., as long as these first 4 storeys were constructed of noncombustible construction in accordance with Article 3.2.2.23. or 3.2.2.42., as applicable. (See also Articles 3.2.2.6. and 3.2.2.7.)

A-3.2.3.   Fire Protection Related to Limiting Distance versus Separation Between Buildings. Code provisions that address protection against fire spread from building to building use the limiting distance (see the definition in Article 1.4.1.2. of Division A) for a building rather than using the distance between adjacent buildings on separate properties, since this would result in situations where the design and construction of a building on one property affects the design and construction of a building on an adjacent property.

The Code requirements that deal with reducing the probability of building-to-building fire spread were originally developed based on the assumption that the exposing building faces of adjacent buildings are of similar size and configuration, and are equidistant from the shared property line. Where buildings are of different sizes, the smaller building may be subject to a higher heat flux in the event of a fire compared to the larger building. Where buildings are closely spaced and not equidistant from the property line, the construction of the building with the greater limiting distance does not recognize the proximity of the building with the lesser limiting distance.

The Code has more stringent requirements for buildings with lesser limiting distance as regards the maximum area and spacing of unprotected openings, and the construction, cladding and fire resistance of walls. This increased stringency recognizes that the fire hazard is greater where buildings are closer together and that adjacent buildings may have exposing building faces of different sizes, configurations or limiting distances, which could further increase the hazard.

The authority having jurisdiction may also address limiting distances through legal agreements with the parties involved that stipulate that the limiting distance be measured to a line that is not the property line. Such agreements would normally be registered with the titles of both properties.

A-3.2.3.1.(4)   Spatial Separation Design. In the application of Sentences 3.2.3.1.(3) and (4), it is intended that Sentence (3) be used first to establish the basic requirements for the exterior wall in terms of fire-resistance rating, type of construction and type of cladding. The percentage of unprotected openings determined from the application of Sentence (3) would be unnecessarily restrictive if the actual unprotected openings occur in a plane that is set back from the front of the building face.

Sentence (4) applies to the calculation of the allowable percentage of unprotected openings based upon projection onto a plane that is in front of all unprotected openings. The application of these two Sentences is shown in Figure A-3.2.3.1.(4). The modifications permitted by Article 3.2.3.12. would be applied, if applicable, to the area of unprotected openings derived from Sentence (4).

Figure A-3.2.3.1.(4)

Spatial separation design

A-3.2.3.1.(8)   Intervention Time and Limiting Distance. The total time from the start of a fire until fire suppression by the fire department depends on the time taken for a series of actions. Sentence 3.2.3.1.(8) is only concerned with the time from receipt of notification of a fire by the fire department until the arrival of the first fire department vehicle at the building. It specifies a 10-min time limit which must be met in more than 90% of the calls to the building served by the fire department. This reliability level and provision for flexibility is essentially consistent with NFPA 1710, “Standard for the Organization and Deployment of Fire Suppression Operations, Emergency Medical Operations, and Special Operations to the Public by Career Fire Departments.”

Clause 4.1.2.1 of NFPA 1710 establishes “time objectives” for fire incidents as follows:

•   1 min (60 s) for turn-out of responders after receipt of notification of a fire, and

•   4 min (240 s) or less for arrival of the first arriving engine company at a fire suppression incident and/or 8 min (480 s) or less for the deployment of a full first alarm assignment at a fire suppression incident.

The standard requires that the fire department establish a “performance objective” of not less than 90% for each response time objective. This reliability level is referred to in NFPA 1710 as a “performance objective.”

Where the 10-min limit cannot be met by the fire department at least 90% of the time, Sentence 3.2.3.1.(8) specifies that a value corresponding to half the actual limiting distance be used in requirements that depend on limiting distance to define other criteria.

For new subdivisions, legal agreements may be made for the construction of fire stations to serve those areas. The fire department response time in those subdivisions may temporarily exceed 10 min until the fire station is constructed.

See also Sentences 9.10.14.3.(1) and 9.10.15.3.(1).

A-3.2.3.4.(1)   Party Walls. By definition, a party wall is a wall jointly owned and used by two parties under easement agreement or by right in law, and is erected at or upon a line that separates two parcels of land that are, or are capable of being, separate real estate entities. With the exception of some Part 9 residential occupancies, both Part 3 and Part 9 of the Code require that, where party walls are constructed on property lines, they be constructed as a 2- or 4-hour firewall (see also Article 9.10.11.1.). Buildings on each side of a party wall that is constructed as a firewall are considered as separate buildings (see Article 1.3.3.4. of Division A).

In a Part 9 residential building that has no dwelling unit above another, a party wall constructed on a property line between two dwelling units need not be constructed as a firewall, but must be constructed as a continuous fire separation that extends from the top of the footings to the underside of the roof, with a fire-resistance rating of at least 1 hour (see Article 9.10.11.2.). These party walls do not create separate buildings.

Where two parties share a party wall on a property line, each party is responsible for fire safety in their unit, but is still subject to possible fire risks from activities in the adjoining units. The separating party wall is intended to provide a significant degree of fire protection between the adjacent units, often exceeding even that required between suites in multiple-unit residential and non-residential occupancies.

When a building spans a property line, constructing a party wall on the property line is not mandated by the Code, but subdividing the building at the property line is an option the owner can consider. The Code permits a building constructed on more than one property to be designed as a single undivided building, whether the properties have a common owner or not. However, if a subdividing wall is constructed on the property line within the building for the purpose of separating the two real estate entities and is shared by two different owners, the wall would, by definition, be deemed a party wall. As such, this party wall would need to meet the construction requirements described above, depending on the building's occupancy classification and size.

A building that spans two or more properties, but that does not have a party wall at the property line, may need to address the Code requirements for party walls in the future.

A-3.2.3.6.(2)   Protection of Roof Soffits Near Property Lines. Sentences 3.2.3.6.(2) to (5) and parallel Sentences 9.10.14.5.(5) to (7) and 9.10.15.5.(5) to (7) provide requirements for the protection of soffits where the soffit of the subject building is located close to the property line or to an imaginary line between two buildings on the same property. Fire from inside the roof space of the subject building can exit unprotected soffits and expose the adjacent building to flames.

A-3.2.3.7.(4)(d)(iv)   Thickness of Cladding. In the case of insulated vinyl siding, the maximum 2 mm thickness stated in Subclause 3.2.3.7.(4)(d)(iv) refers to the total thickness of the siding and the insulation, not of the siding alone.

A-3.2.3.14.(1)   Wall Exposed to Another Wall. The requirements of Article 3.2.3.14. are to ensure that the control of fire spread by the interior fire separations between fire compartments is not defeated through the spread of fire by thermal radiation outside the building. Minimum spatial separations are specified between the openings in separate fire compartments where the exterior faces of these compartments are deemed to expose each other to a thermal radiation hazard. This situation may arise where the angle, θ, between the intersecting planes of the exposing building faces is 135° or less. Examples of situations that would be addressed by this Article are shown in Figures A-3.2.3.14.(1)-A, A-3.2.3.14.(1)-B and A-3.2.3.14.(1)-C.

Figure A-3.2.3.14.(1)-A

Openings in walls at a right-angle corner

Figure A-3.2.3.14.(1)-B

Openings in walls that are parallel to one another

Figure A-3.2.3.14.(1)-C

Openings in walls with an included angle of 45°

A-3.2.4.   Fire Alarm System. The term “fire alarm system” used in this Subsection applies to fire alarm systems with or without voice communication capability.

A-3.2.4.4.(1)   Single Stage Fire Alarm System. This requirement, in combination with Article 3.2.4.22., is intended to allow for the provision of voice communication capability as an integral part of a single stage fire alarm system.

A-3.2.4.4.(2)(c)   Fire Alarm Alert Signal. In a 2-stage fire alarm system described in Sentence 3.2.4.4.(2), the alert signal may be transmitted to audible signal devices in designated locations or to audible signal devices throughout the building. If actuated, the second stage alarm signal in a 2-stage fire alarm system may sound throughout all zones in the building. All manual station key switches would typically initiate the alarm signal.

Sentence 3.2.4.4.(2) also allows the implementation of a “zoned 2-stage” sequence of operation, whereby the alarm signal sounds in the zone of key switch actuation (and perhaps in the adjacent zones, which may be the storey above and the storey below) and the alert signal sounds throughout the rest of the building. This sequencing would be created automatically by the fire alarm control unit.

The key or special device referred to in Clause 3.2.4.4.(2)(c) should be immediately available to all persons on duty who have been given authority to sound an alarm signal.

A-3.2.4.4.(2)   Two-Stage Fire Alarm System. Sentence 3.2.4.4.(2), in combination with Article 3.2.4.22. or 3.2.4.23., is intended to allow for the provision of voice communication capability as an integral part of a 2-stage fire alarm system.

A-3.2.4.6.(2)   Access to Silencing Switches. This requirement is intended to prevent easy access to silencing switches. The satisfactory operation of a fire alarm system to alert the occupants of a building to an emergency is predicated on the assumption that the alarm signal will be silenced only after responsible staff have verified that no emergency exists. Details on the emergency procedures to be used in case of fire are contained in the British Columbia Fire Code.

A-3.2.4.7.(4)   Design and Installation of Fire Department Notification. In some jurisdictions, the fire department may utilize, or have available, a municipal fire alarm system or equipment intended for receiving notification by means of a direct connection. If used, it is expected that these systems and installations conform to the requirements of Sentence (4) so as to achieve and provide a uniform and reliable level of service. It is also intended that a proprietary central station as well as a fire brigade used by a large corporation, university campus or similar site comply with Sentence (4).

CAN/ULC-S561, “Standard for Installation and Services for Fire Signal Receiving Centres and Systems,” which is referenced in Sentence 3.2.4.7.(4), and CAN/ULC-S524, “Standard for Installation of Fire Alarm Systems,” which is referenced in Sentence 3.2.4.5.(1), go hand-in-hand: conformity to CAN/ULC-S561 entails conformity with the fire alarm system components required in that standard, which include the fire alarm transmitter (signal transmitting unit), the interconnections, and the communication path.

A-3.2.4.7.(5)(b)   Emergency Telephone Number.  In many municipalities an emergency telephone number, for example 911, is used for all emergency services and it is preferable to post that number.

A-3.2.4.8.(2)   Fire Alarm Zones. Alarm initiating devices referred to in this Sentence include fire detectors, waterflow switches and manual stations. If a room or space in a building extends through more than one storey of the building, as in the case of multi-level dwelling units and machinery rooms, judgment must be exercised in the zoning and annunciation of the fire detectors in that room or space. In general, the lowest storey on which access is provided into the room or space should be indicated on the annunciator to avoid unnecessary delays for the responding firefighters. Consideration should also be given to the use of numbers or letters on the annunciator that correspond to those used in the building elevators.

A-3.2.4.9.(3)(f)   Supervision for Fire Pumps. Specific electrical supervision for fire pumps is stated in NFPA 20, “Standard for the Installation of Stationary Pumps for Fire Protection,” which is referenced in NFPA 13, “Standard for the Installation of Sprinkler Systems.”

A-3.2.4.11.(1)   Smoke Detector Location. In the design and installation of the smoke detection system, consideration must be given to all features which could have a bearing on the location and sensitivity of the detectors, including ceiling height, sloped ceilings, diffusion from air conditioning and ventilating currents, obstructions, baffles, and other pertinent physical configurations that might interfere with the proper operation of the system.

A-3.2.4.11.(3)   Visible Signals. If staff located in each zone or compartment can see each sleeping room door, visible signals may be located above each door. If staff cannot see every door, it is intended that the visible signals be provided at the location where the staff are normally in attendance. The audible signal is intended to alert staff of the need to check the visible signals.

A-3.2.4.16.(1)   Manual Station. Only one manual station need be provided near a group of doors serving as a principal entrance or as a single exit facility. Egress facilities that are provided for convenience and that do not include all the features of required exits need not be provided with a manual pull station.

A-3.2.4.18.   Acoustic Measurement and Terminology. The following notes on acoustic measurement and terminology are intended to assist in the application of the requirements for audibility of fire alarm system sounding devices.

The background or ambient measurement should be a spatial averaged A-weighted equivalent sound level measured for 60 s. This can be obtained using an integrating sound level meter with the integration time set to 60 s. During the measurement period the meter should be slowly moved about so as to sample the space uniformly but coming no closer than 0.5 m from any solid wall, floor or ceiling. Alternatively, measurements can be made at 3 or more positions throughout the space and an energy average calculated.

The measurement of the alarm level depends on the type of alarm signal. If the signal is a continuous signal from a bell or siren, the spatial averaged A-weighted equivalent sound level should be obtained. The integration time should be long enough to obtain a reasonable spatial average of the space, but not less than 10 s.

If the alarm has a temporal pattern, then the A-weighted sound level should be measured using the 'fast' time constant during the 'on' part of the cycle. In this situation it is not appropriate to use an integrating sound level meter. Since the duty cycle of the alarm is only 37.5% at best, that type of meter would give a reading that is 4 or more decibels lower than the level while the alarm is 'on.' A number of measurements should be made about the space in question and the average value used to obtain a good spatial representation. Strictly speaking, the energy average of the measurements should be used; however, the frequency spectrum associated with most alarms is of a type that should give little variation about the space. If the measured levels don't vary by more than 2 to 3 dB, then an arithmetic average rather than an energy average can be used.

Effect of Furnishings

The final inspection of a fire alarm system is seldom made when the building is furnished and ready for occupancy. This results in measured levels which may be several decibels higher than will be found in the occupied building. The importance of this difference depends on the situation.

If the building is complete except for furnishings, so that the sources of ambient noise are present, then the amount by which the alarm signal exceeds the ambient level will not change appreciably with the introduction of furnishings. In this case both levels will be reduced by about the same amount.

If the primary source of ambient noise will be office equipment and workers, as would be expected in an open plan office, then measurements made prior to occupancy may differ substantially from those made afterwards. This may be true for both the absolute sound levels and the difference between the alarm level and the ambient.

A problem arises in trying to estimate what the absolute sound levels will be after the building is occupied.

In general, if the measurement is made in a totally bare room then the level will be about 3 dB higher than if the room were carpeted, assuming a reasonable carpet with an underlay. In most cases this will account for most of the absorption in the room and no further correction will be necessary. Adding heavy drapes and absorptive furnishings to a carpeted room can reduce the sound level by a further 2 to 3 dB.

Commercial buildings are more problematic. For example, if an open plan office is measured before any office screens are installed, there could be a substantial difference in the before and after levels, depending on the distance to the nearest alarm device.

Glossary of Acoustical Terms

Audible: A signal is usually considered to be clearly audible if the A-weighted sound level exceeds the level of ambient noise by 15 dB or more.

Awakening threshold: The level of sound that will awaken a sleeping subject 50% of the time.

A-weighted: A frequency weighting network which emphasizes the middle frequency components similar to the response of the human ear. The A-weighted sound level correlates well with subjective assessment of the disturbing effects of sounds. The quantity is expressed in dBA.

Masked threshold: The level of sound at which a signal is just audible in ambient noise.

Sound level: A sound pressure level obtained using a signal to which a standard frequency-weighting has been applied.

Sound pressure: A fluctuating pressure superimposed on the static pressure by the presence of sound. The unqualified term means the root-mean-square sound pressure. In air, the static pressure is barometric pressure.

Sound pressure level: Ten times the common logarithm of the ratio of the square of the sound pressure under consideration to the square of the standard reference pressure of 20 mPa. The quantity obtained is expressed in decibels.

A-3.2.4.18.(1)   Alert and Alarm Signals.  Alert signals are part of a 2 stage fire alarm system. The intent of the first, alert, stage is to notify persons in authority of a potential threat to building occupants. If a continuously staffed location is available, the alert signal can be restricted to that location.

A-3.2.4.18.(2)   Alarm Signal Temporal Pattern. The temporal pattern of an alarm signal relates to the time during which the signal is produced and the intervals between the individual signal pulses. The international standard ISO 8201, “Acoustics – Audible emergency evacuation signal,” includes a pattern that is becoming widely used in different countries and it is appropriate for this pattern to be adopted in Canada. The temporal pattern can be produced on most signalling devices. Most existing alarm systems can be modified, and this pattern could be phased in when the systems require modification. The characteristic of the pattern is a 3-pulse phase followed by an off phase. The 3 pulses each consist of an on phase lasting for 0.5 ± 0.05 s followed by an off phase lasting for 0.5 ± 0.05 s sounded for 3 successive on periods and then followed by an off phase lasting for 1.5 ± 0.15 s. Figure A-3.2.4.18.(2)-A indicates the pattern that is intended.

Figure A-3.2.4.18.(2)-A

Temporal pattern for fire alarm signal

Although the diagram shows a square wave form, the wave can have other shapes that produce a similar effect.

If single stroke bells are to be used, the temporal pattern can be produced by having the bell struck three times at a rate of one stroke per second followed by an interval of 2 s of silence. Figure A-3.2.4.18.(2)-B shows the pattern that results.

Figure A-3.2.4.18.(2)-B

Temporal pattern imposed on a single stroke bell or chime

Note to Figure A-3.2.4.18.(2)-B:

(1) The on phase represents the time that the striker mechanism is actuated. The sound produced by the bell or chime will continue at a level that decreases until the striker mechanism is re-actuated.

A-3.2.4.18.(3)   Audibility of Alarm Systems. It is very difficult to specify exactly what types of sound patterns are considered to be “significantly different” from one another. The intent is to ensure that there is a noticeable or measurable difference between the alert signals and the alarm signals such that it reduces the possibility of confusion.

A-3.2.4.18.(4)   Sound Pressure Level. For the purposes of this requirement, an audible signalling device should not produce a sound pressure level more than 110 dBA when measured at a distance of 3 m.

A-3.2.4.18.(5)   Residential Sound Level.  In a building in which corridors or hallways serve more than one suite or dwelling unit, there will be situations in which an audible signal device cannot be placed in the corridor or hallway to alert persons sleeping in suites and dwelling units, because the sound level in the vicinity of the device would exceed that permitted by Sentence 3.2.4.18.(4). In these situations it will be necessary to supplement the building fire alarm system with an audible signal device in the suite or dwelling unit. These devices could be piezoelectric devices similar to the sounding units in many smoke alarms, subject to the device emitting the appropriate temporal pattern required by Sentence 3.2.4.18.(2).

A-3.2.4.18.(6)   Low Frequency Signal. Audible signal devices that emit a low frequency signal in the range of 470 Hz to 570 Hz have been shown to be more effective in waking people.

A-3.2.4.18.(8)   Disconnect Device for Dwelling Units. In order to minimize the annoyance caused by false and unwanted alarms, the disconnect will permit a person to silence the local audible device within the dwelling unit. At that time the person would be aware of sounds from devices in common spaces and could plan appropriate action. The disconnect will reduce the possibility of tampering with the audible devices.

A-3.2.4.18.(9) and (10)   Signal Circuits. Clause 3.2.4.18.(9)(a) permits Class A wiring, or Class B wiring with signal circuit isolators located outside of the suites, to serve audible signal devices within residential suites.

Clause 3.2.4.18.(9)(b) permits a separate signal circuit to serve each suite without the need for signal circuit isolators or Class A wiring.

Open circuits and Class A and Class B wiring circuits are terms defined in CAN/ULC-S524, “Standard for Installation of Fire Alarm Systems.”

A-3.2.4.19.(1)(g)   Visible Alarm Signals in Hotels and Motels.  Visible signal devices should be installed in a combination of regular suites and designated accessible suites in hotels and motels so that people who are deaf or hard of hearing can safely occupy either type of suite.

Visible signal devices are not required to be installed in all the rooms of the suite. The signal should be visible from any room in the suite, which can be accomplished by installing glazing panels between the rooms or additional visible signal devices.

In addition, CAN/ULC-S524, “Standard for Installation of Fire Alarm Systems,” requires that high-intensity strobes be used in sleeping rooms.

A-3.2.4.19.(3)   Visible Alarm Signal. CAN/ULC-S526, “Visible Signaling Devices for Fire Alarm and Signaling Systems, Including Accessories,” applies to visible signalling units. This document is referenced by the most recent standard for the installation of fire alarm systems and would automatically apply. Current Canadian technology does not integrate visible and audible alarms to have the same temporal pattern. Visible and audible alarms should have as close a temporal pattern as possible but without interference beats that might have a deleterious effect on some persons. Visible signalling devices with the same temporal pattern as required for audible devices are available from some sources and they should become available in Canada. Not all units that comply with the ULC standard will have sufficient power to adequately cover large areas; care will have to be taken to specify units with adequate power when large spaces are being designed.

A-3.2.4.20.(9)(a)   Smoke Alarm Installation. CSA C22.1, “Canadian Electrical Code, Part I,” which is adopted by the Electrical Safety Regulation, permits a smoke alarm to be installed on most residential circuits that carry lighting outlets and receptacles. It is the intent of the British Columbia Building Code that any other item on a circuit with a smoke alarm should be unlikely to be overloaded and trip the breaker with a resultant loss of power that is not sufficiently annoying for the breaker to be restored to the on position. It is considered that an interior bathroom light or a kitchen light fulfills this intent, but that circuits restricted to receptacles do not fulfill this intent.

A-3.2.4.20.(10)   Smoke Detectors in lieu of Smoke Alarms. It is intended that the smoke detector in this application will function as per the requirements of a smoke alarm; specifically, it will be a localized alarm to that suite. The advantage of this type of installation is that the detector would be monitored by the fire alarm panel, which would provide notification to supervisory personnel and be inspected as per CAN/ULC-S524, “Standard for Installation of Fire Alarm Systems.”

A-3.2.4.22.(1)(b)   Voice Messages. The concept of intelligibility expressed in Clause 3.2.4.22.(1)(b) is intended to mean that a person with average hearing and cognitive abilities is able to understand the messages that are transmitted into the space occupied by the person. There is no absolute measure to predetermine the effect of loudspeakers and it may be necessary, once the building has been furnished and occupied, to increase the number of loudspeakers to improve the quality of the messages.

The intelligibility of the message depends on the speech level, the background level, and the reverberation time of the space. ISO 7731, “Ergonomics – Danger signals for public and work areas – Auditory danger signals,” addresses audibility. The standard suggests that an A-weighted sound level at least 15 dBA above the ambient is required for audibility, but allows for more precise calculations using octave or 1/3 octave band frequencies to tailor the alarm signal for particular ambient noise conditions. Design of the alarm system is limited to ensuring that all areas receive an adequately loud alarm signal.

If a public address system is to be used to convey instructions during an emergency, then the requirements of the system are less straightforward. In general, however, a larger number of speakers operating at lower sound levels would be required.

Additional guidance on how to design and evaluate the intelligibility of a communication system can be found in the following documents:

•   IEC 60268-16, “Sound system equipment – Part 16: Objective rating of speech intelligibility by speech transmission index”

•   ISO 7240-19, “Fire detection and alarm systems – Part 19: Design, installation, commissioning and service of sound systems for emergency purposes”

•   NEMA SB 50, “Emergency Communications Audio Intelligibility Applications Guide”

•   Annex D of NFPA 72, “National Fire Alarm and Signaling Code”

A-3.2.5.4.(1)   Fire Department Access for Detention Buildings. Buildings of Group B, Division 1 used for housing persons who are under restraint include security measures that would prevent normal access by local fire departments. These security measures include fencing around the building site, exterior walls without openings or openings which are either very small or fitted with bars, and doors that are equipped with security hardware that would prevent easy entry. These buildings would have firefighting equipment installed and the staff would be trained to handle any small incipient fires. It is expected that appropriate fire safety planning would be undertaken in conjunction with local fire departments in order that special emergencies could be handled in a cooperative manner.

A-3.2.5.6.(1)   Fire Department Access Route. The design and construction of fire department access routes involves the consideration of many variables, some of which are specified in the requirements in the Code. All these variables should be considered in relation to the type and size of fire department vehicles available in the municipality or area where the building will be constructed. It is appropriate, therefore, that the local fire department be consulted prior to the design and construction of access routes.

A-3.2.5.7.(1)   Water Supply. The intent of Sentence 3.2.5.7.(1) is that an adequate water supply for firefighting be readily available and of sufficient volume and pressure to enable emergency response personnel to control fire growth so as to enable the safe evacuation of occupants and the conduct of search and rescue operations, prevent the fire from spreading to adjacent buildings, and provide a limited measure of property protection.

The water supply requirements for buildings containing internal fire suppression systems, including sprinkler systems and standpipe systems, are contained in specific standards referenced in the Code. Compliance with the referenced standard, including any variations made by this Code, is deemed to satisfy the intent of Sentence 3.2.5.7.(1). However, it will be necessary to verify that an adequate source of water is available at the building site to meet the required quantities and pressures.

For a building with no internal fire suppression system, the determination of the minimum requirements applicable to the water supply for firefighting is relevant mainly to building sites not serviced by municipal water supply systems. For building sites serviced by municipal water supply systems, where the water supply duration is not a concern, water supply flow rates at minimum pressures is the main focus of this provision. However, where municipal water supply capacities are limited, it may be necessary for buildings to have supplemental water supplies on site or readily available.

The sources of water supply for firefighting purposes may be natural or developed. Natural sources may include ponds, lakes, rivers, streams, bays, creeks, and springs. Developed sources may include aboveground tanks, elevated gravity tanks, cisterns, swimming pools, wells, reservoirs, aqueducts, artesian wells, tankers, hydrants served by a public or private water system, and canals. Consideration should be given to ensuring that water sources will be accessible to fire department equipment under all climatic conditions.

The volume of on-site water supply is dependent on the building size, construction, occupancy, exposure and environmental impact potential, and should be sufficient to allow at least 30 minutes of fire department hose stream use.

For the purposes of calculating adequate water supply requirements for fire fighting, the following documents may be useful:

- Insurance Services Office (ISO), “Needed Fire Flow Guide,”

- NFPA 1142, “Standard on Water Supplies for Suburban and Rural Fire Fighting,” and

- American Water Works Association, “Distribution Requirements for Fire Protection.”

A-3.2.5.9.(4)(c)   Fire Department Pumping Equipment. Availability of appropriate pumping equipment from the local fire department or, in the case of industrial plants or complexes, from their fire brigade, is considered sufficient to meet the intent of this requirement.

A-3.2.5.11.(2)   Hose Stations. A building that is partially sprinklered may have some floor areas where local sprinklers are installed that do not cover the entire floor area. It is intended that hose stations be provided in these floor areas to allow emergency responders to fight fires that cannot be controlled by local sprinklers.

A-3.2.5.12.(1)   Sprinkler System Design. In NFPA 13, “Standard for the Installation of Sprinkler Systems,” reference is made to other NFPA standards that contain additional sprinkler design criteria. These criteria apply to industrial occupancies with high fire loads and industrial occupancies intended for the use, manufacture or storage of highly flammable materials. Therefore, while only NFPA 13 is called up directly by Sentence 3.2.5.12.(1), the additional criteria in the other NFPA standards are included automatically.

In some NFPA standards, certain aspects of sprinkler protection are dependent on the fire-resistance rating of the vertical structural members. In these cases, the sprinkler system design options can be affected by the fire-resistance rating of these elements. For example, in buildings used for the storage of rubber tires, sprinklers directed at the sides of a column are required if the column does not have the required fire-resistance rating.

Other NFPA standards may require that certain occupancies be sprinklered in conformance with NFPA 13, as in the case of some garages. These requirements do not supersede the requirements in the Code. An occupancy is required to be sprinklered only when this is specified in the Code, but when it is so required, it must be sprinklered in conformance with NFPA 13 and its referenced standards.

Additionally, while Part 4 contains seismic force provisions that apply to the design of sprinklers, NFPA 13 contains other structural requirements for sprinklers that are also required to be met.

A-3.2.5.12.(2)   Sprinklering of Residential Buildings above a Storage Garage Considered as a Separate Building. For the purpose of determining whether NFPA 13R, “Standard for the Installation of Sprinkler Systems in Low-Rise Residential Occupancies,” applies to a residential building constructed over a storage garage, it is not intended that a storage garage constructed as a separate building in accordance with Article 3.2.1.2. be considered as a storey when determining the building height of the residential building. Similarly, this would not preclude the use of NFPA 13D, “Standard for the Installation of Sprinkler Systems in One- and Two-Family Dwellings and Manufactured Homes,” for any one- or two-family home constructed above such a storage garage.

A-3.2.5.12.(6)   Sprinklering of Roof Assemblies. Sprinkler protection for roof assemblies in lieu of fire resistance is based on the assumption that the sprinklers will protect the roof assembly from the effects of fire in spaces below the roof. If a ceiling membrane is installed, the sprinklers would have to be located below the membrane in order to react quickly to the fire. In certain instances, however, sprinklers may be required within the concealed spaces as well as below the membrane. NFPA 13, “Standard for the Installation of Sprinkler Systems,” requires sprinklers in certain concealed spaces.

According to NFPA 13 and 13R, some small rooms and closets within a dwelling unit in a sprinklered building, including those that may be in the storey immediately below the roof assembly, do not require sprinklers. However, the British Columbia Building Code requires sprinkler protection within all rooms and closets immediately below the roof so as to control any fire that might start in that space and thereby limit the probability of the fire spreading into the roof assembly.

Moreover, NFPA 13D, “Standard for the Installation of Sprinkler Systems in One- and Two-Family Dwellings and Manufactured Homes,” also allows the omission of sprinklers in such rooms and closets under certain circumstances, provided the building is sprinklered in conformance with this standard. In this case, the British Columbia Building Code concurs with the provisions of the NFPA 13D standard.

A-3.2.5.12.(7)   Balconies and Decks. The intent of Sentence 3.2.5.12.(7) is to suppress or control the spread of a fire originating from a balcony or deck to the roof assembly or other parts of the building.

A-3.2.5.12.(8)   Sprinkler Rating. The requirements of this Sentence can be met by using sprinklers with a rating of 79°C to 107°C.

A-3.2.5.12.(10) Fast-Response Sprinklers. Several types of sprinkler will respond to a fire faster than a conventional standard response sprinkler. The Response Time Index (RTI) is used to quantify the sensitivity of the sprinkler link for any given sprinkler. The RTI for the group of fast-response sprinklers described below will on average range from 22 s0.5•m0.5 to 33 s0.5•m0.5. RTI values for standard response sprinklers will typically be in the range of 83 s0.5•m0.5 to 110 s 0.5•m0.5.

Any confusion as to the appropriate type of fast-response sprinkler for different types of building should be alleviated by considering the testing criteria described below and the reference to the appropriate NFPA installation standards.

Although the Code specifies where fast-response sprinklers are required, it does not prevent the appropriate use of fast-response sprinklers in other occupancies.

Residential sprinklers are tested in accordance with ANSI/UL-1626, “Residential Sprinklers for Fire-Protection Service.” They are installed in accordance with NFPA 13R, “Installation of Sprinkler Systems in Residential Occupancies up to and Including Four Stories in Height,” with NFPA 13D, “Installation of Sprinkler Systems in One- and Two-Family Dwellings and Manufactured Homes,” and with Section 5-4.5 of NFPA 13, “Installation of Sprinkler Systems,” for residential occupancies and for dwelling units.

Quick-response sprinklers are tested in accordance with ANSI/UL-199, “Automatic Sprinklers for Fire-Protection Service.” They are installed in accordance with NFPA 13, “Installation of Sprinkler Systems,” for spacing, density and location. They are acceptable for limited use as described in NFPA 13R, “Installation of Sprinkler Systems in Residential Occupancies up to and Including Four Stories in Height,” but are not permitted for use under NFPA 13D, “Installation of Sprinkler Systems in One- and Two-Family Dwellings and Manufactured Homes.”

Early-suppression fast-response sprinklers are tested in accordance with FM Approvals Class Number 2008, “Approval Standard for Quick Response Storage Sprinklers for Fire Protection.” They are installed in accordance with NFPA 13, “Installation of Sprinkler Systems,” but are not accepted for use under either NFPA 13R, “Installation of Sprinkler Systems in Residential Occupancies up to and Including Four Stories in Height,” or NFPA 13D, “Installation of Sprinkler Systems in One- and Two-Family Dwellings and Manufactured Homes.”

Quick-response extended-coverage sprinklers are tested in accordance with ANSI/UL 199, “Automatic Sprinklers for Fire-Protection Service.” They are installed in accordance with NFPA 13, “Installation of Sprinkler Systems,” for spacing, density and location. They are acceptable for limited use as permitted by NFPA 13R, “Installation of Sprinkler Systems in Residential Occupancies up to and Including Four Stories in Height,” but are not permitted for use under NFPA 13D, “Installation of Sprinkler Systems in One- and Two-Family Dwellings and Manufactured Homes.”

A-3.2.5.13.(1)   Hazard Classification for Sprinkler Selection. The reference to light hazard occupancies is based on the descriptions of these occupancies given in NFPA 13, “Standard for the Installation of Sprinkler Systems,” and is intended only for use in the design of sprinkler systems. These descriptions should not be confused with the occupancy classifications in the Code.

In NFPA 13, a light hazard occupancy is one in which the quantity or combustibility of contents is low and fires with relatively low rates of heat release are expected. Typical buildings or parts of buildings include: churches; clubs; eaves and overhangs, if of combustible construction with no combustibles beneath; educational buildings; hospitals; institutional buildings; libraries, except very large stack rooms; museums; nursing or convalescent homes; offices, including data processing rooms; residential buildings; restaurant seating areas; theatres and auditoria, excluding stages and proscenia; and unused attics.

Although NFPA 13R, “Standard for the Installation of Sprinkler Systems in Low-Rise Residential Occupancies,” and NFPA 13D, “Standard for the Installation of Sprinkler Systems in One- and Two-Family Dwellings and Manufactured Homes,” as referenced by NFPA 13, are concerned with specific types of residential occupancy, namely apartment buildings up to four storeys, one and two family dwellings, and mobile homes, for the purpose of acceptance of combustible sprinkler piping these occupancies are considered to be included in the category of residential buildings under light hazard occupancies.

A-3.2.5.18.(1)   Fire Pumps. In order to ensure an adequate water supply, it may be necessary to install a fire pump for a building that has either a standpipe system or an automatic sprinkler system installed.

A-3.2.6.   Smoke Control for High Buildings. Experience with high buildings has shown that the time required for complete evacuation can exceed that which is considered necessary for the safe egress of all occupants. Studies of the “chimney effect” and observations of smoke movement in actual fires have shown that fire compartmentation to contain a fire on any one storey will not usually prevent the movement of smoke through elevator, stair and other vertical shafts to the upper floors of a high building. Occupants of a high building in which an automatic sprinkler system is not installed, and particularly those on upper storeys, could be faced with severe smoke conditions from fires occurring in storeys below them before their own evacuation is possible. The requirements of Subsection 3.2.6. are intended to maintain safe conditions for occupants of a high building who may have to remain in the building during a fire, and to assist the firefighters by providing efficient access to the fire floor. The Notes for Subsection 3.2.6. are intended to assist a designer in complying with the requirements of Subsection 3.2.6. The knowledge requirements are well within the capabilities of a competent designer. The designer should appreciate, however, that successful application requires a clear understanding of the principles that govern smoke movement. Subsection 3.2.6. contains only those items that relate to the design and construction of a building; operation of the facilities and recommended actions to be taken by the building owner, occupant and fire department are covered by the British Columbia Fire Code.

The designer is cautioned that the tabular and graphical information in the Notes for Subsection 3.2.6. was developed for buildings having conventional configurations. The designer has to judge the extent to which the building under consideration has characteristics that will allow the application of this information; this is particularly true of designs employing air-handling systems for which a realistic assessment of the leakage characteristics of the enclosures of spaces may be critical.

It is assumed that buildings regulated by Subsection 3.2.6. will be in an area served by a fire department capable of an early response and that all firefighting and rescue situations will be under the direct control of the officer-in-charge of the fire department responding to the emergency. It is important that firefighters be provided with a smoke-free access to fire floors below grade. Provisions are included to separate exit stairways serving storeys above grade from those serving storeys below grade, and to limit entry of smoke into these shafts. Similarly, elevator hoistways and service shafts are required to be provided with a separation near grade, or be designed to limit their functioning as paths of smoke movement into upper floor areas from storeys below grade.

It is assumed that in the event of fire, occupants of the floor on which the fire occurs will leave by exit stairs immediately following the sounding of a fire alarm, and that occupants of the floor immediately above the floor on which the fire occurs will be advised to leave by the first fire department officer on the scene or other person assigned this responsibility. Occupants of all other floors may remain on their floors unless otherwise directed. It is also assumed that the owner of the building has complied with the Emergency Planning Section of the British Columbia Fire Code by preparing a comprehensive fire safety plan to safeguard the building occupants and that the building supervisory staff are familiar with the requirements of Subsection 3.2.6. and with their responsibilities under the fire safety plan.

The British Columbia Building Code requires that a check be made of the smoke control and mechanical venting systems. Testing will indicate deficiencies caused by inexact estimates of the leakage characteristics or of air supply requirements and, in all but the most extreme cases, will provide an opportunity for appropriate adjustments before the system is put into service.

A-3.2.6.2.(2)   Stairway Protection Below Lowest Exit Level. A stairway serving floors below the lowest exit level is considered to comply with the intent of Sentence 3.2.6.2.(2) if the following conditions are satisfied.

1)    The stairway has a vent or door to the outdoors at or near the top of the stair shaft that has an openable area of not less than 0.1 m2 for each storey served by the stairway, less 0.01 m2 for each weatherstripped door and 0.02 m2 for each door that is not weatherstripped opening into the stairway.

2)    The stairway is enclosed in a shaft that

a)    does not pass through the floor above the lowest exit level and is separate from a shaft that contains a stairway serving upper storeys, or

b)    contains a stairway serving upper storeys, but is separated from that stairway at the lowest exit level by a fire separation having a fire-resistance rating not less than that required for the shaft enclosure.

3)    The stairway is provided with equipment capable of maintaining a flow of air introduced at or near the bottom of the stair shaft, at a rate equal to 0.47 m3/s for each storey served by the stairway.

A-3.2.6.2.(3)   Pressurization of Stair Shafts. The purpose of providing open doors and vents at the bottom of a stair shaft is to create a positive pressure in the shaft relative to adjacent floor areas and thus keep it free of smoke. The pressure depends on the temperature differential between the interior and the exterior of the building which is most pronounced during winter months when stack effect is greatest. If a shaft does not have a direct opening to the exterior, alternative means must be provided to achieve smoke control. If a corridor or vestibule is used as a link between the exit level of an interior stair shaft and the outdoors to provide a venting system, it will be necessary to assess the reliability of the overall system. The probability of all doors or closures being opened at the same time has to be addressed, as well as the size of the vestibule and its impact on the overall smoke control system.

If mechanical methods are used to develop a positive pressure in a stair shaft, a minimum pressure differential of 12 Pa is recommended to prevent smoke migration from floor areas in a sprinklered building where fire temperatures are controlled and smoke movement may be dominated by stack effect in a stair shaft. During a fire emergency, persons will be entering and exiting a stair shaft as they move to a place of safety and under these conditions the number of doors open to the stair shaft cannot be predetermined. The number will vary depending on the occupancy of the building, population density and the evacuation plan for the building. It should be assumed that two doors are open. This is based in part as a practical level for most buildings and considers the positive fire experience in sprinklered buildings.

The maximum pressure differential created by a mechanical system should not prevent doors to the stair shafts from being opened. A specific maximum value cannot be given, as this value will depend on the door opening force and size of the door. These values should be calculated for each specific case. Although a maximum value of 130 N is suggested by research as the force that can be opened by the majority of people in most occupancies, this value is above the maximum value of 90 N generally specified in this Code. The use of values below 130 N can create a practical problem in achieving effective smoke control as it is difficult to design for the acceptable minimum and maximum pressure differential range. Special consideration may need to be given for doors located in an accessible path of travel.

Care should be taken by designers and by building and fire officials in implementation of these requirements. Assumptions involved in the design of a smoke control system may be different from final construction conditions. For this reason each system should be tested after installation to ensure that the design intent is met. The minimum pressure differential is not intended to apply to locations in stair shafts when doors in their proximity are open to adjacent floor areas.

A-3.2.6.2.(4)   Limiting Smoke Movement.  Measures to prevent the migration of smoke from floor areas below the lowest exit storey into upper storeys include the following.

1)    An elevator hoistway that passes through the floor above the lowest exit storey should not penetrate the floor of the storey immediately below the lowest exit storey, unless there is a vestibule between the shaft and each floor area below the lowest exit storey that

a)    has a fire separation, with a fire-resistance rating not less than 45 min, between the vestibule and any public corridor,

b)    has a fire separation, with a fire-resistance rating not less than that required for an exit by Article 3.4.4.1., between the vestibule and any stair or elevator enclosure or any part of a floor area, other than a public corridor, and

c)    except for elevator hoistway entrances, has a self-closing device on any door through the fire separation required by Clauses (a) and (b), with the door opening in the direction of travel from the floor area to the exit stairway.

Figure A-3.2.6.2.(4)-A

Vent to a vertical service space with no other pressurized shaft in the building

Notes to Figure A-3.2.6.2.(4)-A:

(1) Curve A applies to a vertical service space that is enclosed by unplastered unit masonry or by plaster and steel stud construction with all openings in the shaft sealed to the degree required by Articles 3.1.9.1. to 3.1.9.4.

(2) Curve B applies to a vertical service space that is enclosed by monolithic concrete or by plastered unit masonry with all openings in the shaft sealed tightly to minimize air leakage.

(3) A shaft having a vent that is 100% of the cross-sectional area of the shaft is acceptable for buildings up to 1.5 times the height shown by the appropriate curve in Figures A-3.2.6.2.(4)-A and A-3.2.6.2.(4)-B.

(4) The total leakage area, based on measurements in typical high buildings, is assumed to be 0.025 m2 for every 10 m 2 of shaft wall area in the case of Curve A and 0.015 m2 for every 10 m2 of shaft wall area in the case of Curve B.

2)    A vertical service space, other than an elevator hoistway, that passes through the floor assembly above the lowest exit storey, should be provided with a tight-fitting noncombustible seal or firestop at the floor assembly of the storey immediately below the lowest exit storey, unless

a)    the vertical service space is vented to the outdoors at the top and the vent has an openable area that is not less than

i)   that obtained from Figure A-3.2.6.2.(4)-A if the vertical service space is in a building in which other shafts are not mechanically pressurized, or

ii)   that obtained from Figure A-3.2.6.2.(4)-B if the vertical service space is in a building in which other shafts are mechanically pressurized,

b)    for a shaft that serves floor areas above the lowest exit storey, a vent is located

i)   at or near the top of the shaft if the shaft is above the mid-height of the building, or

ii)   at or near the foot of the shaft at or near the exit level if the top of the shaft is below the mid-height of the building, or

c)    for a shaft that serves floor areas below the lowest exit storey, a vent is located at or near the top of the shaft.

3)    Any closure provided for a vent opening referred to in Sentence (2) must be openable:

a)    manually,

b)    on a signal from a smoke detector located at or near the top of the shaft, and

c)    by a control device located at the central alarm and control facility.

Figure A-3.2.6.2.(4)-B

Vent to a vertical service space with other pressurized shafts in the building

Notes to Figure A-3.2.6.2.(4)-B:

(1) Curve A applies to a vertical service space that is enclosed by unplastered unit masonry or by plaster and steel stud construction with all openings in the shaft sealed to the degree required by Articles 3.1.9.1. to 3.1.9.4.

(2) Curve B applies to a vertical service space that is enclosed by monolithic concrete or by plastered unit masonry with all openings in the shaft sealed tightly to minimize air leakage.

(3) A shaft having a vent that is 100% of the cross-sectional area of the shaft is acceptable for buildings up to 1.5 times the height shown by the appropriate curve in Figures A-3.2.6.2.(4)-A and A-3.2.6.2.(4)-B.

(4) The total leakage area, based on measurements in typical high buildings, is assumed to be 0.025 m2 for every 10 m 2 of shaft wall area in the case of Curve A and 0.015 m2 for every 10 m2 of shaft wall area in the case of Curve B.

A-3.2.6.3.(1)    Connected Buildings. The measures described here are intended to prevent movement of smoke from one building to another. They are of particular significance for two buildings of unequal height that are joined together. The techniques suggested are the provision of a large opening to the outdoors in a connecting vestibule so that smoke entering through leakage areas around doors will be vented to the outdoors, or pressurization to maintain a higher pressure in the vestibule than in adjacent spaces, as illustrated in Figures A-3.2.6.3.(1)-A, A-3.2.6.3.(1)-B and A-3.2.6.3.(1)-C.

The provisions for protection of openings are described in terms appropriate to a doorway. Openings other than doorways should be avoided if possible. Openings should be protected by an airlock that gives the same standard of protection as the vestibule referred to below.

The requirement of Article 3.2.6.3. that limits movement of smoke from one building to another may be met by incorporating in the link between the buildings the provisions of Sentences (1) and (2).

1)    A firewall conforming to Subsection 3.1.10. is constructed between one building and the other with any opening in the firewall protected against the passage of smoke by a vestibule that has

a)    a fire separation between the vestibule and a public corridor with a fire-resistance rating not less than 45 min,

b)    a fire separation between the vestibule and the remainder of the floor area, other than a public corridor, with a fire-resistance rating not less than that required by Article 3.4.4.1. for an exit,

c)    a fire separation between the vestibule and a stair enclosure or elevator hoistway with a fire-resistance rating not less than that required by Article 3.4.4.1. for an exit, and

d)    any door in the fire separation required by Clause (a), (b) or (c), except for an elevator entrance, provided with a self-closing device as required by Article 3.1.8.13. and opening in the direction of travel from the floor area to the exit stairway.

2)    The vestibule referred to in Sentence (1) should have

a)    a vent to the outdoors that has a net area of 10(0.023 d + 0.00045 a) m2, where 'd' is the number of doors having a perimeter not more than 6 m that open into the vestibule, or if the perimeter of doors exceeds 6 m, the value 'd' is increased in direct proportion to the increase in the perimeter, and 'a' is the area in square metres of enclosing walls, floors and ceilings whose outer face is in contact with the outside air, except that where the outer face of a wall is in contact with the ground or fill, it is assumed that there is no leakage through that portion, and the value of 'a' is assumed to be zero, or

b)    equipment capable of maintaining a supply of air into the vestibule sufficient to ensure that the air pressure in the vestibule when the doors are closed is higher by at least 12 Pa than that in adjacent floor areas when the outdoor temperature is equal to the January design temperature on a 2.5% basis.

Figure A-3.2.6.3.(1)-A

Buildings connected by a tunnel

Figure A-3.2.6.3.(1)-B

Buildings connected at a firewall

Figure A-3.2.6.3.(1)-C

Buildings connected by a bridge

A-3.2.6.5.(6)(b)   Protection of Electrical Conductors. Electrical conductors are part of a system that includes, among other components, raceways, conduits, splices, couplings, vertical supports, grounds and pulling lubricants. When selecting electrical conductors to provide a circuit integrity rating, it is important to understand how they will be installed and to know if the fire performance of the system as a whole was tested.

A-3.2.6.6.(1)   Venting to Aid Firefighting. The requirements of Sentence 3.2.6.6.(1) are met by incorporating in a floor area windows or wall panels, as described in Sentence (1), by smoke shafts as described in Sentences (2) to (8), or by the use of building exhaust systems as described in Sentence (9).

1)    If windows or wall panels are used for venting, they must

a)    be uniformly distributed along the exterior wall of each storey,

b)    have a total area not less than 1% of the exterior wall area of each storey,

c)    be readily openable from the interior without the use of wrenches or keys,

d)    be readily identified from the interior, and from the exterior where they are accessible to firefighters, and

e)    be designed so that when opened they will not endanger persons outside the building during a fire.

2)    If one or more smoke shafts or vertical service spaces are used for venting, they must

a)    have an opening or openings into each storey with an aggregate area not less than that obtained from Table A-3.2.6.6.(1)-A for the height of the building and the area of the largest floor area served by the smoke shaft, and the leakage characteristics of the shaft wall and closures obtained from Tables A-3.2.6.6.(1)-B and A-3.2.6.6.(1)-C,

b)    have an aggregate unobstructed cross-sectional area equal to that required by Clause (a), and

c)    be designed to comply with the requirements of Sentence (3).

3)    Each smoke shaft or vertical service space described in Sentence (2) must

a)    be separated from the remainder of the building by a fire separation that has a fire-resistance rating not less than that required for the floor assembly through which it passes, or be designed as a chimney conforming to Part 6, except that flue liners need not be provided,

b)    have an opening to the outdoors at the top that has an area not less than the cross-sectional area of the shaft, with the opening protected from the weather,

c)    terminate not less than 900 mm above the roof surface where it penetrates the roof, and

d)    contain no combustible material, fuel lines or services that are required for use in an emergency.

4)    Each opening required by Clause (2)(a) must be located so that the top of the opening is not more than 250 mm below the ceiling, except that the opening may be above the ceiling if the ceiling freely allows passage of air.

5)    The opening into the smoke shaft must be provided with a closure that

a)    has a fire-protection rating conforming to Sentence 3.1.8.4.(2), except that the temperature on the unexposed face of the closure shall be not more than 250 °C after 30 min during the fire test used to determine its rating,

b)    is no closer to combustible material, except for paint or tightly-adhering paper covering not more than 1 mm thick applied to a noncombustible backing, than the distances described in Table A-3.2.6.6.(1)-D,

c)    can be opened from a remote location such as a stair shaft, the storey immediately below, or the central alarm and control facility, and

d)    does not open automatically on any floor, other than the fire floor, when smoke and hot gases pass through the shaft.

6)    Closures for openings described in Clause (3)(b) must

a)    be openable from outside the shaft, and

b)    open automatically

i)   on a signal from a smoke detector in the shaft,

ii)   by operation of the fire alarm system, and

iii)   when the closure required by Sentence (5) opens.

7)    A smoke shaft opening referred to in Sentence (2) that is less than 1 070 mm above the floor must conform to Article 3.3.1.18.

8)    If a closure is required to comply with Sentence (5), the leakage area between closure components and between closure and frame must not be more than 3% of the openable area of the closure.

9)    The building air handling system may be used for smoke venting, provided

a)    the system can maintain an exhaust to the outdoors at the rate of 6 air changes per hour from any floor area, and

b)    emergency power to the fans providing the exhaust required by Clause (a) is provided as described in Article 3.2.7.9.

Table  A-3.2.6.6.(1)-A

Minimum Size of Vent Openings into Smoke Shafts from Each Floor Area, m2(1)(2)

Forming Part of Note A-3.2.6.6.(1)

| Floor Area, m2 | Leakage Area, %(3) | Building Height, m |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | 18 | 37 | 73 | 110 | 146 | 183 | 220 | 256 | 293 |
| 200 |  | 0.10 | 0.11 | 0.13 | 0.15 | 0.16 | 0.18 | 0.19 | 0.20 | 0.22 |
| 500 |  | 0.22 | 0.25 | 0.29 | 0.32 | 0.36 | 0.37 | 0.39 | 0.41 | 0.43 |
| 1 000 |  | 0.43 | 0.48 | 0.53 | 0.59 | 0.63 | 0.67 | 0.71 | 0.75 | 0.77 |
| 2 000 |  | 0.83 | 0.91 | 1.01 | 1.08 | 1.16 | 1.22 | 1.29 | 1.34 | 1.39 |
| 3 000 | 0 | 1.21 | 1.33 | 1.46 | 1.55 | 1.67 | 1.75 | 1.82 | 1.90 | 1.97 |
| 4 000 |  | 1.62 | 1.75 | 1.90 | 2.02 | 2.15 | 2.25 | 2.35 | 2.44 | 2.53 |
| 5 000 |  | 2.01 | 2.17 | 2.34 | 2.46 | 2.63 | 2.74 | 2.86 | 2.88 | 3.07 |
| 6 000 |  | 2.39 | 2.57 | 2.76 | 2.91 | 3.10 | 3.23 | 3.37 | 3.47 | 3.58 |
| 200 |  | 0.10 | 0.12 | 0.15 | 0.19 | 0.22 | 0.27 | 0.35 | 0.43 | 0.55 |
| 500 |  | 0.23 | 0.27 | 0.35 | 0.40 | 0.49 | 0.57 | 0.69 | 0.83 | 1.04 |
| 1 000 |  | 0.44 | 0.50 | 0.71 | 0.72 | 0.86 | 1.01 | 1.19 | 1.43 | 1.73 |
| 2 000 |  | 0.85 | 0.97 | 1.15 | 1.33 | 1.56 | 1.81 | 2.10 | 2.48 | 2.95 |
| 3 000 | 1 | 1.26 | 1.42 | 1.67 | 1.91 | 2.23 | 2.56 | 2.97 | 3.47 | 4.08 |
| 4 000 |  | 1.66 | 1.88 | 2.18 | 2.49 | 2.37 | 3.28 | 3.79 | 4.40 | 5.16 |
| 5 000 |  | 2.07 | 2.32 | 2.69 | 3.05 | 3.51 | 3.99 | 4.60 | 5.32 | 6.21 |
| 6 000 |  | 2.47 | 2.76 | 3.18 | 3.59 | 4.14 | 4.68 | 5.37 | 6.20 | 7.23 |
| 200 |  | 0.10 | 0.13 | 0.18 | 0.24 | 0.37 | 0.61 | 1.28 | 4.60 | 89.57 |
| 500 |  | 0.24 | 0.29 | 0.39 | 0.52 | 0.75 | 1.13 | 2.10 | 6.11 | 94.50 |
| 1 000 |  | 0.46 | 0.55 | 0.72 | 0.94 | 1.30 | 1.90 | 3.27 | 8.29 | 102.11 |
| 2 000 |  | 0.88 | 1.05 | 1.34 | 1.73 | 2.32 | 3.28 | 5.36 | 12.14 | 116.80 |
| 3 000 | 2 | 1.31 | 1.53 | 1.95 | 2.47 | 3.29 | 4.58 | 7.28 | 15.63 | 130.83 |
| 4 000 |  | 1.73 | 2.01 | 2.55 | 3.20 | 4.23 | 5.83 | 9.12 | 19.97 | 144.03 |
| 5 000 |  | 2.15 | 2.49 | 3.13 | 3.92 | 5.15 | 7.05 | 10.90 | 22.15 | 157.05 |
| 6 000 |  | 2.57 | 2.96 | 3.73 | 4.63 | 6.07 | 8.26 | 12.65 | 25.39 | 169.29 |
| 200 |  | 0.11 | 0.14 | 0.21 | 0.37 | 0.88 | 2.06 |  |  |  |
| 500 |  | 0.25 | 0.31 | 0.47 | 0.76 | 1.58 | 9.00 |  |  |  |
| 1 000 |  | 0.47 | 0.59 | 0.86 | 1.33 | 2.60 | 11.99 |  |  |  |
| 2 000 |  | 0.91 | 1.12 | 1.60 | 2.41 | 4.47 | 17.46 |  |  |  |
| 3 000 | 3 | 1.35 | 1.64 | 2.31 | 3.43 | 5.21 | 22.48 |  |  |  |
| 4 000 |  | 1.79 | 2.17 | 3.02 | 4.43 | 7.91 | 27.29 |  |  |  |
| 5 000 |  | 2.22 | 2.68 | 3.71 | 5.42 | 9.55 | 31.95 |  |  |  |
| 6 000 |  | 2.65 | 3.20 | 4.40 | 6.39 | 11.18 | 36.47 |  |  |  |
| 200 |  | 0.11 | 0.15 | 0.28 | 0.70 | 24.83 |  |  |  |  |
| 500 |  | 0.25 | 0.34 | 0.58 | 1.33 | 29.18 |  |  |  |  |
| 1 000 |  | 0.49 | 0.63 | 1.06 | 2.27 | 36.07 |  |  |  |  |
| 2 000 |  | 0.95 | 1.21 | 1.97 | 3.99 | 48.56 |  |  |  |  |
| 3 000 | 4 | 1.41 | 1.78 | 2.84 | 6.63 | 60.15 |  |  |  |  |
| 4 000 |  | 1.86 | 2.34 | 3.70 | 7.22 | 71.15 |  |  |  |  |
| 5 000 |  | 2.21 | 2.90 | 4.55 | 8.79 | 81.81 |  |  |  |  |
| 6 000 |  | 2.75 | 3.46 | 5.40 | 10.33 | 90.05 |  |  |  |  |
| 200 |  | 0.11 | 0.16 | 0.36 | 3.33 |  |  |  |  |  |
| 500 |  | 0.28 | 0.36 | 0.76 | 5.09 |  |  |  |  |  |
| 1 000 |  | 0.50 | 0.69 | 1.37 | 7.67 |  |  |  |  |  |
| 2 000 |  | 0.99 | 1.31 | 2.54 | 12.35 |  |  |  |  |  |
| 3 000 | 5 | 1.46 | 1.94 | 3.65 | 16.75 |  |  |  |  |  |
| 4 000 |  | 1.92 | 2.55 | 4.75 | 20.99 |  |  |  |  |  |
| 5 000 |  | 2.40 | 3.16 | 5.84 | 25.11 |  |  |  |  |  |
| 6 000 |  | 2.87 | 3.74 | 6.92 | 29.11 |  |  |  |  |  |

Notes to Table A-3.2.6.6.(1)-A:

(1) The minimum size of a vent opening into a smoke shaft is obtained from Table A-3.2.6.6.(1)-A and is dependant on the floor area and total leakage area of the smoke shaft walls and closures. This total leakage area may be estimated by adding the leakage areas for the shaft wall obtained from Table A-3.2.6.6.(1)-B and for the dampered openings obtained from Table A-3.2.6.6.(1)-C, provided the cross-sectional area of the smoke shaft, the opening into the shaft and the opening to the outdoors at the top of the shaft are equal.

(2) The size of the vent opening refers to the free or unobstructed area of the opening.

(3) Leakage area is the total of the leakage area of smoke shaft wall obtained from Table A-3.2.6.6.(1)-B and the leakage area of openings in smoke shafts obtained from Table A-3.2.6.6.(1)-C.

Table  A-3.2.6.6.(1)-B

Leakage Area of Smoke Shaft Wall

Forming Part of Note A-3.2.6.6.(1)

| Wall Construction | Leakage Area as % of Wall Area |
| --- | --- |
| Monolithic concrete | 0.5 |
| Masonry wall unplastered | 1.5 |
| Masonry wall plastered | 0.5 |
| Gypsum board on steel studs | 1.0 |

Table  A-3.2.6.6.(1)-C

Leakage Area of Closures in Openings into Smoke Shaft

Forming Part of Note A-3.2.6.6.(1)

| Type of Closure | Leakage Area as % of Closure Area(1)(2) |
| --- | --- |
| Curtain fire damper | 2.5 |
| Single-blade fire damper | 3.5 |
| Multi-blade fire damper | 4.5 |

Notes to Table A-3.2.6.6.(1)-C:

(1) Values include allowance for 0.5% leakage between frame and wall construction.

(2) These leakage data are based on clearances applicable to closures that have been tested in accordance with CAN/ULC-S112, “Standard Method of Fire Test of Fire Damper Assemblies.”

Table  A-3.2.6.6.(1)-D

Minimum Distance from Closure to Combustible Material

Forming Part of Note A-3.2.6.6.(1)

| Area of Closure(1), m2 | Minimum Distance in Front of or Above Closure, m | Minimum Distance to the Sides or Below Closure, m |
| --- | --- | --- |
| 0.5 | 0.35 | 0.20 |
| 1.0 | 0.50 | 0.25 |
| 1.5 | 0.60 | 0.30 |
| 2.0 | 0.70 | 0.35 |
| 2.5(2) | 0.80 | 0.40 |

Notes to Table A-3.2.6.6.(1)-D:

(1) For closure areas between those given in Table A-3.2.6.6.(1)-D, interpolation may be used to determine the appropriate distances.

(2) For closure areas greater than 2.5  m2, the minimum distance in front of or above the closure shall be one half of the square root of the closure area, and the minimum distance to the sides or below the closure shall be one quarter of the square root of the closure area.

A-3.2.6.7.(1)   Protection of Central Control Room. The design of a room provided for a central alarm and control facility should take into account the nature and sensitivity of the electronic components of the equipment and the room should be adequately protected from fire and smoke. The room should be ventilated with a supply of fresh air so that it has a clean environment and should be provided with adequate lighting.

A-3.2.6.7.(2)   Central Control Room Air Control. Depending on the method of mechanical venting and air control that is selected for the building, additional controls may be required at the central alarm and control facility. These additional controls include those with a capability of opening closures to vents in shafts, stopping air-handling systems, and initiating mechanical air supply to stair shafts.

A-3.2.6.9.(1)   Testing for Smoke Control.  The efficiency of a smoke control system may be checked by measuring pressure differences and the directions of airflow around doors and through separating walls of compartments. A pressure meter can be used to measure pressure differences on either side of a door or partition. Where this is impracticable, a punk stick held near a crack will indicate the direction of airflow. Measurements of airflow may be taken on the intake side of supply fans or in supply ducts to determine whether the specified airflow is being provided. In general, airflow should be from the spaces which may be occupied for various lengths of time during a fire emergency (e.g., vestibules, stair shafts, and elevator hoistways) toward the space in which the fire is assumed to have occurred. Measurements may be taken at certain critical locations to check the overall efficiency of the smoke control system.

In buildings where protection is obtained by venting corridors or vestibules to the outdoors, inspection of the building to determine whether the requirements have been met should be sufficient. Where service shafts are vented to the outdoors at the top, a check may be made of the wall between the shaft and the uppermost occupied floor areas, to ensure that the direction of flow is from each floor area into the shaft, when the vent to the outside is open and the outdoor air temperature is significantly less than that indoors. Where mechanically pressurized vestibules are used, a check may be made to ensure that the pressure in each vestibule or area of refuge is greater than that in the adjacent floor areas at each floor level.

Doors to stair shafts, elevator hoistways and vestibules in locations subject to pressure differences that may interfere with normal opening should be checked when the outdoor temperature is near the January design temperature, with the air injection system operating and a number of windows open to the outdoors on each floor in turn.

A-3.2.7.4.(1)   Emergency Power Reliability.  In some areas power outages are frequent and may be of long duration. These local conditions should be taken into account in determining the type of system for supplying emergency power for lighting. This should be studied at the planning stage of a building project in conjunction with the local fire safety and building officials.

A-3.2.7.6.(1)   Emergency Power for Treatment Occupancies. CSA Z32, “Electrical safety and essential electrical systems in health care facilities,” contains requirements for three classes of health care facilities—Class A, Class B and Class C. The intent of Article 3.2.7.6. is to apply specific requirements to emergency equipment for Class A facilities, which are designated as hospitals by the authorities having jurisdiction and where patients are accommodated on the basis of medical need and are provided with continuing medical care and supporting diagnostic and therapeutic services.

A-3.2.7.8.(3)   Emergency Power Duration.  The times indicated in this Sentence are the durations for which emergency power must be available for a building under fire emergency conditions. Additional fuel for generators or additional battery capacity is required to handle normal testing of the equipment, as indicated in the NFC. If the operation of emergency generators or batteries is intended for other than fire emergency conditions, such as power failures, fuel supplies or battery capacity must be increased to compensate for that use.

A-3.2.7.9.(1)   Emergency Power Reliability.  In some areas power outages are frequent and may be of long duration. These local conditions should be taken into account in determining the type of system for supplying emergency power for building services. This should be studied at the planning stage of a building project in conjunction with the local fire safety and building officials.

A-3.2.7.10.(2)(a) and (3)(a)   Protection of Electrical Conductors. It is important to understand that electrical conductors are part of a system that includes—among other components—raceways, conduits, splices, couplings, vertical supports, grounds and pulling lubricants. When selecting electrical conductors to provide a circuit integrity rating, it is therefore important to understand how they will be installed and to know if the fire performance of the system as a whole was tested.

A-3.2.7.10.(5)(b)   Electrical Conductors in the Same Room. If the distribution panel and the equipment it serves are within the same room, only the electrical conductors leading up to the distribution panel need to be protected. It is assumed that the distribution panel and the equipment it serves are within sufficient proximity to each other such that a fire in the same area of origin would affect both.

A-3.2.7.10.(7)   Fire Alarm Branch Circuits. In order to ensure continuous operation of the fire alarm and voice communication systems in a high-rise building for a sufficient duration of time to control and direct the evacuation of building occupants, a level of protection is required by Sentence 3.2.7.10.(2) for those electrical conductors interconnecting the major elements of the fire alarm system. Sentence 3.2.7.10.(7) permits the protection of electrical conductors to be waived for portions connecting a transponder or fault isolation device to fire alarm input devices (fire detectors, manual stations, etc.) or a voice communication transponder to a fire alarm audible signalling device, provided all circuits or portions of the circuits are contained within the same storey.

A-3.2.8.2.(3)   Special Protection of Opening. In manufacturing operations involving the use of conveyor systems to transport material through fire separations, it may not be possible to use standard closure devices. NFPA 80, “Standard for Fire Doors and Other Opening Protectives,” includes appendix information concerning protection of openings through vertical fire separations. NFPA 13, “Standard for the Installation of Sprinkler Systems,” includes methods of protecting openings through floor assemblies, however, it is assumed by that standard that the remainder of the building would be sprinklered. Combinations of methods may be required to ensure that the level of safety inherent in the requirements of the Code is maintained.

A-3.2.8.2.(6)(b)   Restriction on Size of Openings Through Floors. The phrase “used only for stairways, escalators or moving walks” is intended to restrict the size of a floor opening to what is necessary to accommodate the stairway, escalator or moving walk.

A-3.2.8.2.(6)(c)   Waiver of Occupancy Separation Continuity. The typical application of this Sentence is to buildings with a mixture of occupancies that are randomly located throughout the building. Examples include shopping centres, podia of large commercial and business complexes, and recreational buildings that are combined with mercantile and business operations. A shopping mall with two interconnected storeys is an example that is frequently encountered in many jurisdictions. The permission to breach the floor assembly between the storeys does not override requirements for separation of specific suites or occupancies. For instance, although storage garages are Group F, Division 3 occupancies, the requirement in Article 3.3.5.6. for the storage garage to be separated from other occupancies by a fire separation with at least a 1.5 h fire-resistance rating must be observed. In a similar manner, a theatre or cinema (Group A, Division 1 occupancy) must be separated from other occupancies in accordance with Sentence 3.3.2.2.(1) and seats in an arena-type building (Group A, Division 3) must be separated from space below in accordance with Sentence 3.3.2.2.(3).

A-3.2.8.4.(1)(c)   Contamination of Vestibule. The vestibule should have equipment capable of maintaining a supply of air into the vestibule that is sufficient to ensure that the air pressure in the vestibule when the doors are closed is higher by at least 12 Pa than the air pressure in the adjacent floor areas when the outdoor temperature is equal to the January design temperature on a 2.5% basis.

A-3.2.8.7.(1)   Smoke Exhaust System. The mechanical exhaust system is intended as an aid to firefighters in removing smoke and is to be designed to be actuated manually by the responding fire department. Although smoke is normally removed from the top of the interconnected floor space, exhaust outlets at other locations may be satisfactory.

A-3.2.9.1.(1)   Testing of Fire Protection and Life Safety Systems. Building owners should verify that fire protection and life safety systems and their components (i.e. fire alarm systems, sprinklers, standpipes, smoke control, ventilation, pressurization, door hold-open devices, elevator recalls, smoke and fire shutters and dampers, emergency power, emergency lighting, fire pumps, generators, etc.), including their interconnections with other building systems, are functioning according to the intent of their design. CAN/ULC-S1001, “Standard for Integrated Systems Testing of Fire Protection and Life Safety Systems,” provides the methodology for verifying and documenting that interconnections between building systems satisfy the intent of their design and that the systems function as intended by the Code.

Clause 6.1.5 of CAN/ULC-S1001 allows the Integrated Testing Coordinator to accept documented evidence of any tests that have been performed on a system as part of its acceptance testing for the purpose of demonstrating compliance with the integrated testing requirements of that standard, so as to avoid duplication of work.

A-3.3.   Safety Within Floor Areas. Section 3.3. regulates safety within floor areas including rooms and other spaces within a building. The requirements are grouped according to the occupancy of the floor area, room or space, which is not necessarily the same as the major occupancy for which the building is classified. For example, a building may be classified by major occupancy as an office building: therefore, the provisions for structural fire protection and fire protection equipment for office buildings prescribed in Section 3.2. apply. However, within that building, a room or floor area may be used for mercantile, care, treatment, detention, business, residential, industrial or other occupancy.

Life safety for the occupants of any floor area depends in the first instance on the use or occupancy of that floor area. The risks to the occupants occur in the early stages of a fire. These special life risks differ from one occupancy to another and, consequently, must be regulated differently. Section 3.3. regulates risks within floor areas: these requirements apply regardless of the major occupancy of the building that contains the floor areas. For example, an assembly room must comply with the requirements for assembly occupancy whether it is contained in an office building, hospital, hotel, theatre, industrial building or other major occupancy.

Since this Code regulates new construction, alterations and changes of occupancy, the construction of kiosks and similar structures in public corridors must take into consideration all the requirements that apply to the remainder of the building, including structural fire protection, construction type, finish materials, egress widths and sprinkler installations. Special activities of an occasional nature that were not contemplated in the original design of a public corridor and that represent only a temporary change in occupancy are regulated by the NFC. These regulations include maintaining egress paths clear of obstructions, controlling combustible contents and providing measures to ensure quick response for firefighting.

A-3.3.1.2.(1)   Hazardous Substances. The term “hazardous substances” refers to dangerous goods that are regulated by “Transportation of Dangerous Goods Regulations (TDGR)” or that are classified as “controlled products” under the “Workplace Hazardous Materials Information System (WHMIS)” established to meet the requirements of HC SOR/2015-17, “Hazardous Products Regulations.” It also refers to materials and products that are not regulated by the TDGR or WHMIS, but that pose a fire or explosion hazard due to their own properties or because of the manner in which they are stored, handled or used. These include combustible products, rubber tires, combustible fibres, combustible dusts, products producing flammable vapours or gases, etc.

A-3.3.1.2.(2)   Cooking Equipment Ventilation. Cooking equipment manufactured for use in dwelling units and other residential suites is often installed in buildings used for assembly and care, treatment or detention purposes. It is not obvious from the Code requirements or those of NFPA 96, “Standard for Ventilation Control and Fire Protection of Commercial Cooking Operations,” whether a ventilation and grease removal system is required in all assembly and care, treatment or detention uses. If the equipment is to be used in a manner that will produce grease-laden vapours that are substantially more than would be produced in a normal household environment, then it would be appropriate to apply the requirements of NFPA 96. If the equipment is used primarily for reheating food prepared elsewhere or is used occasionally for demonstration or educational purposes, there would be no expectation of applying the requirements of NFPA 96. In all cases the circumstances should be reviewed with the authority having jurisdiction.

A-3.3.1.3   Means of Egress Serving Podiums and Terraces.  The requirements for podiums and terraces in Sentence 3.3.1.3.(2) and (3) are intended for areas situated on a level that is not at the highest elevation in a building, and where the area can be accessed by a storey of the building. The requirements of Sentence 3.3.1.3.(4) to (9) are intended for roof-top areas, including “terraces” where the area is at the highest elevation of the building, and there is no access to a storey of the building at that level.

A-3.3.1.7.(1)   Temporary Refuge for Persons with Disabilities. These measures are intended to provide temporary refuge for persons with disabilities. It is acknowledged, however, that the measures cannot provide absolute safety for all occupants in the fire area. It may, therefore, be necessary to develop special arrangements in the fire safety plan to evacuate persons with disabilities from these areas. Details for a suitable plan are contained in the British Columbia Fire Code.

The protected elevator referred to in Clause 3.3.1.7.(1)(a) is intended to be used by firefighters as a means for evacuating persons with disabilities. It is not intended that this elevator be used by persons with disabilities as a means of egress without the assistance of firefighters.

If an estimate is to be made of the number of persons with disabilities in a floor area who can be accommodated in each zone in Clause 3.3.1.7.(1)(b), this estimate may be based on Table 3.8.2.3., which is used to determine the minimum number of spaces to be provided for persons using wheelchairs in fixed seating areas. If more precise information is available, it should be used for sizing the zones.

For residential occupancies, the choice of protection include the option to provide an accessible balcony, but it is not required that balconies be the chosen means of protection.

A-3.3.1.8.(2) and (3)   Protruding Building Elements in Paths of Travel. The term “protruding building elements” refers to elements regulated by this Code that are permanently affixed to the building and protrude into the path of travel.

The sweep of a cane normally detects protruding building elements that are within 680 mm of the floor. Any protruding element above this height would not normally be detected and can, therefore, create a hazard if it projects more than 100 mm into the path of travel.

A-3.3.1.12.(3)   Movable Partitions. Should an emergency situation arise outside of normal working hours but when occupants are still in the space, they could be left without a clear way out. This could occur during inventory or after closing time when all occupants have not yet left, but staff close the door to prevent other persons from entering. In many small tenant areas, the movable partitions (store fronts) provide the only way out. There should always be a second way out or a swinging door within or adjacent to the sliding partitions.

A-3.3.1.13.(4)   Door Hardware. The permission to have additional door releasing devices is intended to allow the use of a security chain, night latch or dead bolt to supplement the normal door latching device. These are permitted for dwelling units and locations where guests in a hotel or motel require additional security. The height of these items is also governed by the maximum height stipulated in Sentence 3.3.1.13.(5) to ensure that they can be operated by persons with physical disabilities. This additional hardware should not require appreciable dexterity by the user and the general requirements on the ability to operate the device without the use of keys, special tools or specialized knowledge still apply.

A-3.3.1.13.(6)   Controlled Egress Doors.  It is intended that Sentence 3.3.1.13.(6) apply to doors used at the perimeter of a contained use area or an impeded egress zone. If the contained use area consists of a single room, the requirements would apply to that room. In the case of individual cells within a contained use area, exterior keyed locks could be used on the cell doors consistent with the fire safety plan and continuous supervision by staff who can release the doors in an emergency.

A-3.3.1.19.(1)   Tactile Attention Indicators at Unenclosed Stairs and at Drop-off Edges. Stairs in open spaces, stairs from mezzanines, and stairs that are not separated from the floor area by an element, such as a door or gate, are examples of stairs that are unenclosed. Transit platforms and the edges of a reflecting pool are examples of locations with drop-off edges where tactile attention indicators should be installed.

A-3.3.1.24.(1)   Obstructions in Means of Egress. Obstructions including posts, counters or turnstiles should not be located in a manner that would restrict the width of a normal means of egress from a floor area or part of a floor area unless an alternative means of egress is provided adjacent to and plainly visible from the restricted means of egress.

A-3.3.2.1.(2)   Use of NFPA 101. The intention of Sentence (2) is to allow Code users the option of using NFPA 101, “Life Safety Code,” to address the following issues: means of egress; egress routes within assembly occupancies; aisles and access serving seating not at tables; guards and railings; life safety evaluation; and smoke-protected assembly seating. However, opting to use NFPA 101 under this application entails adherence to all the provisions listed in Sentence (2): it is not intended that Code users randomly select and apply a mix of provisions from both the British Columbia Building Code and the NFPA.

A-3.3.2.4.(2)   Tablet Arms. Although it is intended that the motion to raise the tablet arm be essentially a single fluid motion, it is acceptable that the motion be a compound motion of raising the tablet arm and including an articulation to allow the tablet to fall back alongside the arm rest.

A-3.3.2.10.   Installation Configurations of Handrails in Aisles with Steps. Figure A-3.3.2.10. illustrates possible installation configurations of handrails serving aisles with steps.

Figure A-3.3.2.10.

Handrail installation configurations

A-3.3.2.18.   Daycare Facilities for Children under 30 Months. These daycare facilities are subject to additional requirements to address the unique profile of the occupants. The Community Care and Assisted Living Act and pursuant regulations establish care programs and prescribes the ages for children in those various programs. The Code’s requirements for daycare facilities for children under 30 months is intended to coordinate with those care programs, which inform the intended use and applicable Code requirements, but the Code does not regulate the actual ages of children in those care programs or in the facility (See Note A-3.1.2.8.)

A-3.3.3.1.(1)   Safety in Care, Treatment and Detention Occupancies. Fire safety for patients in bedroom areas in hospitals and nursing homes with treatment is predicated on the ability of staff to carry out at all times essential life safety functions in accordance with the fire safety plan. Details for a plan are contained in the British Columbia Fire Code.

Many factors may affect the ability of staff to carry out life safety functions, including the mobility of patients who cannot fend for themselves and the built-in protection for patients who cannot be moved except under exceptional circumstances.

Should a patient area in a hospital or nursing home with treatment contain factors which would increase the time normally required for staff to evacuate patients or to undertake other life safety measures, consideration should be given to providing additional fire protection measures to ensure that equivalent safety is available.

A-3.3.3.4.(2)   Doorway Width. The 1 050 mm minimum clear width of doorways accounts for door stops and, thus, is intended to allow for the use of 1 100 mm doors.

A-3.3.3.5.(9)   Intercommunicating Rooms. Rooms that are interconnected can include more than one sleeping room, together with ensuite toilet rooms, shower rooms, and storage closets used for the storage of personal items of the persons occupying the sleeping rooms. It is not intended that storage rooms for other purposes be included within the group of interconnected rooms.

A-3.3.3.5.(13)   Grilles and Louvres. In order to permit the supply of make-up air to compensate for the removal of exhaust air from these toilet rooms, shower rooms and similar spaces, it is permitted to incorporate grilles and louvres for the transfer of air provided the air movement cannot allow smoke to pass through these spaces to other parts of the building. It is considered that in normal designs the air is exhausted directly to the exterior and is not circulated. If air is to be circulated back to other parts of the building, smoke operated dampers should be included in the air circulating system.

A-3.3.4.4.(1)   Landing in Egress Stairway.  A landing level used in an egress stairway from a dwelling unit is not considered to be a storey of that dwelling unit if the landing is used only for pedestrian travel purposes.

A-3.3.4.5.(1)   Automatic Locking Prohibited. Doors that must be manually reset to lock them when they are opened from the inside meet the intent of this requirement.

A-3.3.6.1.(1)   Design of Buildings Containing Dangerous Goods. Subsection 3.3.6. applies to the short- or long-term storage of products, whether raw or waste materials, goods in process, or finished goods.

This Subsection does not deal with products or materials that are directly supplied to appliances, equipment or apparatus through piping, hose, ducts, etc. For example, the gas cylinders that are mounted on propane barbecues are not covered by Subsection 3.3.6.; they are considered to be “in use” as opposed to “in storage” and are not intended to be regulated by the storage requirements stated in the British Columbia Fire Code.

A-3.3.6.2.(2)   Storage of Reactive Materials. Reactive materials include various classes of unstable or reactive dangerous goods, such as flammable solids, pyrophoric materials, oxidizers, corrosives, water-reactive substances and organic peroxides.

In general, it is unsafe to store highly reactive oxidizers close to liquids with low flash points, combustible products or chemically incompatible products. Quantities of oxidizers or other dangerously reactive materials should therefore be limited and the storage area should be constructed of noncombustible materials, should be kept cool and ventilated, and should not impede egress.

In some cases, depending on the quantity and nature of the oxidizing agent, normal fire protection measures (e.g. sprinklers, fire hose and extinguishers) are ineffective due to the self-yielding of oxygen by the oxidizing agent.

When containers of highly reactive oxidizers become damaged or are exposed to excessive heat, humidity or contamination (e.g. sawdust, petroleum products, or other chemicals), a very violent fire or explosion can result.

The following oxidizing substances, among others, are known to supply oxygen: organic and inorganic peroxides; pool chemicals (e.g. calcium hypochlorite, sodium dichloroisocyanurate); oxides; permanganates; perrhenates; chlorates; perchlorates; persulfates; organic and inorganic nitrates; bromates; iodates; periodates; perselenates; chromates, dichromates; ozone; perborates.

When containers of dangerously reactive materials become damaged or are exposed to water or humidity, a flammable gas (such as hydrogen, ammonia or methane) or a toxic gas (such as hydrogen chloride, hydrogen bromide or phosphine) can be released.

The following dangerously reactive materials, among others, are known to release a flammable gas in reaction to contact with water or humidity: alkali metals (e.g. sodium, potassium, cesium); reactive metals (e.g. zinc, aluminum, magnesium); metallic hydride (e.g. sodium borohydride, germanium tetrahydride, calcium hydride).

The following dangerously reactive materials, among others, are known to release a toxic gas in reaction to contact with water or humidity: organic and inorganic chloride (e.g. phosphorus trichloride, phosphorus oxide trichloride, acetyl chloride); organic and inorganic bromide (e.g. phosphorus tribromide, aluminum tribromide, acetyl bromide).

A-3.3.6.2.(4)   Wiring and Electrical Equipment in Hazardous Locations. In addition to the general requirements of CSA C22.1, “Canadian Electrical Code, Part I,” special attention must be given to Sections 18, 20 and 22: Section 18 specifies wiring requirements for Class I, II and III hazardous locations; Section 20 provides specific requirements for areas where flammable or combustible liquids are stored or dispensed; Section 22 specifies wiring requirements for areas where corrosive liquids or vapours or excessive moisture are present.

A-3.3.6.4.(2)   Explosion Venting in Hazardous Locations. When a flammable mixture of air and vapour/gas/dust is ignited and causes an explosion, the exothermic reaction results in the rapid expansion of heated gases and the corresponding pressure waves travel through the mixture at sonic or supersonic velocities. The pressures developed by an explosion very rapidly reach levels that most buildings and equipment cannot withstand unless specifically designed to do so. Explosion venting consists of devices designed to open at a predetermined pressure to relieve internal pressure build-up inside a room or enclosure, hence limiting the structural and mechanical damage.

The major parameters to be considered in designing an explosion venting system for a building are:

•   the physical and chemical properties of the flammable air mixture, such as the particle size or the droplet diameter, the moisture content, the minimum ignition temperature and explosive concentration, the burning velocity or explosibility classification, the maximum explosion pressure and the rate of pressure rise,

•   the concentration and dispersion of the flammable mixture in the room,

•   the turbulence and physical obstructions in the room,

•   the size and shape of the room, the type of construction and its ability to withstand internal pressures, and

•   the type, size and location of relief panels, which should also be designed to reduce the possibility of injury to people in the immediate vicinity of the panels.

A-3.3.6.5.(1)   Measurement of Tire Storage Volume. The volume of tires in a storage area can be determined by measuring to the nearest 0.1 m the length, width and height of the piles or racks intended to contain the tires. In racks, the top shelf is assumed to be loaded to maximum possible height, while observing required clearances between structural elements and sprinklers.

A-3.3.6.6.(6)   Products Stored with Ammonium Nitrate. Copper and its alloys should not be used where they can come into contact with ammonium nitrate. The presence of copper represents the single biggest hazard with respect to the accidental detonation of ammonium nitrate during a fire.

Steel and wood can be protected with special coatings such as sodium silicate, epoxy, or polyvinyl chloride.

Asphalt and similar hydrocarbon-based roof coverings should not be used. Stored ammonium nitrate may become sensitized during a fire if such roof coverings melt and leak into the interior of the building, causing burning droplets to fall on the stored product.

A-3.4.1.1.(1)   Type of Exit Facility. The requirements for exits in Section 3.4. were developed for new construction. If alterations are made to an existing building or changes of occupancy occur, other design solutions than those in Section 3.4. may have to be developed to maintain an acceptable level of safety if it is not practicable to fully conform to the requirements of this Section. In some cases the use of fire escapes to supplement the existing exit facilities may be the only practicable solution. Because of the variety of conditions that may be encountered in existing buildings, it is difficult to standardize or codify such requirements. Alternative means of providing acceptable levels of safety may have to be tailored to the particular building design. In all cases, however, the requirements described in Section 3.4. are intended to provide the level of safety to be achieved. If alternative measures are used, they should develop the level of safety implied in these requirements.

A-3.4.1.6.(2)   Sleeping Area. Areas serving patients' sleeping rooms include sleeping areas and areas where patients are taken for treatment.

A-3.4.2.3.(1)   Least Distance Between Exits. The least distance measurement does not apply to each combination of exits on a multi-exit storey. It only applies to at least 2 of the required exits from that storey.

A-3.4.3.2.(6)   Evacuation of Interconnected Floor Space. This Sentence ensures that egress facilities allow for the simultaneous evacuation of all portions of an interconnected floor space. It does not contemplate the phased evacuation of occupants; thus in buildings where that type of evacuation is intended, fire protection requirements in addition to those prescribed in the Code may be necessary.

In the first instance, this Sentence provides for cumulative exiting that can accommodate the efficient movement of all occupants in the exit stairs. Clause 3.4.3.2.(6)(a) permits an alternative approach that will accommodate all the occupants in the stairs but will restrict the egress flow rate. Clause 3.4.3.2.(6)(b) provides a second alternative that assumes the occupants must queue before entering the stair. A “protected floor space” conforming to Article 3.2.8.5. is intended to provide an intermediate area of safety that is protected from the hazards of the interconnected floor space. It does not provide a holding or refuge area for all occupants of a floor area for an extended period of time.

To ensure that evacuation is not unduly delayed and that queuing of the occupants in the protected floor space can be accommodated, requires careful consideration in the design of the interface between the interconnected floor space/protected floor space/exit.

It is not appropriate, for example, to share a common vestibule in complying with Sentences 3.2.8.4.(1) and 3.2.8.5.(1). Under evacuation conditions, occupants entering the vestibule would flow towards the exit, as opposed to the protected floor space, thus resulting in queuing outside the vestibule and potential exposure to fire. To comply with the intent, it is necessary to design the egress path such that the occupants enter the protected floor space through a vestibule, then in turn enter the exit stair from the protected floor space. In addition, sufficient space should be provided between the vestibule and the exit to allow for the queuing of occupants in the protected floor space.

A-3.4.3.2.(6)(a)   Temporary Safety Area.  The objective of Clause 3.4.3.2.(6)(a) is to provide an area of temporary safety in the exit stair shafts for the occupants of the interconnected floor space. This requirement is considered to be met if 0.3 m2 per person is provided in the stair shaft between the floor level served and the floor level immediately beneath it.

A-3.4.3.4.   Clear Height and Width. Clear height is intended to be measured from a line tangent to the nosings extended to the underside of the lowest element above the walking surface, over the clear width of the exit (see Figure A-3.4.3.4.). Examples of low elements above the walking surface include light fixtures or sprinkler heads and piping.

Clear width is intended to be measured from a line tangent to horizontal protrusions such as handrails.

Figure A-3.4.3.4.

Measuring clear height

A-3.4.4.2.(2)(e)   Requirements for Lobby.  If an exit is permitted to lead through a lobby, the lobby must provide a level of protection approaching that of the exit. As well as meeting the width and height requirements for exits, the lobby must be separated from the remainder of the building by a fire separation having a fire-resistance rating at least equal to that required for the exit, unless one of the exceptions in this Clause is applied.

A-3.4.5.1.(2)(c)   Graphical Symbols for Exit Signs. ISO 7010, “Graphical symbols – Safety colours and safety signs – Registered safety signs,” identifies the following internationally recognized symbols for use at required exits.

Figure A-3.4.5.1.(2)(c)-A

“E001 Emergency exit (left hand)” symbol from ISO 7010

Figure A-3.4.5.1.(2)(c)-B

“E005 Direction, arrow (90º increments), safe condition” symbol from ISO 7010

A-3.4.5.1.(3)   Internally Illuminated Signs. Photoluminescent signs are not internally illuminated and therefore must conform to Sentence 3.4.5.1.(4).

A-3.4.5.1.(4)   Externally Illuminated Signs. An external lighting source is required to properly charge photoluminescent signs. In addition to being continuously illuminated as required by Sentence 3.4.5.1.(4), these types of signs must be lit in conformance with the charging requirements indicated on the exit signs in accordance with CAN/ULC-S572, “Standard for Photoluminescent and Self-Luminous Exit Signs and Path Marking Systems.”

A-3.4.6.   Application to Means of Egress. The requirements in Subsection 3.4.6. apply to interior and exterior exits, as well as to ramps, stairways and passageways used by the public as access to exit. The treads, risers, landings, handrails and guards for the latter access to exit facilities must thus be provided in conformance with the appropriate requirements for exit facilities.

A-3.4.6.4.   Dimensions of Landings. A landing is a floor area provided at the top or bottom of a flight of stairs or a ramp, or a platform built as part of a stairway or ramp. Landings provide a safe surface for users to rest upon, allow design flexibility, and facilitate a change in direction.

Figure A-3.4.6.4. illustrates how to measure the length of a landing for various landing configurations turning less than 90°, including straight landings.

Figure A-3.4.6.4.

Landing configurations

Notes to Figure A-3.4.6.4.:

(1)

L1 + L2   = length of the landing

= the lesser of the required width of the stair or ramp, or 1 100 mm

See Sentences 3.4.6.4.(2) and 9.8.6.3.(2).

(2)

D   = distance from the narrow edge where the length of the landing is measured

= half the required length of the landing

See Sentences 3.4.6.4.(3) and 9.8.6.3.(3).

A-3.4.6.5.(4)   Wider Stairs than Required. The intent of Sentence 3.4.6.5.(4) is that handrails be installed in relation to the required exit width only, regardless of the actual width of the stair and ramp. The required handrails are provided along the assumed natural path of travel to, from, and within the building.

A-3.4.6.5.(11)   Termination of Handrails. Handrails should terminate at the wall, floor or post so as not to constitute a hazard to persons.

A-3.4.6.10.(5)   Door Swing. Although it is required that the door on the right hand side of a pair of doors shall swing in the direction of travel through the exit, the direction of swing of the door on the left side will depend on the function of the horizontal exit. If the horizontal exit provides for movement from one building to the adjacent building but does not require movement in the reverse direction, both doors must swing in the direction of travel to the adjacent building. If the design is based upon both buildings providing complementary movement in either direction, then the doors must swing in opposite directions. Location of a required exit sign directly above a door that swings in the direction of travel is deemed to meet the intent of Clause 3.4.6.10.(5)(b).

A-3.4.6.11.(4)   Exit Concealment. Hangings or draperies placed over exit doors may conceal or obscure them.

Exit Doors Concealed with Murals

Some people with cognitive disabilities such as dementia are at risk of wandering away from the residence or healthcare facility in which they are being treated. To reduce this risk, some residences and healthcare facilities install special hardware on egress and exit doors that can only be operated by designated persons. This solution keeps residents/patients from wandering, but the doors can still trigger anxiety in residents/patients who may nevertheless try to leave the space through them, without success.

Recent studies have shown that applying murals (of a landscape, for example) on exit and egress doors in these environments can help reduce anxiety in people with cognitive disabilities who tend to view them as a pleasant natural barrier rather than as a means of escape.

Where this approach is implemented and the doors are not reasonably discernible, an alternative means of egress from the space should be provided. It is expected that the designers and authorities having jurisdiction will use judgement in determining whether or not an alternative means of egress is required. Where this approach is implemented, the murals should be applied with care so that they do not conceal or impair the operation of any fire and life safety systems installed nearby, including, but not limited to, exit signage, emergency lighting, fire alarm devices, sprinklers or door hardware. Egress and exit doors with murals should be reasonably discernible to residential care or healthcare staff who will be required to assist residents/patients in the event that the space must be evacuated, and to visitors who will be expected to evacuate on their own.

A-3.4.6.16.(1)   Fastening Device. Turnpieces of a type which must be rotated through an angle of more than 90° before releasing a locking bolt are not considered to be readily openable. The release of a locking bolt should allow the door to open without having to operate other devices on the door.

A-3.4.6.16.(5)   Electromagnetic Lock. Electromagnetic locks are intended for use where there is a need for security additional to that provided by traditional exit hardware. They are not intended for indiscriminate use as alternative locking devices. The design of these devices requires evaluation to ensure that their operation will be fail-safe in allowing exiting in the event of foreseeable emergencies. If more than one locking device is used in a building, it is expected that one switch will release and reset all devices simultaneously.

A-3.4.6.16.(6)   Electromagnetic Locks in Care and Treatment Occupancies. The installation of electromagnetic locks in care and treatment occupancies requires special provisions to address the compromised condition of residents and the nature of daily operations. Accordingly, to reduce the incidence of false operation by residents, transparent boxes that set off an audible signal when opened can be installed to cover the manual stations. Also, one optional additional release device (e.g. swipe card device, key pad) can be installed to facilitate the free movement of staff and visitors in the building.

A-3.4.6.17.(1)   Special Security for Doors. The need for security in banks and in mercantile occupancies requires the ability to use positive locking devices on doors that may not readily be opened from inside the building. In a fully sprinklered building, the risk to persons inside the building is substantially reduced. The provisions of Sentences 3.4.6.17.(2) to (9) assume that the area is illuminated and that a means of communication is available to any occupant during times that the doors are locked.

A-3.5.2.1.(1)   Elevator Design. The reference to the Safety Standards Act and pursuant regulations in this Sentence implies conformance with all requirements of the pursuant regulations for elevator cars, hoistways, pits and machine rooms, including restrictions on other services in these areas and detailed design criteria.

A-3.5.4.1.(1)   Elevator Car Dimensions. In some circumstances it is necessary to maintain a patient on a stretcher in the prone position during transit to a hospital or to treatment facilities. Inclining the stretcher to load it into an elevator could be fatal or at the very least detrimental to the patient's health. Many ambulance services use a mobile patient stretcher whose size is 2 010 mm long and 610 mm wide. As well as space for the stretcher in the elevator, there should be sufficient additional space for at least two attendants who may also be providing treatment during transit.

Limited-use/limited-application (LULA) elevators are limited in size, capacity, speed and rise and are not expected to meet the minimum elevator car dimensions stated in Sentence (1).

A-3.6.2.5.(1)   Storage of Combustible Refuse and Recycling.  Storage of refuse consisting of combustible materials including waste paper, cardboard and plastic, and noncombustible materials such as glass and metallic containers can be accumulated in these rooms for the purpose of recycling. The storage of hazardous materials destined for recycling may need to satisfy other requirements than those stated in Sentence 3.6.2.5.(1).

A-3.6.2.7.(5)   Explosion Relief. Examples of good engineering practice for this application can be found in NFPA 68, “Standard on Explosion Protection by Deflagration Venting,” NFPA 69, “Standard on Explosion Prevention Systems,” and the NFPA “Fire Protection Handbook.”

A-3.6.3.1.(1)   Vertical Service Spaces. Sentence 3.6.3.1.(1) does not prohibit the internal subdivision of a vertical service space to allow different building services to be installed in physically separated spaces unless other requirements apply (see, for example, Sentences 3.2.7.10.(2) and (3)). Fire separation requirements apply to the perimeter of the group of service spaces. Article 3.6.3.3. has special requirements for linen chutes and refuse chutes.

A-3.6.3.5.   Grease Duct Enclosures. NFPA 96, “Standard for Ventilation Control and Fire Protection of Commercial Cooking Operations,” presents two options for enclosing grease ducts for commercial cooking equipment: the first option is to use continuous fire-rated building component assemblies to enclose the ducts and the second one consists of installing proprietary, fire-rated, field-applied or factory-built grease duct assemblies in accordance with the manufacturer's instructions. These types of enclosure assemblies are evaluated for their resistance to fire and their ability to protect adjacent combustibles through reduced clearances. Although NFPA 96 references other standards that deal with grease duct assemblies, Sentence 3.6.3.5.(2) requires that CAN/ULC-S144, “Standard Method of Fire Resistance Test – Grease Duct Assemblies,” be used to determine the fire-resistance rating of factory-built and field-applied grease duct assemblies.

A-3.6.4.2.(2)   Ceiling Membrane Rating. In construction assemblies that utilize membrane ceiling protection and have been assigned a fire-resistance rating on the basis of a fire test, the membrane is only one of the elements that contribute to the performance of the assembly and does not in itself provide the protection implied by the rating. For the fire-resistance rating of membrane materials used in this form of construction, reference should be made to the results of fire tests which have been conducted to specifically evaluate the performance of this element.

A-3.6.5.6.(2)   Clearance for Warm-Air Supply Ducts. Applicable to forced-air furnaces where permissible clearance C above plenum is 75 mm or less.

Figure A-3.6.5.6.(2)

Clearance for warm-air supply ducts

A-3.6.5.6.(3)   Clearance for Warm-Air Supply Ducts. Applicable to forced-air furnaces where permissible clearance C above plenum is more than 75 mm but not more than 150 mm.

Figure A-3.6.5.6.(3)

Clearance for warm-air supply ducts

A-3.6.5.6.(4)   Clearance for Warm-Air Supply Ducts. Applicable to forced-air furnaces where permissible clearance C above plenum is more than 150 mm.

Figure A-3.6.5.6.(4)

Clearance for warm-air supply ducts

A-3.7.2.1.(2)   Washroom Units in Industrial Occupancies. Substations and parking garages are examples of industrial occupancies where staff presence may be permanent or may be intermittent. In the case of parking garages, the presence of occupants other than staff is transitory.

A-3.8.   Accessible Design Principles. This Section contains minimum requirements for the design of buildings that accommodate people with diverse abilities, across their lifespan, including, but not limited to, people who use wheelchairs or other assistive mobility devices (e.g., walking aids, canes, crutches, braces, prosthetics), people with personal care providers, people with hearing or vision loss, and people with service animals, so they can access and use buildings.

Building Access Handbook

An illustrated guide and commentary has been produced to assist users of Section 3.8. and other access requirements of the British Columbia Building Code. This handbook contains the entire text of Section 3.8. and other access requirements, and is supplemented by commentary and illustrations on specific requirements.

Examples of basic accessibility requirements of the Code are as follows:

•   a clear floor space of at least 800 mm by 1 350 mm,

•   a 1 000 mm clear width allowing a 90° turn,

•   a 2 100 mm diameter clear floor space allowing a 180° turn in one motion, and

•   a 1 700 mm diameter clear floor space allowing a 180° turn in multiple motions.

A-3.8.2.1.   Accessibility. Industrial buildings often pose a greater risk to their occupants due to the presence of significant quantities of dangerous materials or the use of hazardous processes. For example, plants which are classified as Group F, Division 2 or 3, may store and use toxic or highly flammable substances in significant quantities, or house processes which involve very high temperatures and which have a high degree of automation. In some facilities, particularly in primary industries such as forestry and metallurgy, the construction normally used and the operations carried out within the space can make compliance with the requirements of Section 3.8. impracticable. It is therefore intended that these requirements be applied with discretion in buildings of Group F, Division 2 or 3 major occupancy. However, where industrial buildings contain subsidiary occupancies, such as offices or showrooms, it is reasonable to require that accessibility be provided in these spaces.

A-3.8.2.2.   Entrances. An accessible route should exist from the sidewalk or roadway and parking area to an accessible building entrance. This route should be located so that people do not have to pass through dedicated smoking areas or behind parked cars.  Accessible routes should coordinate with the routes to other buildings and to public transportation stops.

Article 3.8.2.2. applies to all entrances, including public and employee entrances, that provide access to an accessible storey. Doors that open onto exterior facilities that are only accessible from inside the building (e.g., hotel pools) are not considered entrances in the context of Article 3.8.2.2.

If an intercom system is provided, the system shall comply with the requirements for controls and should be useable by persons who communicate using visual language such as a video system.

A-3.8.2.3.   Access to Rooms and Facilities.  If access is required into suites or rooms in Subsection 3.8.2., it is intended that access be provided, with some exceptions identified in Sentence 3.8.2.3.(2), throughout each room or suite including access to all facilities and areas. Some examples of where access is required are as follows:

•   within each suite (subject to Clauses 3.8.2.3.(2)(k) and (l)),

•   within rooms or areas that serve the public or are designated for use by visitors, including interview rooms, holding rooms, changing rooms, areas in assembly occupancies with fixed seats so as to provide viewing of any entertainment areas, display areas and merchandising departments,

•   within each type of membership facility,

•   within rooms or areas for student use in assembly occupancies,

•   within general work areas, including office areas and areas with lockers,

•   within general use or general service areas, including shared laundry areas in residential occupancies, recreational areas, cafeterias, lounge rooms, lunch rooms and infirmaries,

•   within sleeping rooms in hospitals and nursing homes with treatment,

•   (if installed), into at least one passenger elevator or elevating device conforming to Articles 3.5.2.1. and 3.8.3.7.,

•   into washrooms described in Sentences 3.8.2.8.(1) to (4),

•   to any facility required by this Section to be designed to accommodate persons with physical disabilities,

•   onto every balcony provided in conformance with Clause 3.3.1.7.(1)(c), and

•   to service counters used by the general public (examples include ticket counters, refreshment stands, drinking fountains, cafeteria counters, checkout counters and bank service counters), and

•   to equipment designed to serve the public including self-serve kiosks, automated banking machines and night deposit boxes,

Where one or more hairdressing sinks are provided in barber shops, hairdressing shops and beauty parlors, at least one shall be useable by persons using in wheelchairs. Where fitting rooms are provided in a store, an accessible fitting room is required. An enclosure with not less than a 1700 diameter clear floor area is suggested.

The permission to waive an accessible path of travel for wheelchair access to certain specified areas of a building is not intended to waive accessibility requirements for persons whose physical disabilities do not require special provision for access to raised or sunken levels. Persons with vision impairments or who are deaf or hard of hearing that do not require the use of a wheelchair can be expected to move throughout a building.

Seating booths and banquettes in restaurants and bars are considered furniture, which is beyond the scope of the Code. However, various types of seating should be considered to ensure the availability of accessible options. Policies for seating such as those based on reservations or sequence of when patrons arrive is beyond the scope of the Code.

The concept of wheelchair accessibility does not extend to building service facilities, nor to all floor levels within a storey, e.g., mezzanines not served by an elevator. Mezzanines that are accessible by an elevator are therefore not excluded.

A-3.8.2.3.(2)(g)   Access to Facilities on a Floor Level other than the Entrance Level. Subclauses 3.8.2.3.(2)(g)(ii) to (iv) are intended to exempt certain storeys other than the entrance level—including basements and mezzanines that are less than 600 m2 in floor area or 100 m2 or less in floor area in assembly occupancies, that are self-contained and that contain the same facilities as the entrance level— from the requirement to have an accessible path of travel. Examples of buildings and spaces to which this exemption may apply are small office buildings with additional workspaces on the second storey and small restaurants with a second storey that contains only additional seating. However, if a restaurant's only washrooms are in the basement, they must have an accessible path of travel as they are an integral part of the principal function of the first storey. Similarly, staff lunchrooms and washrooms are also integral to the principal function of a restaurant; as such, if they are located in a floor area such as a second storey, basement or mezzanine that contains the only facilities, they must have an accessible path of travel for potential employees with disabilities.

Mezzanines that are not considered as stories for the purpose of determining building height are considered as stories for the purpose of applying Clause 3.8.2.3.(2)(g).

A-3.8.2.3.(4)   Waiting Areas with Fixed Seats. Many types of buildings have waiting areas, such as airports, hospitals, and government office buildings. Waiting areas should have a sufficient number of spaces designated for persons using wheelchairs so they can use the waiting area without blocking any means of egress.

The number of people using wheelchairs is typically much higher in treatment occupancies than in other types of occupancies. Designers should consider adding more designated wheelchair spaces in waiting areas than the numbers indicated in Table 3.8.2.3. in occupancies where a higher number of persons using wheelchairs is expected due to the types of services provided.

A-3.8.2.3.(5) and (6) and 3.8.3.22.(1) and (4)   Distribution of Adaptable Seats, Designated Wheelchair Spaces, and Mobility Aid Storage Spaces in Assembly Occupancies.

Figure A-3.8.2.3.(5) and (6) and 3.8.3.22.(1) and (4)

Example of distribution of adaptable seats, designated wheelchair spaces, and mobility aid storage spaces in an auditorium

A-3.8.2.4.(1)   Accessible Path of Travel to Storeys Served by Escalators and Moving Walks. In some buildings, escalators and inclined moving walks are installed to provide transportation from one floor level to another floor level so as to increase the capacity to move large numbers of persons. Some buildings located on a sloping site are accessible from street level on more than one storey and an escalator or inclined moving walk is provided for internal movement from floor to floor. In both these situations, people must be provided with an equally convenient means of moving between the same floor levels within the building. This may be accomplished by providing elevators, platform-equipped passenger-elevating devices, or ramps, for example.

A-3.8.2.5.   Parking Areas. In localities where local regulations or bylaws do not govern the provision of or dimensions of accessible parking spaces, the CSA B651, “Accessible design for the built environment,” standard as well as the following provides guidance to determine appropriate provisions. If parking spaces are provided, parking spaces for use by persons with physical disabilities should be provided in proportion considerate of anticipated use. Where parking spaces are provided, parking spaces for use by persons with physical disabilities should be provided for each accessible viewing position and for each accessible sleeping room or bed space. Parking spaces for use by persons with physical disabilities should

(1)   be not less than 2 600 mm wide, provided on one side with an access aisle not less than 2 000 mm wide, provided a perpendicular and adjacent rear access aisle not less than 2 000 mm wide, and have a clear height contiguous with the routes of the vehicular approach and exit of not less than 2 750 mm,

(2)   have a firm, slip-resistant and level surface,

(3)   be located close to an entrance required to conform to Article 3.8.2.2.,

(4)   be clearly marked as being for the use of persons with physical disabilities, and

(5)   be identified by a sign located not less than 1 500 mm above ground level, with the International Symbol of Access

Shared access aisle

Asphalt, concrete and firm, compacted gravel are acceptable parking surfaces. Curb ramps should be not less than 1500 mm wide. Parallel parking spaces should be not less than 7 000 mm long. If more than one parking space is provided for persons with physical disabilities, a single access aisle can serve two adjacent parking spaces. Parking to accommodate vans and other vehicles equipped with platform lifts or side ramps should be provided greater dedicated space. The design of the path of travel should accommodate loading to and from lifts and ramps including the necessary vehicle clearances.

A-3.8.2.5.(1) and (2)   Exterior Accessible Paths of Travel. The intent of Sentences 3.8.2.5.(1) and (2) is to ensure that exterior accessible paths of travel are readily available, direct and accessible so that persons of all abilities can move to and from a building with minimal effort.

A-3.8.2.6.(1)   Application to Security Access Systems. Sentence 3.8.2.6.(1) is not intended to reduce the functionality of security devices that limit access to secure areas and are addressed by other Sections of this Code.

A-3.8.2.6.(2) Electrical Outlets. Electrical outlets intended for occupant use shall be located so that their height above the finished floor is not a barrier to use. Outlets that are dedicated for specific equipment or functions and not intended to be readily available to occupants need not conform to the location requirements.

A-3.8.2.7.(1)(b)   Power Door Operators for Interior Doors. It is not intended that all doors located in an  accessible path of travel be equipped with a power door operator, but rather those that are located within public areas of the building, such as public corridors or corridors used by the public. Doors of suites served by a public area do not need to be equipped with a power door operator.

A-3.8.2.7.(3)   Accessible Entrances with Multiple Doorways. In selecting which doorway to equip with a power door operator as required by Sentence 3.8.2.7.(3), consideration should be given to the location of accessible paths of travel, to the ease of access, and to minimizing congestion.

A-3.8.2.8.(1) to (4)   Accessible and Universal Washrooms. A universal washroom is an accessible space providing privacy for one person and their care attendant(s), regardless of their gender. It is intended that a universal washroom be available in close proximity to each bank of washrooms in a floor area. In the case where only one water closet is provided, a universal washroom would satisfy the requirement of Sentence 3.8.2.8.(1).

A-3.8.2.8.(13)   Universal Dressing and Shower Rooms. A universal dressing and shower room is an accessible space that contains a shower and a space for dressing for one person and their care attendant(s) and provides privacy, regardless of gender.

It is intended that a universal dressing and shower room be available within close proximity to each bank of showers in a floor area. In cases where only one shower is provided, a universal dressing and shower room would satisfy the requirement.

A-3.8.2.8.(15)   Accessible Change Spaces. The intent of Sentence 3.8.2.8.(15) is to ensure that in large major occupancies, such as large shopping malls, public pools and libraries, occupants who may need assistance with personal hygiene will have access to an accessible change space that can be found in a consistent location.

Universal washrooms containing an accessible change space should be located so that they are available to the public when the large major occupancy is occupied. A suitable location could be in the lobby of a building housing the large major occupancy that remains open during that major occupancy's business hours, for example.

A-3.8.2.9.(2)   Assistive Listening Systems and Adaptive Technologies. The intent of Sentence 3.8.2.9.(2) is to require that at least one counter with an assistive listening system or adaptive technology be provided at each group of service counters providing the same exchange of information, goods or services. For example, in a stadium with ticket counters at multiple building entrances, at least one ticket counter at each entrance should be equipped with an assistive listening system or adaptive technology.

A-3.8.2.10.(4)   Directional Signage. This Code requires that directional signs be provided in a number of situations. Although they are only required to provide visual information, tactile directional signs should also be provided where practicable.

In some buildings, it may be necessary to supplement signs that provide visual and tactile information with visual displays, such as information displays and electronic interactive displays (e.g., wayfinding, exhibits and self-serve points-of-sale). Visual displays are common in motion picture theatres, law courts, exhibition halls, passenger stations/depots, museums, conference facilities, shops, stores and markets.

Wherever practicable, visual displays should be designed so that they are accessible to all people. In order to be accessible to people with low vision, visually displayed information should also be audibly communicated, either electronically or orally. Where touch screens are installed, an alternative means of accessing the information should be provided, for example by providing tactile buttons on an interactive display or by ensuring an attendant is always available to assist customers or visitors. Visual displays should also be accessible to people who use mobility devices. The degree of operability should accommodate people using a wide range of mobility devices (e.g., wheelchairs, scooters, walkers, canes) and people with a wide range of arm and hand mobility. Approach side, mounting height above the finished floor, amount of knee space, types of controls and the ability to reach them are particularly important considerations.

A-3.8.2.11.(1)   Counters with Work Surfaces. It is not intended that all counters be accessible, but that sufficient accessible counter space be available. Examples of counters that should be accessible include check-in counters and those in financial institutions and reception areas as well as any counter at which processing and signing of documents takes place. The provision is not intended to apply to work surfaces in industrial occupancies.

A-3.8.3.1.(1)   Accessible Design Standards. Code users who opt to apply the provisions of CSA B651, “Accessible design for the built environment,” listed in Table 3.8.3.1. must do so without exception: they cannot randomly select and apply a mix of provisions from this Code and that standard.

A-3.8.3.2.(2)   Reduction in Clear Width of an Accessible Path of Travel. Figure A-3.8.3.2.(2) presents schematic examples of accessible paths of travel with a section whose clear width is reduced as permitted by Sentence 3.8.3.2.(2).

Figure A-3.8.3.2.(2)

Accessible paths of travel with a reduced clear-width section

A-3.8.3.2.(3)   Surfaces in an Accessible Path of Travel. Floor finishes, including walk-off matts and carpet, should be selected, installed and securely fixed to provide a firm and stable surface so that people, including those who use mobility aids, can easily travel over them without tripping or expending undue energy. Other than very high-density, short-pile carpeting, most carpeting does not meet these criteria.

Furthermore, where the path of travel is exposed to intense light conditions, such as daylight or directional lighting, a low-glare or matte floor surface should be selected, as glare from floor surfaces can influence all users' perception, particularly those with vision loss. For the same reasons, heavily patterned flooring should also be avoided.

A-3.8.3.2.(6)   Wheelchair-Turning Space. Sentence 3.8.3.2.(6) presents three options for the design of clear floor spaces at the end of long narrow sections of accessible paths of travel to allow persons using a wheelchair to turn around instead of having to back up.

Figure A-3.8.3.2.(6) illustrates one possible configuration of a T-shaped wheelchair-turning space.

Figure A-3.8.3.2.(6)

T-shaped wheelchair-turning space

A-3.8.3.5.(1)(b)   Ramp Slopes. Ramps with a slope of more than 1 in 16 can be very difficult for persons with certain physical disabilities with upper body mobility to manage. Even though they pose less of a problem for persons using motorized wheelchairs, these ramps can be unsafe to descend, especially in cold climates. Although Article 3.8.3.5. permits slopes on ramps as great as 1 in 12 for distances of up to 9 m, slopes of 1 in 20 are safer and less strenuous. When limited space is available, as may be the case during renovations, ramps with a slope of up to 1 in 12 should be restricted to lengths not exceeding 3 m whenever possible. A strip contrasting in colour and texture should be used at the top and bottom of ramps to warn persons with low or no vision.

The phrase “uniform slope along its length” is intended to mean that the slope remains constant along the length of individual ramp segments.

A-3.8.3.5.(1)(c)   Landing Design at Doorways Leading to Ramps.

Figure A-3.8.3.5.(1)(c)

Landing design at doorways leading to ramps

A-3.8.3.5.(4)(a)   Surface of Ramps.  Sentence 3.8.3.2.(3) requires that all walking surfaces in an accessible path of travel be stable and firm to limit the effort required by persons using wheelchairs or other mobility aids. Therefore, Sentence 3.8.3.5.(4) requires that hard or resilient flooring be used on the surfaces of steeper ramps. Furthermore, carpet and like materials should not be installed on any ramp.

A-3.8.3.6.(2)   Doorway Width. Standard wheelchair width specifications indicate a range of sizes from 584 mm overall to 685 mm overall. Every doorway that is located in an accessible path of travel must have a clear width of not less than 850 mm when the door is in the open position and therefore it is important that this dimension be measured correctly. Figure A-3.8.3.6.(2) shows a door opened to 90°. It is clear that the door, and to a lesser extent the stop, impinges on the space within the door frame. The clear width of not less than 850 mm is measured from the face of the door in the open position of 90° to the doorway to the outside edge of the stop on the door frame. It is not sufficient just to measure the inside width of the door frame. The hardware selected on sliding doors, such as D-shaped handles, may result in a clear width being substantially less than the inside dimension of the door frame. The clear width for sliding doors is measured from the edge of the open door to the outside edge of the stop on the door frame. Other factors should be taken into account, including the location of door stops other than on the door frame, and the installation of door closers and exit devices, even if they do not span the width of the entire door. The intrusion of a door handle or an exit device into the space is of lesser importance because its height above the floor does not typically obstruct passage using a wheelchair. It is recognized that there are many types of door frames and door mounts, but the overall objective is to maintain a clear width of not less than 850 mm.

Figure 3.8.3.6.(2) depicts a somewhat restrictive scenario, as many doors can open wider than 90° to ensure the minimum clear width of 850 mm that is required. Swing of a door beyond 90° may be of less benefit as extended reach to close the door may be required once the doorway is passed through.

In a doorway with multiple swinging leaves, the active leaf must be capable of providing the required clear width in the open position. The clear width is then measured from the face of the active leaf, in the open position of 90° to the doorway, to the outside edge of the adjacent leaf when the adjacent leaf is in the closed position.

Figure A-3.8.3.6.(2)

Clear doorway width

A-3.8.3.6.(3)   Washrooms in Residential Occupancies. This requirement ensures that the doorway to the washroom in a hotel or motel suite is at least large enough to accommodate someone using a wheelchair. The Code does not require these washrooms to be accessible, in order to avoid a set of prescriptive requirements which could limit design flexibility. It is relatively simple to make washrooms accessible through careful planning and positioning of fixtures and this can be achieved in an area not much larger than that of conventional washrooms.

Figure A-3.8.3.6.(3)

Residential washrooms

A-3.8.3.6.(4)   Lever Handles. Lever handles are usable by most people and will meet the intent of this requirement. Lever handles with an end return towards the door are less prone to catch the clothing of someone passing through the doorway. Large D-shaped handles should be used on sliding doors.

A-3.8.3.6.(6) and (7)   Doors with Power Operators.  Doors equipped with a power operator actuated by a pressure plate identified with the International Symbol of Access or, where security is required, by a key, card or radio transmitter, and that can otherwise be opened manually, meet the intent of the requirement. The location of these actuating devices should ensure that a wheelchair will not interfere with the operation of the door once it is actuated. Swinging doors equipped with power operators which are actuated automatically and open into passing pedestrian traffic should be provided with a guard or other device designed to prevent pedestrians from stepping in the swing area of the door. These guards or devices should be detectable by blind persons. For example, inverted U-shaped guards should have an additional rail at a height not more than 680 mm so that it is detectable by the long cane. These doors should also have a device (mat or other sensor) on the swing side to prevent the door from opening if someone is standing in the swing area.

Figure A-3.8.3.6.(6) and (7)

Power operated doors

A-3.8.3.6.(9)   Air Pressure Differences.  Differences in air pressure on opposite sides of a door may be due to the operation of mechanical systems such as those associated with smoke control. So-called “stack action” in buildings in winter can also cause differential pressures due to the buoyancy of warm air. Stack action is usually most noticeable between stairwells and the remainder of the building, and at the entrances to buildings; the taller the building, the greater the effect. Doors with automatic closers have to operate with sufficient opening force to allow the return action to overcome the differential pressure.

A-3.8.3.6.(10)   Delayed Action on Door Closers. In some circumstances, closers with a delay feature which keeps the door open for several seconds before it begins to close might be desirable. However, closers with this feature have limited back-check, a feature of a normal door closer where resistance to opening increases as the door reaches the full arc of swing. Doors equipped with a delayed action closer are therefore more susceptible to damage should the door be opened with too much force or should someone try to force it closed, thinking the closer has failed to operate. Delayed action closers are not recommended for such occupancies as schools.

A-3.8.3.6.(11)   Clearance at Doorways. Sufficient clearance must be provided on the latch side of doors for a user to operate the door-opening mechanism and open the door without interference from the wheelchair. This is particularly important for a door swinging towards the approach side. See Figure A-3.8.3.6.(11).

Figure A-3.8.3.6.(11)

Doorway clearance

A-3.8.3.6.(14) to (16)    Minimum Clear Floor Space at Doors in an Accessible Path of Travel. Figure A-3.8.3.6.(14) to (16) presents schematic examples of the minimum clear floor space required at doors in an accessible path of travel. Power door operators serving doorways with a reduced width of the clear floor space should be operational at all times when the space is intended to be occupied.

Figure A-3.8.3.6.(14) to (16)

Minimum clear floor space required at doors in an accessible path of travel

A-3.8.3.6.(17)   Public Area. In the context of Sentence 3.8.3.6.(17), “public area” is intended to refer to a suite, room or area that is generally open to building occupants, such as a cafeteria, lounge room, washroom or office, but is not intended to include a space such as a janitor's room, service space or service room.

A-3.8.3.8.(1)(c)   Controls with Feedback Signals. Security access systems are a typical example of systems that have controls that provide feedback signals, such as illumination and an audible cue, which should be accessible to all users.

A-3.8.3.9.(1) and (2)   Visual and Tactile Information Signs.

Figure A-3.8.3.9.(1) and (2)

Positioning of visual and tactile information signs on and near doors

A-3.8.3.9.(3)   Accessibility Signs. The International Symbol of Access shown in Figure A-3.8.3.9.(3)-A indicates to persons with physical disabilities that they will have reasonable freedom of movement within a building so signed. The symbol is usually white on a blue background; where these colours do not stand out, the sign can be set on a white background. An arrow can be added to indicate direction or the location of an accessible space or facility.

Figure A-3.8.3.9.(3)-A

Signs indicating accessible facilities

The International Symbol of Access for Hearing Loss shown in Figure A-3.8.3.9.(3)-B, which indicates accessibility for persons who are deaf or hard of hearing, should be used to indicate the availability of variable volume controls on telephones, assistive listening systems, and text telephones (TT). These latter devices may also be referred to as teletypewriters (TTY) or telecommunications devices for the deaf (TDD).

Figure A-3.8.3.9.(3)-B

Signs for assistive listening facilities

When characters are used on signs to indicate accessible features, Arabic numerals and sans-serif letters with a stroke width to height ratio from 1 in 6 to 1 in 10 and a character width to height ratio from 3 in 5 to 1 in 1 should be used. Characters identifying doors and openings that lead from public areas and through which the public is permitted to pass should consist of Arabic numerals or sans-serif letters or both, be not less than 25 mm high and raised between 0.7 mm and 3 mm with a stroke to height ratio for ease of reading by touch. This identification should be located at the side of the doors or openings, centred 1 500 mm above the finished floor and within 150 mm of the jamb.

A-3.8.3.11.(2)(b) and (d)   Water-Bottle Filling Stations.

Figure A-3.8.3.11.(2)(b) and (d)

Clear floor space and operating height requirements for water-bottle filling stations

A-3.8.3.12.(1)(b)   Lateral Transfer Space on Alternate Sides of Water Closet. The lateral transfer space required by Clause 3.8.3.12.(1)(b) should be provided on the right side in one accessible stall or universal washroom and on the left side in another so that users can choose the facility with a transfer space on the side they prefer to use.

A-3.8.3.12.(1)(d)(v)   Water-closet Stalls.  Doors to water-closet stalls for persons with physical disabilities should swing outward, preferably against a side wall.

Figure A-3.8.3.12.(1)(d)(v)

Water-closet stalls

A-3.8.3.12.(1)(d)(vi)   Door Pulls. The door pull should consist of a D-shaped handle mounted horizontally. The centre lines are the lines drawn through the long axis and the short axis of the handle. The midpoint of the handle must be located horizontally at 200 to 300 mm from the hinged side of the door and vertically at 900 to 1 100 mm above the finished floor surface.

Figure A-3.8.3.12.(1)(d)(vi)-A

Door pull location

Figure A-3.8.3.12.(1)(d)(vi)-B

Door pull details

A-3.8.3.12.(1)(f)(ii)   Additional Grab Bars. It is the designer's prerogative to exceed the minimum requirements found in this Code and specify the installation of additional grab bars in other locations. These additional grab bars may be of different configurations and can be installed in other orientations.

A-3.8.3.13.   Clear Floor Space in Universal Washrooms. Unobstructed areas in front of the lavatory, in front of the water closet and on one side of the water closet are necessary for maneuverability of a wheelchair. Wall-mounted fixtures may project into the required floor space, provided that such projections do not restrict the maneuvering space required for persons using wheelchairs. Although outward swinging doors are preferable for accessibility, inward swinging doors are also permitted. Figures A-3.8.3.13.-A and A-3.8.3.13.-B show design options that meet the intent of Article 3.8.3.13.

Figure A-3.8.3.13.-A

Universal washroom with outward swinging door

Notes to Figure A-3.8.3.13.-A:

(1) See Article 3.8.3.12.

(2) See Article 3.8.3.13.

(3) See Article 3.8.3.16.

(4) See Article 3.8.3.6.

Figure A-3.8.3.13.-B

Universal washroom with inward swinging door

Notes to Figure A-3.8.3.13.-B:

(1) See Article 3.8.3.12.

(2) See Article 3.8.3.13.

(3) See Article 3.8.3.16.

(4) See Article 3.8.3.6.

A-3.8.3.14.(1)   Water Closets. Wall- or floor-mounted water closets with recessed bases are preferable because they provide the least amount of obstruction.

A-3.8.3.16.(1)(e)   Clearances Beneath a Lavatory.

Figure A-3.8.3.16.(1)(e)

Clearances beneath a lavatory

A-3.8.3.16.(1)(f)   Pipe Protection. The pipes referred to in Clause 3.8.3.16.(1)(f) include both supply and waste pipes. The hazard can be prevented by insulating the pipes, by locating the pipes in enclosures, or avoided by limiting the temperature of the hot water to a maximum of 45°C.

A-3.8.3.16.(1)(g)   Soap Dispenser Location. The location of accessories, such as soap dispensers and faucets, serving accessible lavatories should be established while taking into consideration that their controls must be usable by and within the direct reach of a person in a seated position directly in front of the accessible lavatory.

A-3.8.3.17.(1)(b)   Clear Space at Entrances to Showers. The clear space at the entrance to a shower may be encroached upon by fixtures such as a wall hung sink which does not interfere with the leg rests of the wheelchair. However, this sink could restrict movement for persons who need to make a lateral transfer if it were installed at the seat end of the shower.

Figure A-3.8.3.17.(1)(b)

Shower design

A-3.8.3.17.(1)(f)   Grab Bars. One L-shaped grab bar is required to be installed on the wall next to the seat. A grab bar behind the seat would prevent the user from leaning back against the wall, while one located on the wall opposite the seat cannot be reached from the seated position. The seat itself may be used in conjunction with the bar for transfer. If design flexibility is required, fold away grab bars can be used as an alternative.

A-3.8.3.17.(2)(f)   Grab Bar at Bench. Where a bench in a universal dressing and shower room is located adjacent to a wall, it is recommended that a grab bar be installed to assist users in transferring to the bench.

A-3.8.3.19.   Assistive Listening Systems.  Examples of assistive listening systems include FM, infrared and induction loop systems. However, the technology in this field is advancing rapidly; as such, other types of assistive listening systems could be considered in the design of a space. In choosing the most appropriate system, a number of factors must be taken into account including cost, installation and maintenance requirements, suitability for the intended user or audience, ease of operation, and the need for privacy. Information on designers and suppliers of such systems can be obtained from the Canadian Hearing Society. The intent of Article 3.8.3.19. is to provide clear communication where information, goods or services are provided to the public.

Wireless sound transmission systems, including FM, infrared and magnetic induction loop systems, improve sound reception for persons who are hard of hearing by providing amplification that can be adjusted by each user while blocking out unwanted background noise. Some of these systems transmit a signal that is picked up by a special receiver (FM, infrared) available for use by a person who is hard of hearing, whether or not a hearing aid is used. None of the systems interfere with the listening enjoyment of others.

The transmitter can be connected into an existing public address (P.A.) system amplifier or used independently with microphones. The induction loop system (see Figure A-3.8.3.19.-C) requires users with a hearing aid or cochlear implant to be in the area circumscribed by the loop; though installation of the loop is relatively simple, the installer should be knowledgeable about these systems if proper functioning is to be achieved. FM and infrared systems can be designed to broadcast signals that cover the entire room and thus do not restrict seating to any one area. Figures A-3.8.3.19.-A and A-3.8.3.19.-B show the general configuration of FM and infrared systems. Although portable systems (FM systems, in particular) are available, these are best suited to small audiences. Generally, the systems installed in church halls, auditoria, theatres and similar places of assembly are not easily portable, as they are installed in a fixed location by a sound technician and form an integral part of the P.A. system of the room or building.

Hard-wired systems (where a connection is provided at a particular seat in an auditorium, for example) might meet this requirement when adequate provisions are made to accommodate persons with hearing aids.

Figure A-3.8.3.19.-A

FM sound transmission system

Figure A-3.8.3.19.-B

Infrared sound transmission system

Figure A-3.8.3.19.-C

Induction loop sound transmission system

A-3.8.3.20.(1)(c)   Knee Space at Service Counters. Where forward-facing interaction with a person is required, the knee space requirement of Clause 3.8.3.20.(1)(c) applies to both sides of the service counter to ensure accessibility for both service providers and those receiving services.

A-3.8.3.21.(2)   Telephone Shelves or Counters. Built-in shelves or counters for public telephones must be designed to accommodate persons using text telephones (TT). These devices may also be referred to as teletypewriters (TTY) or telecommunication devices for the deaf (TDD). These devices require a level surface at least 305 mm deep by 250 mm wide with no obstruction above that space within 250 mm. If a wall-hung telephone or other obstruction extends to less than 250 mm from the shelf or counter, an equivalent clear space must be provided on either side of each telephone. At least one telephone should be equipped with a volume control on a receiver that generates a magnetic field compatible with the T-switch of a hearing aid. The lower portion of the shelf or counter is intended for persons using a wheelchair; therefore all parts of the operating mechanism of the telephone above this portion should be within reach of a person using a wheelchair.

A-3.8.3.22.(4)   Storage Spaces for Mobility Aids. The intent of Sentence 3.8.3.22.(4) is that a sufficient number of storage spaces for mobility aids other than wheelchairs and scooters (e.g., walkers) be located such that they can be accessed without leaving the seating area. These storage spaces should preferably be visible from the adaptable seats. The storage spaces may be located adjacent to an aisle but must not reduce the required egress width of the aisle or obstruct egress from the rows of seats.

A-3.8.5.6.(1)   Adaptable Dwelling Unit Floor Area. An adaptable dwelling unit bedroom shall be designed so that furniture will not be a barrier to functional use of the space. Occupant load is regulated by this Code though beds and furniture are not. Subsection 3.1.17. establishes an occupant load of two people per sleeping room. As such, it is reasonable to account for a bed that can sleep two people and functional maneuvering space adjacent the bed and throughout the room or space. Designs should allow for the bed to be located to accommodate transfer from the turning area to either side of the bed.

A-3.8.5.7.(1)(c) and (d). Plumbing Systems. Plumbing systems that accommodate the future installation of fixtures means that the water supply as well as drainage and venting systems are located so that the future installation of an accessible fixture does not require redesign of the system. An example is a sink that can be installed at multiple different heights without requiring a change to where the DWV pipe penetrates the wall.

A-3.8.5.7.(1)(e).   Reinforced Grab Bar Location. This provision is intended to ensure there is adequate backing for the installation of grab bars by the occupant in the future. For example, plywood or solid lumber behind the wall finish and encompassing the location of future grab bars located as described in Clauses 3.8.3.12.(1)(f) and (g) and Clause 3.8.3.17.(1)(f) or 3.8.3.18.(1)(f) would provide suitable backing for grab bar fasteners.

A-3.9.2.1.(1)   Building Area of Self-service Storage Buildings.  Sentence 3.9.2.1.(1) permits a group of self-service storage buildings to be treated as a single building for determining the construction requirements and number of streets that the group faces under Subsection 3.2.2. This can often result in more stringent construction criteria for the individual buildings than would be required if their construction requirements were determined based on each building's individual area.

Figure A-3.9.2.1.(1)

Building area of self-service storage buildings

A-3.9.2.2.   Spatial Separation Between Self-service Storage Buildings. Where a group of self-service storage buildings is treated as a single building as permitted in Sentence 3.9.2.1.(1), buildings within the same group are exempted from the spatial separation requirements in Subsection 3.2.3. as long as a minimum distance of 6 m is provided between each of them. If the owner wants less distance between the buildings, the requirements of Subsection 3.2.3. must be applied.

In addition, where there are multiple groups of buildings on a single property, the minimum distance required to separate one group from another group is the greater of 9 m and the limiting distance calculated in Subsection 3.2.3.

Except as provided in Article 3.9.2.2., Subsection 3.2.3. applies to each building within a group.

Figure A-3.9.2.2.

Spatial separation between self-service storage buildings

Notes to Figure A-3.9.2.2.:

(1) x = 9 m, or the distance calculated in Subsection 3.2.3., whichever is greater.

(2) y ≥ 6 m, or Subsection 3.2.3. applies.

A-3.9.3.1.(1)   Storage of Flammable and Combustible Liquids. Refer to Subsection 4.2.12. of Division B of the NFC for requirements regarding the storage of flammable and combustible liquids in individual self-service storage units.

A-3.9.3.2.(1)   Sanitary Facilities. Properties with self-service storage buildings on them may have multiple buildings or one large building. Due to the low occupant load of these types of buildings, only one building on the property is required to have a pair of washrooms.