Part 4

Structural Design

Section  4.1.   Structural Loads and Procedures

4.1.1. General

4.1.1.1. Scope

1)   The scope of this Part shall be as described in Subsection 1.3.3. of Division A.

4.1.1.2. Definitions

1)   Words that appear in italics in this Part are defined in Article 1.4.1.2. of Division A.

4.1.1.3. Design Requirements

1)   Buildings and their structural members and connections, including formwork and falsework, shall be designed to have sufficient structural capacity and structural integrity to safely and effectively resist all loads, effects of loads and influences that may reasonably be expected, having regard to the expected service life of buildings, and shall in any case satisfy the requirements of this Section. (See Note A-4.1.1.3.(1).)

2)   Buildings and their structural members shall be designed for serviceability, in accordance with Articles 4.1.3.4., 4.1.3.5. and 4.1.3.6. (See Note A-4.1.1.3.(2).)

3)   All permanent and temporary structural members, including the formwork and falsework of a building, shall be protected against loads exceeding the specified loads during the construction period except when, as verified by analysis or test, temporary overloading of a structural member would result in no impairment of that member or any other member.

4)   Falsework, scaffolding, and formwork shall be designed in conformance with

a)   CSA S269.1, “Falsework and formwork,”

b)   CSA S269.2, “Access scaffolding for construction purposes,” or

c)   CAN/CSA-S269.3-M, “Concrete Formwork.”

5)   Precautions shall be taken during all phases of construction to ensure that the building is not damaged or distorted due to loads applied during construction.

4.1.1.4. Structural Drawings and Related Documents

1)   Structural drawings and related documents shall conform to the appropriate requirements of Section 2.2. of Division C. (See Subsection 2.2.4. of Division C.)

4.1.1.5. Design Basis

1)   Except as provided in Sentence (2), buildings and their structural members shall be designed in conformance with the procedures and practices provided in this Part.

2)   Provided the design is carried out by a person especially qualified in the specific methods applied and provided the design demonstrates a level of safety and performance in accordance with the requirements of Part 4, buildings and their structural components falling within the scope of Part 4 that are not amenable to analysis using a generally established theory may be designed by

a)   evaluation of a full-scale structure or a prototype by a loading test, or

b)   studies of model analogues.

(See Note A-4.1.1.5.(2).)

4.1.2. Specified Loads and Effects

4.1.2.1. Loads and Effects

(See Note A-4.1.2.1.)

1)   Except as provided in Article 4.1.2.2., the following categories of loads, specified loads and effects shall be taken into consideration in the design of a building and its structural members and connections:

D    dead load – a permanent load due to the weight of building components, as specified in Subsection 4.1.4.,

E    earthquake load and effects – a rare load due to an earthquake, as specified in Subsection 4.1.8.,

H    a permanent load due to lateral earth pressure, including groundwater,

L    live load – a variable load due to intended use and occupancy (including loads due to cranes and the pressure of liquids in containers), as specified in Subsection 4.1.5.,

LXC    live load exclusive of crane loads,

C    live load due to cranes including self weight,

Cd    self weight of all cranes positioned for maximum effects,

C7    crane bumper impact load,

P    permanent effects caused by pre-stress,

S    variable load due to snow, including ice and associated rain, as specified in Article 4.1.6.2., or due to rain, as specified in Article 4.1.6.4.,

T    effects due to contraction, expansion, or deflection caused by temperature changes, shrinkage, moisture changes, creep, ground settlement, or a combination thereof (see Note A-4.1.2.1.(1)), and

W    wind load – a variable load due to wind, as specified in Subsection 4.1.7.,

where

a)   load means the imposed deformations (i.e. deflections, displacements or motions that induce deformations and forces in the structure), forces and pressures applied to the building structure,

b)   permanent load is a load that changes very little once it has been applied to the structure, except during repair,

c)   variable load is a load that frequently changes in magnitude, direction or location, and

d)   rare load is a load that occurs infrequently and for a short time only.

2)   Minimum specified values of the loads described in Sentence (1), as set forth in Subsections 4.1.4. to 4.1.8., shall be increased to account for dynamic effects where applicable.

3)   For the purpose of determining specified loads S, W or E in Subsections 4.1.6.,  4.1.7. and 4.1.8., buildings shall be assigned an Importance Category based on intended use and occupancy, in accordance with Table 4.1.2.1. (See Note A-4.1.2.1.(3).)

Table 4.1.2.1.

Importance Categories for Buildings(1)

Forming Part of Sentence 4.1.2.1.(3)

| Type of Building | Importance Category |
| --- | --- |
| A Low Importance Category building is a building that represents a low direct or indirect hazard to human life in the event of structural failure. | Low |
| A Normal Importance Category building is a building that does not meet the criteria for a Low Importance Category building, High Importance Category building or post-disaster building. | Normal |
| A High Importance Category building is a building that provides a greater degree of safety to human life than a Normal Importance Category building. Community centres and elementary, middle and secondary schools are High Importance Category buildings. | High |
| A post-disaster building. | Post-disaster |

Notes to Table 4.1.2.1.:

(1) See Note A-Table 4.1.2.1.

4.1.2.2. Loads Not Listed

1)   Where a building or structural member can be expected to be subjected to loads, forces or other effects not listed in Article 4.1.2.1., such effects shall be taken into account in the design based on the most appropriate information available. (See Note A-4.1.2.2.(1).)

4.1.3. Limit States Design

(See Note A-4.1.3.)

4.1.3.1. Definitions

1)   In this Subsection, the term

a)   limit states means those conditions of a building structure that result in the building ceasing to fulfill the function for which it was designed (those limit states concerning safety are called ultimate limit states (ULS) and include exceeding the load-carrying capacity, overturning, sliding and fracture; those limit states that restrict the intended use and occupancy of the building are called serviceability limit states (SLS) and include deflection, vibration, permanent deformation and local structural damage such as cracking; and those limit states that represent failure under repeated loading are called fatigue limit states),

b)   specified loads (C, D, E, H, L, P, S, T and W) means those loads defined in Article 4.1.2.1.,

c)   principal load means the specified variable load or rare load that dominates in a given load combination,

d)   companion load means a specified variable load that accompanies the principal load in a given load combination,

e)   service load means a specified load used for the evaluation of a serviceability limit state,

f)   principal-load factor means a factor applied to the principal load in a load combination to account for the variability of the load and load pattern and the analysis of its effects,

g)   companion-load factor means a factor that, when applied to a companion load in the load combination, gives the probable magnitude of a companion load acting simultaneously with the factored principal load,

h)   importance factor, I, means a factor applied in Subsections 4.1.6., 4.1.7. and 4.1.8. to obtain the specified load and take into account the consequences of failure as related to the limit state and the use and occupancy of the building,

i)   factored load means the product of a specified load and its principal-load factor or companion-load factor,

j)   effects refers to forces, moments, deformations or vibrations that occur in the structure,

k)   nominal resistance, R, of a member, connection or structure, is based on the geometry and on the specified properties of the structural materials,

l)   resistance factor, φ, means a factor applied to a specified material property or to the resistance of a member, connection or structure, and that, for the limit state under consideration, takes into account the variability of dimensions and material properties, workmanship, type of failure and uncertainty in the prediction of resistance, and

m)   factored resistance, φR, means the product of nominal resistance and the applicable resistance factor.

4.1.3.2. Strength and Stability

1)   A building and its structural components shall be designed to have sufficient strength and stability so that the factored resistance, φR, is greater than or equal to the effect of factored loads, which shall be determined in accordance with Sentence (2).

2)   Except as provided in Sentence (3), the effect of factored loads for a building or structural component shall be determined in accordance with the requirements of this Article and the following load combination cases, the applicable combination being that which results in the most critical effect:

a)   for load cases without crane loads, the load combinations listed in Table 4.1.3.2.-A, and

b)   for load cases with crane loads, the load combinations listed in Table 4.1.3.2.-B.

(See Note A-4.1.3.2.(2).)

3)   Other load combinations that must also be considered are the principal loads acting with the companion loads taken as zero.

4)   Where the effects due to lateral earth pressure, H, restraint effects from pre-stress, P, and imposed deformation, T, affect the structural safety, they shall be taken into account in the calculations, with load factors of 1.5, 1.0 and 1.25 assigned to H, P and T respectively. (See Note A-4.1.3.2.(4).)

5)   Except as provided in Sentence 4.1.8.16.(2), the counteracting factored dead load—0.9D in load combination cases 2, 3 and 4 and 1.0D in load combination case 5 in Table 4.1.3.2.-A, and 0.9D in load combination cases 1 to 5 and 1.0D in load combination case 6 in Table 4.1.3.2.-B—shall be used when the dead load acts to resist overturning, uplift, sliding, failure due to stress reversal, and to determine anchorage requirements and the factored resistance of members. (See Note A-4.1.3.2.(5).)

6)   The principal-load factor 1.5 for live loads L in Table 4.1.3.2.-A and LXC in Table 4.1.3.2.-B may be reduced to 1.25 for liquids in tanks.

7)   The companion-load factor for live loads L in Table 4.1.3.2.-A and LXC in Table 4.1.3.2.-B shall be increased by 0.5 for storage areas, and equipment areas and service rooms referred to in Table 4.1.5.3.

Table 4.1.3.2.-A

Load Combinations Without Crane Loads for Ultimate Limit States

Forming Part of Sentences 4.1.3.2.(2) and (5) to (10), and 4.2.4.1.(3)

| Case | Load Combination(1) |  |
| --- | --- | --- |
|  | Principal Loads | Companion Loads |
| 1 | 1.4D(2) | — |
| 2 | (1.25D(3) or 0.9D(4)) + 1.5L(5) | 1.0S(6) or 0.4W |
| 3 | (1.25D(3) or 0.9D(4)) + 1.5S | 1.0L(6)(7) or 0.4W |
| 4 | (1.25D(3) or 0.9D(4)) + 1.4W | 0.5L(7) or 0.5S |
| 5 | 1.0D(4) + 1.0E(8) | 0.5L(6)(7) + 0.25S(6) |

Notes to Table 4.1.3.2.-A:

(1) See Sentences 4.1.3.2.(2) to (4).

(2) See Sentence 4.1.3.2.(9).

(3) See Sentence 4.1.3.2.(8).

(4) See Sentence 4.1.3.2.(5).

(5) See Sentence 4.1.3.2.(6).

(6) See Article 4.1.5.5.

(7) See Sentence 4.1.3.2.(7).

(8) See Sentence 4.1.3.2.(10).

Table 4.1.3.2.-B

Load Combinations With Crane Loads for Ultimate Limit States

Forming Part of Sentences 4.1.3.2.(2), (5) to (8), and (10)

| Case | Load Combination(1) |  |
| --- | --- | --- |
|  | Principal Loads | Companion Loads |
| 1 | (1.25D(2) or 0.9D(3)) + (1.5C + 1.0LXC) | 1.0S(4) or 0.4W |
| 2 | (1.25D(2) or 0.9D(3)) + (1.5LXC(5) + 1.0C) | 1.0S(4) or 0.4W |
| 3 | (1.25D(2) or 0.9D(3)) + 1.5S | 1.0C + 1.0LXC(4)(6) |
| 4 | (1.25D(2) or 0.9D(3)) + 1.4W | 1.0C(7) + 0.5LXC(4)(6) |
| 5 | (1.25D(2) or 0.9D(3)) + C7 | — |
| 6 | 1.0D(3) + 1.0E(8) | 1.0Cd + 0.5LXC(4)(6) + 0.25S(4) |

Notes to Table 4.1.3.2.-B:

(1) See Sentences 4.1.3.2.(2) to (4).

(2) See Sentence 4.1.3.2.(8).

(3) See Sentence 4.1.3.2.(5).

(4) See Article 4.1.5.5.

(5) See Sentence 4.1.3.2.(6).

(6) See Sentence 4.1.3.2.(7).

(7) Side thrust due to cranes need not be combined with full wind load.

(8) See Sentence 4.1.3.2.(10).

8)   Except as provided in Sentence (9), the load factor 1.25 for dead load, D, for soil, superimposed earth, plants and trees given in Tables 4.1.3.2.-A and 4.1.3.2.-B shall be increased to 1.5, except that when the soil depth exceeds 1.2 m, the factor may be reduced to 1 + 0.6/hs but not less than 1.25, where hs is the depth of soil, in m, supported by the structure.

9)   A principal-load factor of 1.5 shall be applied to the weight of saturated soil used in load combination case 1 of Table 4.1.3.2.-A.

10)   Earthquake load, E, in load combination cases 5 of Table 4.1.3.2.-A and 6 of Table 4.1.3.2.-B includes horizontal earth pressure due to earthquake determined in accordance with Sentence 4.1.8.16.(7).

11)   Provision shall be made to ensure adequate stability of the structure as a whole and adequate lateral, torsional and local stability of all structural parts.

12)   Sway effects produced by vertical loads acting on the structure in its displaced configuration shall be taken into account in the design of buildings and their structural members.

4.1.3.3. Fatigue

1)   A building and its structural components, including connections, shall be checked for fatigue failure under the effect of cyclical loads, as required in the standards listed in Section 4.3. (See Note A-4.1.3.3.(1).)

2)   Where vibration effects, such as resonance and fatigue resulting from machinery and equipment, are likely to be significant, a dynamic analysis shall be carried out. (See Note A-4.1.3.3.(2).)

4.1.3.4. Serviceability

1)   A building and its structural components shall be checked for serviceability limit states as defined in Clause 4.1.3.1.(1)(a) under the effect of service loads for serviceability criteria specified or recommended in Articles 4.1.3.5. and 4.1.3.6. and in the standards listed in Section 4.3. (See Note A-4.1.3.4.(1).)

2)   The effect of service loads on the serviceability limit states shall be determined in accordance with this Article and the load combinations listed in Table 4.1.3.4., the applicable combination being that which results in the most critical effect.

3)   Other load combinations that must also be considered are the principal loads acting with the companion loads taken as zero.

4)   Deflections calculated for load types P, T and H, if present, with load factors of 1.0 shall be included with the calculated deflections due to principal loads.

5)   The determination of the deflection shall consider the following:

a)   for materials that result in increased deformations over time under sustained loads, the deflection calculation shall consider the portion of live load, L, that is sustained over time, Ls, and the portion that is transitory, Lt, and

b)   the calculated deflection due to dead load, D, and sustained live load, Ls, shall be increased by a creep factor as specified in the standards listed in Section 4.3. to obtain the additional long-term deflection.

6)   The determination of the long-term settlement of foundations shall consider the following:

a)   for foundation soil types that result in increased settlement over time under sustained loads, the additional long-term settlements shall be determined for the portion of live load, L, that is sustained over time, Ls, and the portion that is transitory, Lt, and

b)   the additional long-term settlements due to dead load, D, and sustained live loads, Ls, shall be calculated from the foundation soil properties provided by a qualified professional geotechnical engineer.

Table 4.1.3.4.

Loads and Load Combinations for Serviceability

Forming Part of Sentence 4.1.3.4.(2)

| Limit State | Structural Parameter | Load Case | Load Combinations |  |
| --- | --- | --- | --- | --- |
|  |  |  | Principal Loads | Companion Loads |
| Deflection for materials not subject to creep | Deflection of the structure or of components of the structure(1) | 1 | 1.0D + 1.0L | 0.3W or 0.35S |
|  |  | 2 | 1.0D + 1.0W | 0.35L(2) or 0.35S |
|  |  | 3 | 1.0D + 1.0S | 0.3W or 0.35L(2) |
| Deflection for materials subject to creep | Total deflection of the structure or of components of the structure(3) | 1 | 1.0D + 1.0Ls(4) + 1.0Lt(5) | 0.3W or 0.35S |
|  |  | 2 | 1.0D + 1.0W | 0.35L(2) or 0.35S |
|  |  | 3 | 1.0D + 1.0S | 0.3W or 0.35L(2) |
| Vibration serviceability | Acceleration | (6) |  |  |

Notes to Table 4.1.3.4.:

(1) The calculated deflection due to dead load, D, is permitted to be excluded where specified in the standards listed in Section 4.3.

(2) The companion load factor of 0.35 for live load, L, shall be increased to 0.5 for storage areas, equipment areas and service rooms.

(3) The calculated immediate deflection due to dead load, D, is permitted to be excluded where specified in the standards listed in Section 4.3.

(4) Ls = sustained portion of the live load, L.

(5) Lt = transitory portion of the live load, L.

(6) See Note A-Table 4.1.3.4.

4.1.3.5. Deflection

1)   In proportioning structural members to limit serviceability problems resulting from deflections, consideration shall be given to

a)   the intended use of the building or member,

b)   limiting damage to non-structural members made of materials whose physical properties are known at the time of design,

c)   limiting damage to the structure itself, and

d)   creep, shrinkage, temperature changes and pre-stress.

(See Note A-4.1.3.5.(1).)

2)   The lateral deflection of buildings due to service wind and gravity loads shall be checked to ensure that structural elements and non-structural elements whose nature is known at the time the structural design is carried out will not be damaged.

3)   Except as provided in Sentence (4), the total drift per storey under service wind and gravity loads shall not exceed 1/500 of the storey height unless other drift limits are specified in the design standards referenced in Section 4.3. (See Note A-4.1.3.5.(3).)

4)   The deflection limits required in Sentence (3) do not apply to industrial buildings or sheds if experience has proven that greater movement will have no significant adverse effects on the strength and function of the building.

5)   The building structure shall be designed for lateral deflection due to E, in accordance with Article 4.1.8.13.

4.1.3.6. Vibration

1)   Floor systems susceptible to vibration shall be designed so that vibrations will have no significant adverse effects on the intended occupancy of the building. (See Note A-4.1.3.6.(1).)

2)   Where floor vibrations caused by resonance with operating machinery or equipment are anticipated, dynamic analysis of the floor system shall be carried out. (See Note A-4.1.3.6.(2).)

3)   Where the fundamental vibration frequency of a structural system supporting an assembly occupancy used for rhythmic activities, such as dancing, concerts, jumping exercises or gymnastics, is less than 6 Hz, the effects of resonance shall be investigated by means of a dynamic analysis. (See Note A-4.1.3.6.(3).)

4)   A building susceptible to lateral vibration under wind load shall be designed in accordance with Article 4.1.7.1. so that the vibrations will have no significant adverse effects on the intended use and occupancy of the building. (See Note A-4.1.3.6.(4).)

4.1.4. Dead Loads

4.1.4.1. Dead Loads

1)   The specified dead load for a structural member consists of

a)   the weight of the member itself,

b)   the weight of all materials of construction incorporated into the building to be supported permanently by the member,

c)   the weight of partitions,

d)   the weight of permanent equipment, and

e)   the vertical load due to soil, superimposed earth, plants and trees.

2)   In areas of a building for which partitions are shown on the drawings, the weight of partitions referred to in Clause (1)(c) shall be taken as the actual weight of such partitions. (See Note A-4.1.4.1.(2).)

3)   In areas of a building for which partitions are not shown on the drawings, the weight of partitions referred to in Clause (1)(c) shall be a partition weight allowance determined from the anticipated weight and position of the partitions, but shall not be less than 1 kPa over the area of floor being considered. (See Note A-4.1.4.1.(3).)

4)   The weights of partitions and partition weight allowances used in the design shall be shown on the drawings as provided in Clause 2.2.4.3.(1)(d) of Division C.

5)   Where the partition weight allowance referred to in Sentence (3) is counteractive to other loads, it shall not be included in the design calculations.

6)   Except for structures where the dead load of soil is part of the load-resisting system, where the dead load due to soil, superimposed earth, plants and trees is counteractive to other loads, it shall not be included in the design calculations. (See Note A-4.1.4.1.(6).)

4.1.5. Live Loads Due to Use and Occupancy

4.1.5.1. Loads Due to Use of Floors and Roofs

1)   Except as provided in Sentence (2), the specified live load on an area of floor or roof depends on the intended use and occupancy, and shall not be less than either the uniformly distributed load patterns listed in Article 4.1.5.3., the loads due to the intended use and occupancy, or the concentrated loads listed in Article 4.1.5.9., whichever produces the most critical effect. (See Note A-4.1.5.1.(1).)

2)   For buildings in the Low Importance Category as described in Table 4.1.2.1., a factor of 0.8 may be applied to the live load.

4.1.5.2. Uses Not Stipulated

1)   Except as provided in Sentence (2), where the use of an area of floor or roof is not provided for in Article 4.1.5.3., the specified live loads due to the use and occupancy of the area shall be determined from an analysis of the loads resulting from the weight of

a)   the probable assembly of persons,

b)   the probable accumulation of equipment and furnishings, and

c)   the probable storage of materials.

2)   For buildings in the Low Importance Category as described in Table 4.1.2.1., a factor of 0.8 may be applied to the live load.

4.1.5.3. Full and Partial Loading

1)   The uniformly distributed live load shall be not less than the value listed in Table 4.1.5.3., which may be reduced as provided in Article 4.1.5.8., applied uniformly over the entire area or on any portions of the area, whichever produces the most critical effects in the members concerned.

Table 4.1.5.3.

Specified Uniformly Distributed Live Loads on an Area of Floor or Roof

Forming Part of Sentence 4.1.5.3.(1)

| Use of Area of Floor or Roof | Minimum Specified Load, kPa |
| --- | --- |
| Assembly Areas | 4.8 |
| a) Except for the areas listed under b), c), d) and e), assembly areas with or without fixed seats including |  |
| Arenas(1) (areas without fixed seats that have backs) |  |
| Auditoria |  |
| Churches (areas without fixed seats that have backs) |  |
| Dance floors |  |
| Dining areas(2) |  |
| Foyers and entrance halls |  |
| Grandstands(1) (areas without fixed seats that have backs), reviewing stands and bleachers |  |
| Gymnasia |  |
| Lecture halls(1) (areas without fixed seats that have backs) |  |
| Museums |  |
| Promenades |  |
| Rinks |  |
| Stadia(1) (areas without fixed seats that have backs) |  |
| Theatres (areas without fixed seats that have backs) |  |
| Other areas with similar uses |  |
| b) Classrooms and courtrooms with or without fixed seats(1) | 2.4 |
| c) Portions of assembly areas with fixed seats that have backs for the following uses: | 2.9 |
| Arenas(1) |  |
| Grandstands(1) |  |
| Stadia(1) |  |
| d) Portions of assembly areas with fixed seats that have backs for the following uses: | 2.4 |
| Churches |  |
| Lecture halls(1) |  |
| Theatres |  |
| e) Vomitories, exits, lobbies and corridors(1) | 4.8 |
| Attics(1) |  |
| Accessible by a stairway in residential occupancies only | 1.4 |
| Having limited accessibility so that there is no storage of equipment or material | 0.5 |
| Balconies |  |
| Exterior | 4.8 |
| Interior and mezzanines that could be used by an assembly of people as a viewing area(1) | 4.8 |
| Interior and mezzanines other than above | (3) |
| Corridors, lobbies and aisles(1) |  |
| Other than those listed below | 4.8 |
| Not more than 1 200 mm in width, and all upper floor corridors of residential areas only of apartments, hotels and motels (that cannot be used by an assembly of people as a viewing area) | (3) |
| Equipment areas and service rooms including | 3.6(4) |
| Generator rooms |  |
| Mechanical equipment exclusive of elevators |  |
| Machine rooms |  |
| Pump rooms |  |
| Transformer vaults |  |
| Ventilating or air-conditioning equipment |  |
| Exits and fire escapes | 4.8 |
| Factories | 6.0(4) |
| Footbridges | 4.8 |
| Garages for |  |
| Vehicles not exceeding 4 000 kg gross weight | 2.4 |
| Vehicles exceeding 4 000 kg but not exceeding 9 000 kg gross weight | 6.0 |
| Vehicles exceeding 9 000 kg gross weight(1) | 12.0 |
| Kitchens (other than residential) | 4.8 |
| Libraries |  |
| Stack rooms | 7.2 |
| Reading and study rooms | 2.9 |
| Office areas(1) (not including record storage and computer rooms) located in |  |
| Basements, and floors, including mezzanines, with direct access to the exterior at ground level | 4.8 |
| Other floors | 2.4 |
| Operating rooms and laboratories | 3.6 |
| Patients' bedrooms | 1.9 |
| Recreation areas that cannot be used for assembly purposes including | 3.6 |
| Billiard rooms |  |
| Bowling alleys |  |
| Pool rooms |  |
| Residential areas (within the scope of Article 1.3.3.2. of Division A) |  |
| Sleeping and living quarters in apartments, hotels, motels, boarding schools and colleges | 1.9 |
| Residential areas (within the scope of Article 1.3.3.3. of Division A) | 1.9 |
| Bedrooms |  |
| Other areas |  |
| Stairs within dwelling units |  |
| Retail and wholesale areas | 4.8 |
| Roofs(1) | 1.0(5) |
| Sidewalks and driveways over areaways and basements(1) | 12.0(5) |
| Storage areas | 4.8(4) |
| Toilet areas | 2.4 |
| Underground slabs with earth cover | (5) |
| Warehouses | 4.8(4) |

Notes to Table 4.1.5.3.:

(1) See Note A-Table 4.1.5.3.

(2) See Article 4.1.5.6.

(3) See Article 4.1.5.4.

(4) See Sentence 4.1.5.1.(1).

(5) See Article 4.1.5.5.

4.1.5.4. Loads for Occupancy Served

1)   The following shall be designed to carry not less than the specified load required for the occupancy they serve, provided they cannot be used by an assembly of people as a viewing area:

a)   corridors, lobbies and aisles not more than 1 200 mm wide,

b)   all corridors above the first storey of residential areas of apartments, hotels and motels, and

c)   interior balconies and mezzanines.

4.1.5.5. Loads on Exterior Areas

(See Note A-4.1.5.5.)

1)   Exterior areas accessible to vehicular traffic shall be designed for their intended use, including the weight of firefighting equipment, but not for less than the snow and rain loads prescribed in Subsection 4.1.6.

2)   Except as provided in Sentences (3) and (4), roofs shall be designed for either the uniform live loads specified in Table 4.1.5.3., the concentrated live loads listed in Table 4.1.5.9., or the snow and rain loads prescribed in Subsection 4.1.6., whichever produces the most critical effect.

3)   Exterior areas accessible to pedestrian traffic, but not vehicular traffic, shall be designed for their intended use, but not for less than the greater of

a)   the live load prescribed for assembly areas in Table 4.1.5.3., or

b)   the snow and rain loads prescribed in Subsection 4.1.6.

4)   Roof parking decks and exterior areas accessible to vehicular traffic shall be designed

a)   for the appropriate load combination listed in Sentence 4.1.3.2.(2) with a live load, L, consisting of either a uniformly distributed live load as specified in Table 4.1.5.3. or a concentrated live load as listed in Table 4.1.5.9., whichever produces the most critical effect, and a companion snow load, S, as prescribed in Subsection 4.1.6., but with the companion-load factor reduced to 0.2, and

b)   such that the load combination in Clause (a) is not less than the snow and rain loads prescribed in Subsection 4.1.6. with the live load taken as zero.

5)   Roof parking decks that are used for the long-term storage of vehicles shall be designed for the appropriate load combination listed in Sentence 4.1.3.2.(2) with a live load, L, consisting of either a uniformly distributed live load as specified in Table 4.1.5.3. or a concentrated live load as listed in Table 4.1.5.9., whichever produces the most critical effect, and a snow load, S, as prescribed in Subsection 4.1.6.

4.1.5.6. Loads for Dining Areas

1)   The minimum specified live load listed in Table 4.1.5.3. for dining areas may be reduced to 2.4 kPa for areas in buildings that are being converted to dining areas, provided that the floor area does not exceed 100 m2 and the dining area will not be used for other assembly purposes, including dancing.

4.1.5.7. More Than One Occupancy

1)   Where an area of floor or roof is intended for 2 or more occupancies at different times, the value to be used from Table 4.1.5.3. shall be the greatest value for any of the occupancies concerned.

4.1.5.8. Variation with Tributary Area

(See Note A-4.1.5.8.)

1)   One- and two-way floor slabs shall have no reduction for tributary area applied to live load.

2)   An area used for assembly occupancies designed for a live load of less than 4.8 kPa and roofs designed for the minimum loading specified in Table 4.1.5.3. shall have no reduction for tributary area.

3)   Where a structural member supports a tributary area of a floor or a roof, or a combination thereof, that is greater than 80 m2 and either used for assembly occupancies designed for a live load of 4.8 kPa or more, or used for storage, manufacturing, retail stores, garages or as a footbridge, the specified live load due to use and occupancy is the load specified in Article 4.1.5.3. multiplied by

where A is the tributary area in square metres for this type of use and occupancy.

4)   Where a structural member supports a tributary area of a floor or a roof, or a combination thereof, that is greater than 20 m2 and used for any use or occupancy other than those indicated in Sentences (2) and (3), the specified live load due to use and occupancy is the load specified in Article 4.1.5.3. multiplied by

where B is the tributary area in square metres for this type of use and occupancy.

5)   Where the specified live load for a floor is reduced in accordance with Sentence (3) or (4), the structural drawings shall indicate that a live load reduction factor for tributary area has been applied and which structural elements are impacted by this factor.

4.1.5.9. Concentrated Loads

1)   The specified live load due to possible concentrations of load resulting from the use of an area of floor or roof shall not be less than that listed in Table 4.1.5.9. applied over the loaded area noted and located so as to cause maximum effects, except that for occupancies not listed in Table 4.1.5.9., the concentrations of load shall be determined in accordance with Article 4.1.5.2.

Table 4.1.5.9.

Specified Concentrated Live Loads on an Area of Floor or Roof

Forming Part of Sentence 4.1.5.9.(1)

| Area of Floor or Roof | Minimum Specified Concentrated Load, kN | Loaded Area, mm × mm |
| --- | --- | --- |
| Roof surfaces | 1.3 | 200 × 200 |
| Floors of classrooms | 4.5 | 750 × 750 |
| Floors of offices, manufacturing buildings, hospital wards and stages | 9.0 | 750 × 750 |
| Floors and areas used by vehicles not exceeding 4 000 kg gross weight | 18 | 120 × 120 |
| Floors and areas used by vehicles exceeding 4 000 kg but not exceeding 9 000 kg gross weight | 36 | 120 × 120 |
| Floors and areas used by vehicles exceeding 9 000 kg gross weight | 54(1) | 250 × 600(1) |
| Driveways and sidewalks over areaways and basements | 54(1) | 250 × 600(1) |

Notes to Table 4.1.5.9.:

(1) See Note A-Table 4.1.5.9.

4.1.5.10. Sway Forces in Assembly Occupancies

1)   The floor assembly and other structural elements that support fixed seats in any building used for assembly occupancies accommodating large numbers of people at one time, such as grandstands, stadia and theatre balconies, shall be designed to resist a horizontal force equal to not less than 0.3 kN for each metre length of seats acting parallel to each row of seats, and not less than 0.15 kN for each metre length of seats acting at right angles to each row of seats, based on the assumption that these forces are acting independently of each other.

4.1.5.11. Crane-Supporting Structures and Impact of Machinery and Equipment

(See Note A-4.1.5.11.)

1)   The minimum specified load due to equipment, machinery or other objects that may produce impact shall be the sum of the weight of the equipment or machinery and its maximum lifting capacity, multiplied by an appropriate factor listed in Table 4.1.5.11.

2)   Crane-supporting structures shall be designed for the appropriate load combinations listed in Article 4.1.3.2.

3)   Crane runway structures shall be designed to resist a horizontal force applied normal to the top of the rails equal to not less than 20% of the sum of the weights of the lifted load and the crane trolley (excluding other parts of the crane).

4)   The force described in Sentence (3) shall be equally distributed on each side of the runway and shall be assumed to act in either direction.

5)   Crane runway structures shall be designed to resist a horizontal force applied parallel to the top of the rails equal to not less than 10% of the maximum wheel loads of the crane.

Table 4.1.5.11.

Factors for the Calculation of Impact Loads

Forming Part of Sentence 4.1.5.11.(1)

| Cause of Impact | Factor |
| --- | --- |
| Operation of cab or radio-operated cranes | 1.25 |
| Operation of pendant or hand-operated cranes | 1.10 |
| Operation of elevators | (1) |
| Supports for light machinery, shaft or motor-driven | 1.20 |
| Supports for reciprocating machinery (e.g., compressors) | 1.50 |
| Supports for power-driven units (e.g., piston engines) | 1.50 |

Notes to Table 4.1.5.11.:

(1) See the Safety Standards Act and pursuant regulations.

4.1.5.12. Bleachers

1)   Bleacher seats shall be designed for a uniformly distributed live load of 1.75 kN for each linear metre or for a concentrated load of 2.2 kN distributed over a length of 0.75 m, whichever produces the most critical effect on the supporting members.

2)   Bleachers shall be checked by the erector after erection to ensure that all structural members, including bracing specified in the design, have been installed.

3)   Telescopic bleachers shall be provided with locking devices to ensure stability while in use.

4.1.5.13. Helicopter Landing Areas

1)   Helicopter landing areas on roofs shall be constructed in conformance with the requirements for heliports contained in TC SOR/96-433, “Canadian Aviation Regulations – Part III.”

4.1.5.14. Loads on Guards and Handrails

(See Note A-4.1.5.14. and 4.1.5.15.(1).)

1)   The minimum horizontal specified live load applied outward at the minimum required height of every required guard shall be

a)   3.0 kN/m for open viewing stands without fixed seats and for means of egress in grandstands, stadia, bleachers and arenas,

b)   1.0 kN applied at any point, so as to produce the most critical effect, for access ways to equipment platforms, contiguous stairs and similar areas where the gathering of many people is improbable, and

c)   0.75 kN/m or 1.0 kN applied at any point so as to produce the most critical effect, whichever governs, for locations other than those described in Clauses (a) and (b).

2)   The minimum horizontal specified live load applied inward at the minimum required height of every required guard shall be half that specified in Sentence (1).

3)   Individual elements within the guard, including solid panels and pickets, shall be designed for a horizontal specified live load of 0.5 kN applied outward over an area of 100 mm by 100 mm located at any point on the element or elements so as to produce the most critical effect.

4)   The size of the opening between any two adjacent vertical elements within a guard shall not exceed the limits required by Part 3 when each of these elements is subjected to a horizontal specified live load of 0.1 kN applied in opposite directions in the in-plane direction of the guard so as to produce the most critical effect.

5)   The specified live loads required in Sentence (3) need not be considered to act simultaneously with the loads provided for in Sentences (1), (2), (6) and (7).

6)   The minimum specified live load applied vertically at the top of every required guard shall be 1.5 kN/m and need not be considered to act simultaneously with the horizontal specified live load provided for in Sentences (1), (3) and (7).

7)   Handrails and their supports shall be designed and constructed to withstand the following minimum specified live loads, which need not be considered to act simultaneously:

a)   0.9 kN applied at any point and in any direction for all handrails, and

b)   0.7 kN/m applied in any direction for handrails not located within dwelling units.

4.1.5.15. Loads on Vehicle Guardrails

1)   Vehicle guardrails shall be designed for a concentrated load of 22 kN applied horizontally outward at any point 500 mm above the floor surface so as to produce the most critical effect. (See Note A-4.1.5.14. and 4.1.5.15.(1).)

2)   The loads required in Sentence (1) need not be considered to act simultaneously with the loads provided for in Article 4.1.5.14.

4.1.5.16. Loads on Walls Acting As Guards

1)   Where the floor elevation on one side of a wall, including a wall around a shaft, is more than 600 mm higher than the elevation of the floor or ground on the other side, the wall shall be designed to resist the appropriate outward lateral design loads prescribed elsewhere in Subsection 4.1.5. or 0.5 kPa acting outward, whichever produces the more critical effect.

4.1.5.17. Firewalls

(See Note A-4.1.5.17.)

1)   Firewalls shall be designed to resist the maximum effect due to

a)   the appropriate lateral design loads prescribed elsewhere in this Section, or

b)   a factored lateral load of 0.5 kPa under fire conditions, as described in Sentence (2).

2)   Under fire conditions, where the fire-resistance rating of the structure is less than that of the firewall,

a)   lateral support shall be assumed to be provided by the structure on one side only, or

b)   another structural support system capable of resisting the loads imposed by a fire on either side of the firewall shall be provided.

4.1.6. Loads Due to Snow and Rain

4.1.6.1. Specified Load Due to Rain or to Snow and Associated Rain

1)   The specified load on a roof or any other building surface subject to snow and associated rain shall be the snow load specified in Article 4.1.6.2., or the rain load specified in Article 4.1.6.4., whichever produces the more critical effect. (See Note A-4.1.6.1.(1).)

4.1.6.2. Specified Snow Load

(See Note A-4.1.6.2.)

1)   The specified load, S, due to snow and associated rain accumulation on a roof or any other building surface subject to snow accumulation shall be calculated using the formula

where

Is   = importance factor for snow load, as provided in Table 4.1.6.2.-A,

Ss   = 1-in-50-year ground snow load, in kPa, determined in accordance with Subsection 1.1.3.,

Cb   = basic roof snow load factor in Sentence (2),

Cw   = wind exposure factor in Sentences (3) and (4),

Cs   = slope factor in Sentences (5) to (7),

Ca   = accumulation factor in Sentence (8), and

Sr   = 1-in-50-year associated rain load, in kPa, determined in accordance with Subsection 1.1.3., but not greater than Ss(C bCwCsCa).

Table 4.1.6.2.-A

Importance Factor for Snow Load, IS

Forming Part of Sentence 4.1.6.2.(1)

| Importance Category | Importance Factor, Is |  |
| --- | --- | --- |
|  | ULS | SLS |
| Low | 0.8 | 0.9 |
| Normal | 1 | 0.9 |
| High | 1.15 | 0.9 |
| Post-disaster | 1.25 | 0.9 |

2)   The basic roof snow load factor, Cb, shall

a)   be determined as follows:

i)

ii)

where

lc   = characteristic length of the upper or lower roof, defined as 2w − w2/l, in m,

w   = smaller plan dimension of the roof, in m, and

l   = larger plan dimension of the roof, in m,

b)   conform to Table 4.1.6.2.-B, using linear interpolation for intermediate values of , or

c)   be taken as equal to 1 for any roof structure with a mean height of less than 1 + Ss/γ, in m, above grade, where γ is the specific weight of snow determined in accordance with Article 4.1.6.13.

(See Note A-4.1.6.2.(2).)

3)   Except as provided for in Sentence (4), the wind exposure factor, Cw, shall be 1.0.

4)   For buildings in the Low and Normal Importance Categories as set out in Table 4.1.2.1., the wind exposure factor, Cw, given in Sentence (3) may be reduced to 0.75 for rural areas only, or to 0.5 for exposed areas north of the treeline, where

a)   the building is exposed on all sides to wind over open terrain as defined in Clause 4.1.7.3.(5)(a), and is expected to remain so during its life,

b)   the area of roof under consideration is exposed to the wind on all sides with no significant obstructions on the roof, such as parapet walls, within a distance of at least 10 times the difference between the height of the obstruction and CbCwSs/γ, in m, where γ is the specific weight of snow on roofs as specified in Article 4.1.6.13., and

c)   the loading does not involve the accumulation of snow due to drifting from adjacent surfaces.

5)   Except as provided for in Sentences (6) and (7), the slope factor, Cs, shall be

a)   1.0 where the roof slope, α, is equal to or less than 30°,

b)   (70° − α)/40° where α is greater than 30° but not greater than 70°, and

c)   0 where α exceeds 70°.

Table 4.1.6.2.-B

Basic Roof Snow Load Factor for

Forming Part of Sentence 4.1.6.2.(2)

| Value of | Value of Cw |  |  |
| --- | --- | --- | --- |
|  | 1.0 | 0.75 | 0.5 |
|  | Value of Cb |  |  |
| 70 | 0.80 | 0.80 | 0.80 |
| 80 | 0.82 | 0.85 | 0.91 |
| 100 | 0.85 | 0.94 | 1.11 |
| 120 | 0.88 | 1.01 | 1.27 |
| 140 | 0.90 | 1.07 | 1.40 |
| 160 | 0.92 | 1.12 | 1.51 |
| 180 | 0.93 | 1.16 | 1.60 |
| 200 | 0.95 | 1.19 | 1.67 |
| 220 | 0.96 | 1.21 | 1.73 |
| 240 | 0.96 | 1.24 | 1.78 |
| 260 | 0.97 | 1.25 | 1.82 |
| 280 | 0.98 | 1.27 | 1.85 |
| 300 | 0.98 | 1.28 | 1.88 |
| 320 | 0.98 | 1.29 | 1.90 |
| 340 | 0.99 | 1.30 | 1.92 |
| 360 | 0.99 | 1.30 | 1.93 |
| 380 | 0.99 | 1.31 | 1.95 |
| 400 | 0.99 | 1.31 | 1.96 |
| 420 | 0.99 | 1.32 | 1.96 |
| 440 | 1.00 | 1.32 | 1.97 |
| 460 | 1.00 | 1.32 | 1.98 |
| 480 | 1.00 | 1.32 | 1.98 |
| 500 | 1.00 | 1.33 | 1.98 |
| 520 | 1.00 | 1.33 | 1.99 |
| 540 | 1.00 | 1.33 | 1.99 |
| 560 | 1.00 | 1.33 | 1.99 |
| 580 | 1.00 | 1.33 | 1.99 |
| 600 | 1.00 | 1.33 | 1.99 |
| 620 | 1.00 | 1.33 | 2.00 |

6)   The slope factor, Cs, for unobstructed slippery roofs where snow and ice can slide completely off the roof shall be

a)   1.0 where the roof slope, α, is equal to or less than 15°,

b)   (60° − α)/45° where α is greater than 15° but not greater than 60°, and

c)   0 where α exceeds 60°.

7)   Unless otherwise stated in this Subsection, the slope factor, Cs, shall be 1.0 when used in conjunction with accumulation factors for increased snow loads.

8)   The accumulation factor, Ca, shall be 1.0, which corresponds to the uniform snow load case, except that where appropriate for the shape of the roof, it shall be assigned other values that account for

a)   increased non-uniform snow loads due to snow drifting onto a roof that is at a level lower than other parts of the same building or at a level lower than another building within 5 m of it horizontally, as prescribed in Articles 4.1.6.5., 4.1.6.6. and 4.1.6.8.,

b)   increased non-uniform snow loads on areas adjacent to roof projections, such as penthouses, large chimneys and equipment, as prescribed in Articles 4.1.6.7. and 4.1.6.8.,

c)   non-uniform snow loads on gable, arch or curved roofs and domes, as prescribed in Articles 4.1.6.9. and 4.1.6.10.,

d)   increased snow or ice loads due to snow sliding as prescribed in Article 4.1.6.11.,

e)   increased snow loads in roof valleys, as prescribed in Article 4.1.6.12., and

f)   increased snow or ice loads due to meltwater draining from adjacent building elements and roof projections.

9)   For shapes not addressed in Sentence (8), Ca corresponding to the non-uniform snow load case shall be established based on applicable field observations, special analyses including local climatic effects, appropriate model tests, or a combination of these methods.

4.1.6.3. Full and Partial Loading

1)   A roof or other building surface and its structural members subject to loads due to snow accumulation shall be designed for the specified load given in Sentence 4.1.6.2.(1), distributed over the entire loaded area.

2)   In addition to the distribution mentioned in Sentence (1), flat roofs and shed roofs, gable roofs of 15° slope or less, and arch or curved roofs shall be designed for the specified uniform snow load indicated in Sentence 4.1.6.2.(1), which shall be calculated using the accumulation factor Ca = 1.0, distributed on any one portion of the loaded area and half of this load on the remainder of the loaded area, in such a way as to produce the most critical effects on the member concerned. (See Note A-4.1.6.3.(2).)

4.1.6.4. Specified Rain Load

1)   Except as provided in Sentence (4), the specified load, S, due to the accumulation of rainwater on a surface whose position, shape and deflection under load make such an accumulation possible, is that resulting from the one-day rainfall determined in conformance with Subsection 1.1.3. and applied over the horizontal projection of the surface and all tributary surfaces. (See Note A-4.1.6.4.(1).)

2)   The provisions of Sentence (1) apply whether or not the surface is provided with a means of drainage, such as rainwater leaders.

3)   Except as provided in Sentence 4.1.6.2.(1), loads due to rain need not be considered to act simultaneously with loads due to snow. (See Note A-4.1.6.4.(3).)

4)   Where scuppers are provided as secondary drainage systems and where the position, shape and deflection of the loaded surface make an accumulation of rainwater possible, the loads due to rain shall be the lesser of either the one-day rainfall determined in conformance with Subsection 1.1.3. or a depth of rainwater equal to 30 mm above the bottom of the scuppers, applied over the horizontal projection of the surface and tributary areas.

4.1.6.5. Multi-level Roofs

1)   The drifting load of snow on a roof adjacent to a higher roof shall be taken as trapezoidal, as shown in Figure 4.1.6.5.-A, and the accumulation factor, Ca, shall be determined as follows:

where

Ca0   = peak value of Ca at x = 0 determined in accordance with Sentences (3) to (5) and as shown in Figure 4.1.6.5.-B,

x   = distance from roof step as shown in Figure 4.1.6.5.-A, and

xd   = length of drift determined in accordance with Sentence (2) and as shown in Figure 4.1.6.5.-A.

2)   The length of the drift, xd, shall be calculated as follows:

where

γ   = specific weight of snow as specified in Article 4.1.6.13.

Figure 4.1.6.5.-A

Snow load factors for lower level roofs

Forming Part of Sentences 4.1.6.5.(1) and (3), Table 4.1.6.5.-A and Sentence 4.1.6.6.(1)

Notes to Figure 4.1.6.5.-A:

(1) If a > 5 m or h ≤ 0.8Ss/γ, drifting from the higher roof need not be considered.

(2) If h ≥ 5 m, the value of Ca0 for Case I is permitted to be determined in accordance with Sentence 4.1.6.5.(4).

Table 4.1.6.5.-A

Wind Exposure, Slope and Accumulation Factors in Figure 4.1.6.5.-A

| Distance from Roof Step, x | Factors |  |  |
| --- | --- | --- | --- |
|  | Cw | Cs(1) | Ca |
| 0 | 1.0 | f(α) | Ca0 |
| 0 < x ≤ xd | 1.0 | f(α) | Ca0 − (Ca0 − 1)(x/xd) |
| xd < x ≤ 10h′ | 1.0 | f(α) | 1.0 |
| x> 10h′ | 1.0 for unexposed roof areas | f(α) | 1.0 |
|  | 0.75 for exposed roof areas |  |  |
|  | 0.5 for exposed roof areas north of tree line |  |  |

Notes to Table 4.1.6.5.-A:

(1) For lower roofs with parapets, Cs = 1.0; otherwise, Cs varies as a function of slope, α, as defined in Sentences 4.1.6.2.(5) and (6).

3)   Except as provided in Sentence (4), the value of Ca0 for each of Cases I, II and III shall be the lesser of

where

β   = 1.0 for Case I, and 0.67 for Cases II and III,

h   = difference in elevation between the lower roof surface and the top of the parapet on the upper roof as shown in Figure 4.1.6.5.-A, and

where

Cws   = value of Cw applicable to the source of drifting,

lcs   = characteristic length of the source area for drifting, defined as , where ws and ls are respectively the shorter and longer dimensions of the relevant source areas for snow drifting shown in Figure 4.1.6.5.-B for Cases I, II and III, and

where

hp   = height of the roof perimeter parapet of the source area, to be taken as zero unless all the roof edges of the source area have parapets.

4)   Where h ≥ 5 m, the value of Ca0 for Case I is permitted to be taken as

5)   The value of Ca0 shall be the highest of Cases I, II and III, considering the different roof source areas for drifting snow, as specified in Sentences (3) and (4) and Figure 4.1.6.5.-B.

Figure 4.1.6.5.-B

Snow load cases I, II and III for lower level roofs

Forming Part of Sentences 4.1.6.5.(1), (3) and (5), and Table 4.1.6.5.-B

Table 4.1.6.5.-B

Parameters for Snow Load Cases in Figure 4.1.6.5.-B

| Parameter | Case I | Case II | Case III |
| --- | --- | --- | --- |
| β | 1.0 | 0.67 | 0.67 |
| hp | parapet height of upper-roof source area | parapet height of lower-roof source area | parapet height of lower-roof source area |
|  | with ws and ls being the shorter and longer dimensions of the upper roof | with ws and ls being the shorter and longer dimensions of the source area on the lower roof for upwind-facing step | with ws and ls being the shorter and longer dimensions of the source area on the lower roof for downwind-facing step |

4.1.6.6. Horizontal Gap between a Roof and a Higher Roof

1)   Where the roof of one building is separated by a distance, a, from an adjacent building with a higher roof as shown in Figure 4.1.6.5.-A, the influence of the adjacent building on the value of the accumulation factor, Ca, for the lower roof shall be determined as follows:

a)   if a > 5 m, the influence of the adjacent building on Ca for the lower roof can be ignored, and

b)   if a ≤ 5 m, Ca for the lower roof shall be calculated in accordance with Article 4.1.6.5. for values of x ≥ a.

4.1.6.7. Areas Adjacent to Roof Projections

1)   Except as provided in Sentences (2) and (3), the accumulation factor, Ca, for areas adjacent to roof-mounted vertical projections shall be calculated in accordance with Sentence 4.1.6.5.(1) using the following values for the peak accumulation factor, Ca0, and the drift length, xd:

a)   Ca0 shall be taken as the lesser of

b)   xd shall be taken as the lesser of 3.35h and (2/3)l0, where

h   = height of the projection, and

l0   = longest horizontal dimension of the projection.

(See Note A-4.1.6.7.(1).)

2)   Ca is permitted to be calculated in accordance with Article 4.1.6.5. for larger projections. (See Note A-4.1.6.7.(2).)

3)   Where the longest horizontal dimension of the roof projection, l0, is less than 3 m, the drift surcharge adjacent to the projection need not be considered.

4.1.6.8. Snow Drift at Corners

1)   The drift loads on the lower level roof against the two faces of an outside corner of an upper level roof or roof obstruction shall be extended radially around the corner as shown in Figure 4.1.6.8.-A and may be taken as the least severe of the drift loads lying against the two faces of the corner.

2)   The drift loads on the lower level roof against the two faces of an inside corner of an upper level roof or a parapet shall be calculated for each face and the higher of the two loads shall be applied where the drifts overlap as shown in Figure 4.1.6.8.-B

Figure 4.1.6.8.-A

Snow load at outside corner

Forming Part of Sentence 4.1.6.8.(1)

Figure 4.1.6.8.-B

Snow load at inside corner

Forming Part of Sentence 4.1.6.8.(2)

4.1.6.9. Gable Roofs

(See Note A-4.1.6.9.)

1)   For all gable roofs, the full and partial load cases defined in Article 4.1.6.3. shall be considered.

2)   For gable roofs with a slope α > 15°, the unbalanced load case shall also be considered by setting the values of the accumulation factor, Ca, as follows:

a)   on the upwind side of the roof peak, Ca shall be taken as 0, and

b)   on the downwind side of the roof peak, Ca shall be taken as

i)   0.25 + α/20, where 15° ≤ α ≤ 20°, and

ii)   1.25, where 20° < α ≤ 90°.

3)   For all gable roofs, the slope factor, Cs, shall be as prescribed in Sentences 4.1.6.2.(5) and (6).

4)   For all gable roofs, the wind exposure factor, Cw, shall be

a)   as prescribed in Sentences 4.1.6.2.(3) and (4) for the full and partial load cases, and

b)   1.0 for the unbalanced load case referred to in Sentence (2).

4.1.6.10. Arch Roofs, Curved Roofs and Domes

1)   For all arch roofs, curved roofs and domes, the full and partial load cases defined in Article 4.1.6.3. shall be considered.

2)   For arch roofs, curved roofs and domes with a rise-to-span ratio h/b > 0.05 (see Figure 4.1.6.10.-A), the load cases provided in Sentences (3) to (7) shall also be considered.

3)   For arch roofs with a slope at the edge αe ≤ 30° (see Figure 4.1.6.10.-A and Table 4.1.6.10.), Ca shall be

a)   taken as 0 on the upwind side of the peak, and

b)   on the downwind side of the peak, taken as

where

x   = horizontal distance from the roof peak,

h   = height of arch, and

b   = width of arch.

Figure 4.1.6.10.-A

Accumulation factors for arch roofs and curved roofs

Forming Part of Sentences 4.1.6.10.(2) to (4)

Note to Figure 4.1.6.10.-A:

(1) Refer to Table 4.1.6.10. for applicable values of Cw and Sentences 4.1.6.2.(5) and (6) for applicable values of Cs.

4)   For arch roofs with a slope at the edge αe > 30° (see Figure 4.1.6.10.-A and Table 4.1.6.10.), Ca shall be

a)   taken as 0 on the upwind side of the peak, and

b)    on the downwind side of the peak,

i)   for the part of the roof between the peak and point where the slope α = 30°, taken as

where

x, h, b   = as specified in Sentence (2), and

x30   = value of x where the slope α = 30°, and

ii)   for the part of the roof where the slope α > 30°, taken as

5)   Except as provided in Sentence (6), Ca for curved roofs shall be determined in accordance with the requirements for arch roofs stated in Sentences (3) and (4).

Table 4.1.6.10.

Load Cases for Arch Roofs, Curved Roofs and Domes

Forming Part of Sentences 4.1.6.10.(3), (4) and (9)

| Load Case | Range of Application | Factors |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  |  | All Arch or Curved Roofs and Domes | Arch and Curved Roofs |  | Domes |
|  |  | Cw | Ca Upwind Side | Ca Downwind Side | Ca Downwind Side |
| Case I | All values of h/b | As stated in 4.1.6.2.(3) and (4) | 1.0 | 1.0 | 1.0 |
| Case II | Slope at edge ≤ 30° h/b > 0.05 all values of x | 1.0 | 0.0 |  |  |
|  | Slope at edge > 30° h/b > 0.05 0 < x < x30 | 1.0 | 0.0 |  |  |
|  | Slope at edge > 30° h/b > 0.05 x ≥ x30 | 1.0 | 0.0 |  |  |

6)   Where the slope, α, of a curved roof at its peak is greater than 10°, Ca shall be determined in accordance with the requirements for gable roofs stated in Article 4.1.6.9. using a slope equal to the mean slope of the curved roof.

7)   For domes of circular plan form (see Figure 4.1.6.10.-B), Ca shall

a)   along the central axis parallel to the wind, vary in the same way as for an arch roof with the same rise-to-span ratio, h/b, and

b)   off this axis, vary according to

where

Ca(x,y)   = value of Ca at location (x,y),

Ca(x,0)   = value of Ca on the central axis parallel to the wind,

x   = distance along the central axis parallel to the wind,

y   = horizontal coordinate normal to the x direction, and

r   = radius of dome.

8)   For all arch roofs, curved roofs and domes, the slope factor, Cs, shall be as prescribed in Sentences 4.1.6.2.(5) and (6).

9)   For all arch roofs, curved roofs and domes, the wind exposure factor, Cw, shall be as prescribed in Table 4.1.6.10.

Figure 4.1.6.10.-B

Unbalanced snow accumulation factor on a circular dome

Forming Part of Sentence 4.1.6.10.(7)

Notes to Figure 4.1.6.10.-B:

(1) Refer to Table 4.1.6.10. for applicable values of Cw and Sentences 4.1.6.2.(5) and (6) for applicable values of Cs.

(2) Refer to Sentences 4.1.6.10.(3) and (4) for the calculation of Ca(x,0).

4.1.6.11. Snow Loads Due to Sliding

1)   Except as provided in Sentence (2), where an upper roof, or part thereof, slopes downwards with a slope α > 0 towards a lower roof, the snow load, S, on the lower roof, determined in accordance with Articles 4.1.6.2. and 4.1.6.5., shall be augmented in accordance with Sentence (3) to account for the additional load resulting from sliding snow.

2)   Sentence (1) need not apply where

a)   snow from the upper roof is prevented from sliding by a parapet or other effective means, or

b)   the upper roof is not considered slippery and has a slope of less than 20°.

3)   The total weight of additional snow resulting from sliding shall be taken as half the total weight of snow resulting from the uniform load case prescribed in Article 4.1.6.2. with

a)   the accumulation factor Ca = 1.0 for the relevant part of the upper roof,

b)   the slope factor, Cs, based on the slope of the lower roof, as prescribed in Sentences 4.1.6.2.(5) and (6), and

c)   the sliding snow distributed on the lower roof such that it is a maximum for x = 0 and decreases linearly to 0 at x = xd, as shown in Figure 4.1.6.11., where x and xd are as defined in Article 4.1.6.5.

Figure 4.1.6.11.

Snow distribution on lower roof with sloped upper roof

Forming Part of Sentence 4.1.6.11.(3)

4.1.6.12. Valleys in Curved or Sloped Roofs

1)   For valleys in curved or sloped roofs with a slope α > 10°, in addition to the full and partial load cases defined in Article 4.1.6.3., the non-uniform load cases II and III presented in Sentences (2) and (3) shall be considered to account for sliding, creeping and movement of meltwater.

2)   For case II (see Figure 4.1.6.12.), the accumulation factor, Ca, shall be calculated as follows:

where

x   = horizontal distance from the bottom of the valley, and

b   = twice the horizontal distance between the bottom of the valley and the peak of the roof surface in question.

3)   For case III (see Figure 4.1.6.12.), Ca shall be calculated as follows:

where

x, b   = as specified in Sentence (2).

Figure 4.1.6.12.

Snow loads in valleys of sloped or curved roofs

Forming Part of Sentences 4.1.6.12.(2) and (3)

Notes to Figure 4.1.6.12.:

(1) Cw = 1, as per Sentence 4.1.6.2.(3).

(2) Cs = 1, as per Sentence 4.1.6.2.(7).

4.1.6.13. Specific Weight of Snow

1)   For the purposes of calculating snow loads in drifts, the specific weight of snow, γ, shall be taken as 4.0 kN/m3 or 0.43SS + 2.2 kN/m3, whichever is lesser.

4.1.6.14. Snow Removal

1)   Snow removal by mechanical, thermal, manual or other means shall not be used as a rationale to reduce design snow loads.

4.1.6.15. Ice Loading of Structures

1)   For lattice structures connected to the building, and other building components or appurtenances involving small width elements subject to significant ice accretion, the weight of ice accretion and the effective area presented to wind shall be as prescribed in CAN/CSA-S37, “Antennas, towers, and antenna-supporting structures.”

4.1.6.16. Roofs with Solar Panels

(See Note A-4.1.6.16.)

1)   Where solar panels are installed on a roof, the snow loads, S, shall be determined in accordance with Sentences (2) to (6) or with the requirements for roofs without solar panels, whichever produces the most critical effect.

2)   For the purposes of this Article, solar panels shall be classified as

a)   Parallel Flush, where the panels are installed parallel to the roof surface with their upper surface less than or equal to CbCwSs/γ above the roof surface,

b)   Parallel Raised, where the panels are installed parallel to the roof surface with their upper surface greater than CbCwSs/γ above the roof surface, or

c)   Tilted, where the panels are installed at an angle to the roof surface with their highest edge greater than CbCwSs/γ above the roof surface.

3)   For sloped roofs with solar panels, the snow loads, S, shall be determined in accordance with the requirements for roofs without solar panels, except that the slope factor, Cs, shall be

a)   taken as 1.0 for roof areas extending upslope from the downslope edge of a panel or array of panels at an angle of 45° from each side edge of the panel or array, and

b)   as specified in Sentences 4.1.6.2.(5) to (7) for all other roof areas.

(See Note A-4.1.6.16.(3).)

4)   For sloped roofs with Parallel Flush solar panels, the snow loads, S, shall be determined in accordance with the requirements for roofs without solar panels, except that

a)   Cs shall be determined in accordance with Sentence (3),

b)   where the gap width, wg, between the panels along the roof slope is greater than or equal to the panel width, wp, along the roof slope, the accumulation factor, Ca, shall be taken as

i)   0.0 for the panels,

ii)   2.0 for roof areas within a distance of wp downslope from a downslope panel edge, and

iii)   1.0 for all other roof areas

(see Note A-4.1.6.16.(4)(b)), and

c)   where the gap width, wg, between the panels along the roof slope is less than the panel width, wp, along the roof slope, Ca shall be taken as

i)   0.0 for panel areas within a distance of wg downslope from an upslope panel edge,

ii)   1.0 for other panel areas,

iii)   2.0 for roof areas in gaps between the panels, and

iv)   1.0 for all other roof areas

(see Note A-4.1.6.16.(4)(c)).

5)   For roofs with Parallel Raised solar panels, the snow loads, S, shall be determined in accordance with the requirements for roofs without solar panels, except that

a)   where the roof is flat, Ca shall be taken as

i)   1.0 for the panels,

ii)   1.0 for roof areas not under the panels,

iii)   1.0 for roof areas under the panels within a distance of min(2hg,2wg) from a panel edge, where hg is the gap height between the lower surface of the panels and the roof surface, and wg is the gap width between the panels, and

iv)   0.0 for other roof areas under the panels

(see Note A-4.1.6.16.(5)(a)), and

b)   where the roof is sloped, the snow loads, S, derived from Clause (a) shall be used, except that

i)   Cs shall be determined in accordance with Sentence (3),

ii)   S shall be taken as 0.0 on the panels, and

iii)   S for all roof areas shall be taken as the sum of S on the panels, as derived from Subclause (a)(i) and shifted by a distance of wp downslope onto the roof, where wp is the panel width along the roof slope, and S on the roof areas, as derived from Subclauses (a)(ii) to (a)(iv)

(see Note A-4.1.6.16.(5)(b)).

6)   For flat roofs with Tilted solar panels, the snow loads, S, shall be determined in accordance with the requirements for roofs without solar panels, except that

a)   Ca shall be taken as 0.0 for the panels,

b)   Ca shall be taken as 1.0 for roof areas beyond a distance of 5(h – CbCwSs/γ) from the lowest edge of the panels, where h is the height of the highest edge of the panels above the roof surface,

c)   except as provided in Clauses (d) and (e), for roof areas within a distance of 5(h – CbCwSs/γ) from the lowest edge of the panels, Ca shall be taken as

i)   1.25 for (hg – CbCwSs/γ) ≤ 0.3 m, where hg is the gap height between the lowest edge of the panels and the roof surface,

ii)   1.294 – 0.1471(hg – CbCwSs/γ) for 0.3 < (hg – CbCwSs/γ) ≤ 2.0 m, and

iii)   1.0 for (hg – CbCwSs/γ) > 2.0 m

(see Note A-4.1.6.16.(6)(c)),

d)   except as provided in Clause (e), Ca shall be taken as 2.0 for roof areas within a distance of wph beyond the lowest edge of the panels, where wph is the horizontal projection of the panel width, wp, along the sloped panel edges, and

e)   where the panels, panel supports or back plates obstruct snow from sliding under the panels, the load of the increased volume of snow in the gaps between the panels shall be considered to be uniformly distributed.

(See Note A-4.1.6.16.(6).)

4.1.7. Wind Load

4.1.7.1. Specified Wind Load

1)   The specified wind loads for a building and its components shall be determined using the Static, Dynamic or Wind Tunnel Procedure as stated in Sentences (2) to (5).

2)   For the design of buildings that are not dynamically sensitive, as defined in Sentence 4.1.7.2.(1), one of the following procedures shall be used to determine the specified wind loads:

a)   the Static Procedure described in Article 4.1.7.3.,

b)   the Dynamic Procedure described in Article 4.1.7.8., or

c)   the Wind Tunnel Procedure described in Article 4.1.7.14.

3)   For the design of buildings that are dynamically sensitive, as defined in Sentence 4.1.7.2.(2), one of the following procedures shall be used to determine the specified wind loads:

a)   the Dynamic Procedure described in Article 4.1.7.8., or

b)   the Wind Tunnel Procedure described in Article 4.1.7.14.

4)   For the design of buildings that may be subject to wake buffeting or channelling effects from nearby buildings, or that are very dynamically sensitive, as defined in Sentence 4.1.7.2.(3), the Wind Tunnel Procedure described in Article 4.1.7.14., shall be used to determine the specified wind loads.

5)   For the design of cladding and secondary structural members, one of the following procedures shall be used to determine the specified wind loads:

a)   the Static Procedure described in Article 4.1.7.3., or

b)   the Wind Tunnel Procedure described in Article 4.1.7.14.

6)   Computational fluid dynamics shall not be used to determine the specified wind loads for a building and its components. (See Note A-4.1.7.1.(6).)

4.1.7.2. Classification of Buildings

(See Note A-4.1.7.2.(2))

1)   Except as provided in Sentences (2) and (3), a building is permitted to be classified as not dynamically sensitive.

2)   A building shall be classified as dynamically sensitive if

a)   its lowest natural frequency is less than 1 Hz and greater than 0.25 Hz,

b)   its height is greater than 60 m, or

c)   its height is greater than 4 times its minimum effective width, where the effective width, w, of a building shall be taken as

where the summations are over the height of the building for a given wind direction, hi is the height above grade to level i, and wi is the width normal to the wind direction at height hi; the minimum effective width is the lowest value of the effective width considering all wind directions.

3)   A building shall be classified as very dynamically sensitive if

a)   its lowest natural frequency is less than or equal to 0.25 Hz, or

b)   it contains a human occupancy, and its height is more than 6 times its minimum effective width as defined in Clause (2)(c).

4.1.7.3. Static Procedure

1)   The specified external pressure or suction due to wind on part or all of a surface of a building shall be calculated as follows:

where

p   = specified external pressure acting statically and in a direction normal to the surface, considered positive when the pressure acts towards the surface and negative when it acts away from the surface,

IW   = importance factor for wind load, as provided in Table 4.1.7.3.,

q   = reference velocity pressure, as provided in Sentence (4),

Ce   = exposure factor, as provided in Sentences (5) and (7),

Ct   = topographic factor, as provided in Article 4.1.7.4.,

Cg   = gust effect factor, as provided in Sentence (8), and

Cp   = external pressure coefficient, as provided in Articles 4.1.7.5. and 4.1.7.6.

Table 4.1.7.3.

Importance Factor for Wind Load, IW

Forming Part of Sentences 4.1.7.3.(1) and 4.1.7.8.(4)

| Importance Category | Importance Factor, IW |  |
| --- | --- | --- |
|  | ULS | SLS |
| Low | 0.8 | 0.75 |
| Normal | 1 | 0.75 |
| High | 1.15 | 0.75 |
| Post-disaster | 1.25 | 0.75 |

2)   The net wind load for the building as a whole shall be the algebraic difference of the loads on the windward and leeward surfaces, and in some cases, may be calculated as the sum of the products of the external pressures or suctions and the areas of the surfaces over which they are averaged as provided in Sentence (1).

3)   The net specified pressure due to wind on part or all of a surface of a building shall be the algebraic difference, such as to produce the most critical effect, of the external pressure or suction calculated in accordance with Sentence (1) and the specified internal pressure or suction due to wind calculated as follows:

where

pi   = specified internal pressure acting statically and in a direction normal to the surface, either as a pressure directed towards the surface or as a suction directed away from the surface,

IW, q, Ct   = as defined in Sentence (1),

Cei   = exposure factor for internal pressure, as provided in Sentence (7),

Cgi   = internal gust effect factor, as provided in Sentence (10), and

Cpi   = internal pressure coefficient, as provided in Article 4.1.7.7.

4)   The reference velocity pressure, q, shall be the appropriate value determined in conformance with Subsection 1.1.3., based on a probability of being exceeded in any one year of 1 in 50.

5)   The exposure factor, Ce, shall be based on the reference height, h, determined in accordance with Sentence (6), for the surface or part of the surface under consideration and shall be

a)   (h/10)0.2 but not less than 0.9 for open terrain, where open terrain is level terrain with only scattered buildings, trees or other obstructions, open water or shorelines thereof,

b)   0.7(h/12)0.3 but not less than 0.7 for rough terrain, where rough terrain is suburban, urban or wooded terrain extending upwind from the building uninterrupted for at least 1 km or 20 times the height of the building, whichever is greater, or

c)   an intermediate value between the two exposures defined in Clauses (a) and (b) in cases where the site is less than 1 km or 20 times the height of the building from a change in terrain conditions, whichever is greater, provided an appropriate interpolation method is used (see Note A-4.1.7.3.(5)(c)).

6)   The reference height, h, shall be determined as follows:

a)   for buildings whose height is less than or equal to 20 m and less than the smaller plan dimension, h shall be the mid-height of the roof above grade, but not less than 6 m,

b)   for other buildings, h shall be

i)   the actual height above grade of the point on the windward wall for which external pressures are being calculated,

ii)   the mid-height of the roof for pressures on surfaces parallel to the wind direction, and

iii)   the mid-height of the building for pressures on the leeward wall, and

c)   for any structural element exposed to wind, h shall be the mid-height of the element above the ground.

7)   The exposure factor for internal pressures, Cei, shall be determined as follows:

a)   for buildings whose height is greater than 20 m and that have a dominant opening, Cei shall be equal to the exposure factor for external pressures, Ce, calculated at the mid-height of the dominant opening, and

b)   for other buildings, Cei shall be the same as the exposure factor for external pressures, Ce, calculated for a reference height, h, equal to the mid-height of the building or 6 m, whichever is greater.

8)   Except as provided in Sentences (9) and 4.1.7.6.(1), the gust effect factor, Cg, shall be one of the following values:

a)   2.0 for the building as a whole and main structural members, or

b)   2.5 for external pressures and suctions on secondary structural members, including cladding.

9)   For cases where Cg and Cp are combined into a single product, CgCp, the values of Cg and Cp need not be independently specified. (See Article 4.1.7.6.)

10)   The internal gust effect factor, Cgi, shall be 2.0, except it is permitted to be calculated using the following equation for large structures enclosing a single large unpartitioned volume that does not have numerous overhead doors or openings:

where

V0   = internal volume, in m3, and

A   = total area of all exterior openings of the volume, in m2.

(See Note A-4.1.7.3.(10).)

4.1.7.4. Topographic Factor

1)   Except as provided in Sentence (2), the topographic factor, Ct, shall be taken as 1.0.

2)   For buildings on hills or escarpments with a slope, Hh/(2Lh), greater than 0.1 (see Figure 4.1.7.4.), the topographic factor, Ct, shall be calculated as follows:

where

where

ΔSmax   = applicable value from Table 4.1.7.4.,

x   = horizontal distance from the peak of the hill or escarpment,

Lh   = horizontal distance upwind from the peak to the point where the ground surface lies at half the height of the hill or escarpment, or 2Hh (where Hh = height of hill or escarpment), whichever is greater,

z   = height above ground, and

k and α   = applicable constants from Table 4.1.7.4. based on shape of hill or escarpment.

Table 4.1.7.4.

Parameters for Maximum Speed-up Over Hills and Escarpments

Forming Part of Sentence 4.1.7.4.(2)

| Shape of Hill or Escarpment | ΔSmax(1) | α | k |  |
| --- | --- | --- | --- | --- |
|  |  |  | x < 0 | x ≥ 0 |
| 2-dimensional hill | 2.2Hh/Lh | 3 | 1.5 | 1.5 |
| 2-dimensional escarpment | 1.3Hh/Lh | 2.5 | 1.5 | 4 |
| 3-dimensional axi-symmetrical hill | 1.6Hh/Lh | 4 | 1.5 | 1.5 |

Notes to Table 4.1.7.4.:

- For Hh/Lh > 0.5, assume Hh/Lh = 0.5 and substitute 2Hh for Lh in the equation for ΔS.

Figure 4.1.7.4.

Speed-up of mean velocity on a hill or escarpment

Forming Part of Sentence 4.1.7.4.(2)

Note to Figure 4.1.7.4.:

(1) V(z) = wind speed

4.1.7.5. External Pressure Coefficients

1)   Applicable values of external pressure coefficients, Cp, are provided in

a)   Sentences (2) to (9), and

b)   Article 4.1.7.6. for certain shapes of low buildings.

2)   For the design of the main structural system, the value of Cp shall be established as follows, where H is the height of the building and D is the width of the building parallel to the wind direction:

a)   on the windward face,

Cp   = 0.6 for H/D < 0.25

= 0.27(H/D + 2) for 0.25 ≤ H/D < 1.0, and

= 0.8 for H/D ≥ 1.0,

b)   on the leeward face,

Cp   = –0.3 for H/D < 0.25,

= –0.27(H/D + 0.88) for 0.25 ≤ H/D < 1.0, and

= –0.5 for H/D ≥ 1.0, and

c)   on the walls parallel to the wind, Cp = –0.7.

(See Note A-4.1.7.5.(2) and (3).)

3)   For the design of roofs, the value of Cp shall be established as follows, where x is the distance from the upwind edge of the roof:

a)   for H/D ≥ 1.0, Cp = –1.0, and

b)   for H/D < 1.0,

Cp   = –1.0 for x ≤ H, and

= –0.5 for x > H.

(See Note A-4.1.7.5.(2) and (3).)

4)   For the design of the cladding and of secondary structural elements supporting the cladding, the value of Cp shall be established as follows, where W and D are the widths of the building:

a)   on walls, Cp shall be taken as ±0.9, except that within a distance equal to the larger of 0.1D and 0.1W from a building corner, the negative value of Cp shall be taken as –1.2,

b)   on walls where vertical ribs deeper than 1 m are placed on the facade, Cp shall be taken as ±0.9, except that, within a distance equal to the larger of 0.2D and 0.2W from a building corner, the negative value of Cp shall be taken as –1.4, and

c)   on roofs, Cp shall be taken as –1.0, except that

i)   within a distance equal to the larger of 0.1D and 0.1W from a roof edge, Cp shall be taken as –1.5,

ii)   in a zone that is within a distance equal to the larger of 0.2W and 0.2D from a roof corner, Cp shall be taken as –2.3 but is permitted to be taken as –2.0 for roofs with perimeter parapets that are higher than 1 m, and

iii)   on lower levels of flat stepped roofs, positive pressure coefficients established for the walls of the steps apply for a distance b (see Figure 4.1.7.6.-D for the definition of b).

(See Note A-4.1.7.5.(4).)

5)   Except as provided in Sentence (6), for the design of balcony guards, the internal pressure coefficient, Cpi, shall be taken as zero and the value of Cp shall be taken as ±0.9, except that, within a distance equal to the larger of 0.1W and 0.1D from a building corner, Cp shall be taken as ±1.2.

6)   Where the top of the balcony guard is 2.0 m or less below the roof surface, the values of Cp shall be taken as equal to those determined for parapets in Sentences (7) and (8).

7)   To determine the contribution from parapets to the wind loads on the main structural system, the values of Cp shall be taken as

a)   on the outer faces, equal to those on the walls below,

b)   on the inner face of the windward parapet, equal to that on the upwind edge of a roof surface at the level of the top of the parapet, and

c)   on the inner faces of the other parapets, zero.

8)   For the structural design of parapets themselves, the values of Cp shall be taken as equal to those specified in Sentence (7), except that the value of Cp on the inner face of the leeward parapet shall be taken as equal to that on the outer face of the windward parapet.

9)   For the design of cladding on parapets, the values of Cp shall be taken as

a)   on the outer vertical surfaces, equal to those on the cladding on the walls below, and

b)   on the inner and top surfaces, equal to those on the cladding of a roof surface at the level of the top of the parapet.

4.1.7.6. External Pressure Coefficients for Low Buildings

1)   For the design of buildings with a height, H, that is both less than or equal to 20 m and less than the smaller plan dimension, the values of the product of the pressure coefficient and gust factor, CgCp, provided in Sentences (2) to (9) are permitted to be used.

2)   For the design of the main structural system of the building, which is affected by wind pressures on more than one surface as shown in Figure 4.1.7.6.-A, the values of CgCp are provided in Table 4.1.7.6.

Figure 4.1.7.6.-A

Primary structural actions arising from wind load acting simultaneously on all surfaces of low buildings (H ≤ 20 m)

Forming Part of Sentence 4.1.7.6.(2) and Table 4.1.7.6.

Notes to Figure 4.1.7.6.-A:

(1) The building must be designed for all wind directions. Each corner must be considered in turn as the windward corner shown in the sketches. For all roof slopes, Load Case A and Load Case B are required as two separate loading conditions to generate the wind actions, including torsion, to be resisted by the structural system.

(2) For the design of foundations, exclusive of anchorages to the frame, only 70% of the effective load is to be considered.

(3) The reference height, h, for pressures is the mid-height of the roof or 6 m, whichever is greater. The eave height, H, may be substituted for the mid-height of the roof if the roof slope is less than 7°.

(4) End-zone width y should be the greater of 6 m or 2z, where z is the width of the gable-wall end zone defined for Load Case B below. Alternatively, for buildings with frames, the end-zone width y may be the distance between the end and the first interior frame.

(5) End-zone width z is the lesser of 10% of the least horizontal dimension and 40% of height, H, but not less than 4% of the least horizontal dimension or 1 m.

(6) For B/H > 5 in Load Case A, the negative coefficients listed for surfaces 2 and 2E in Table 4.1.7.6. should only be applied on an area whose width is 2.5H measured from the windward eave. The pressures on the remainder of the windward roof should be reduced to the pressures for the leeward roof.

Table 4.1.7.6.

External Peak Values of CgCp in Figure 4.1.7.6.-A

Forming Part of Sentence 4.1.7.6.(2)

| Load Case | Roof Slope | External Peak Values of CgCp(1)(2) |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Building Surfaces |  |  |  |  |  |  |  |  |  |  |  |
|  |  | 1 | 1E | 2 | 2E | 3 | 3E | 4 | 4E | 5 | 5E | 6 | 6E |
| A | 0° to 5° | 0.75 | 1.15 | −1.3 | −2.0 | −0.7 | −1.0 | −0.55 | −0.8 | – | – | – | – |
|  | 20° | 1.0 | 1.5 | −1.3 | −2.0 | −0.9 | −1.3 | −0.8 | −1.2 | – | – | – | – |
|  | 30° to 45° | 1.05 | 1.3 | 0.4 | 0.5 | −0.8 | −1.0 | −0.7 | −0.9 | – | – | – | – |
|  | 90° | 1.05 | 1.3 | 1.05 | 1.3 | −0.7 | −0.9 | −0.7 | −0.9 | – | – | – | – |
| B | 0° to 90° | −0.85 | −0.9 | −1.3 | −2.0 | −0.7 | −1.0 | −0.85 | −0.9 | 0.75 | 1.15 | −0.55 | −0.8 |

Notes to Table 4.1.7.6.:

(1) For values of roof slope not shown, the coefficient CgCp can be interpolated linearly.

(2) Positive coefficients denote forces toward the surface, whereas negative coefficients denote forces away from the surface.

3)   For the design of individual walls and wall cladding, the values of CgCp are provided in Figure 4.1.7.6.-B.

4)   For the design of roofs with a slope less than or equal to 7°, the values of CgCp are provided in Figure 4.1.7.6.-C.

5)   For the design of flat roofs with steps in elevation, the values of CgCp are provided in Figure 4.1.7.6.-D.

6)   For the design of gabled or hipped, single-ridge roofs with a slope greater than 7°, the values of CgCp are provided in Figure 4.1.7.6.-E.

7)   For the design of gabled, multi-ridge roofs, the values of CgCp are provided in

a)   Figure 4.1.7.6.-C for roofs with a slope less than or equal to 10°, and

b)   Figure 4.1.7.6.-F for roofs with a slope greater than 10°.

8)   For monosloped roofs, the values of CgCp are provided in

a)   Figure 4.1.7.6.-C for roofs with a slope less than or equal to 3°, and

b)   Figure 4.1.7.6.-G for roofs with a slope greater than 3° and less than or equal to 30°.

9)   For sawtooth roofs, the values of CgCp are provided in

a)   Figure 4.1.7.6.-C for roofs with a slope less than or equal to 10°, and

b)   Figure 4.1.7.6.-H for roofs with a slope greater than 10°.

10)   The wind loads on balcony guards on low buildings shall be as specified in Sentences 4.1.7.5.(5) and (6).

11)   The wind loads on parapets on low buildings shall be as specified in Sentences 4.1.7.5.(7) to (9).

Figure 4.1.7.6.-B

External peak values of CgCp on individual walls for the design of cladding and secondary structural members

Forming Part of Sentence 4.1.7.6.(3)

Notes to Figure 4.1.7.6.-B:

(1) These coefficients apply for any roof slope, α.

(2) End-zone width z is the lesser of 10% of the least horizontal dimension and 40% of height, H, but not less than 4% of the least horizontal dimension or 1 m.

(3) Combinations of external and internal pressures must be evaluated to obtain the most severe loading.

(4) Positive coefficients denote forces toward the surface, whereas negative coefficients denote forces away from the surface. Each structural element must be designed to withstand forces of both signs.

(5) Pressure coefficients generally apply for facades with architectural features; however, where vertical ribs deeper than 1 m are placed on a facade, a local CgCp of –2.8 applies to zone e.

Figure 4.1.7.6.-C

External peak values of CgCp on roofs with a slope of 7° or less for the design of structural components and cladding

Forming Part of Sentences 4.1.7.6.(4), (7), (8) and (9)

Notes to Figure 4.1.7.6.-C:

(1) Coefficients for overhung roofs have the prefix “o” and refer to the same roof areas as referred to by the corresponding symbol without a prefix. They include contributions from both upper and lower surfaces. In the case of overhangs, the walls are inboard of the roof outline.

(2) s and r apply to both roofs and upper surfaces of canopies.

(3) End-zone width z is the lesser of 10% of the least horizontal dimension and 40% of height, H, but not less than 4% of the least horizontal dimension or 1 m.

(4) Combinations of external and internal pressures must be evaluated to obtain the most severe loading.

(5) Positive coefficients denote forces toward the surface, whereas negative coefficients denote forces away from the surface. Each structural element must be designed to withstand forces of both signs.

(6) For calculating the uplift forces on tributary areas larger than 100 m2 on unobstructed nearly-flat roofs with low parapets, and where the centre of the tributary area is at least twice the height of the building from the nearest edge, the value of CgCp may be reduced from –1.5 to –1.1 at x/H = 2 and further reduced linearly to –0.6 at x/H = 5, where x is the distance to the nearest edge and H is the height of the building.

(7) For roofs having a perimeter parapet with a height of 1 m or greater, the corner coefficients CgCp for tributary areas less than 1 m2 can be reduced from –5.4 to –4.4.

Figure 4.1.7.6.-D

External peak values of CgCp for the design of the structural components and cladding of buildings with stepped roofs

Forming Part of Sentence 4.1.7.6.(5)

Notes to Figure 4.1.7.6.-D:

(1) The zone designations, pressure-gust coefficients and notes provided in Figure 4.1.7.6.-C apply on both the upper and lower levels of flat stepped roofs, except that on the lower levels, positive pressure-gust coefficients equal to those in Figure 4.1.7.6.-B for walls apply for a distance, b, where b is equal to 1.5h1 but not greater than 30 m. For all walls in Figure 4.1.7.6.-D, zone designations and pressure coefficients provided for walls in Figure 4.1.7.6.-B apply.

(2) Note (1) above applies only when the following conditions are met: h1 ≥ 0.3H, h1 ≥ 3 m, and W1, W2 or W3 is greater than 0.25W but not greater than 0.75W.

Figure 4.1.7.6.-E

External peak values of CgCp on single-span gabled and hipped roofs with a slope greater than 7° for the design of structural components and cladding

Forming Part of Sentence 4.1.7.6.(6)

Notes to Figure 4.1.7.6.-E:

(1) Coefficients for overhung roofs have the prefix “o” and refer to the same roof areas as referred to by the corresponding symbol without a prefix. They include contributions from both upper and lower surfaces.

(2) End-zone width z is the lesser of 10% of the least horizontal dimension and 40% of height, H, but not less than 4% of the least horizontal dimension or 1 m.

(3) Combinations of external and internal pressures must be evaluated to obtain the most severe loading.

(4) Positive coefficients denote forces towards the surface, whereas negative coefficients denote forces away from the surface. Each structural element must be designed to withstand forces of both signs.

(5) For hipped roofs with 7° < α ≤ 27°, edge/ridge strips and pressure-gust coefficients for ridges of gabled roofs apply along each hip.

Figure 4.1.7.6.-F

External peak values of CgCp on multi-span gabled (folded) roofs with a slope greater than 10° for the design of structural components and cladding

Forming Part of Sentence 4.1.7.6.(7)

Notes to Figure 4.1.7.6.-F:

(1) End-zone width z is the lesser of 10% of the least horizontal dimension and 40% of height, H, but not less than 4% of the least horizontal dimension or 1 m.

(2) Combinations of external and internal pressures must be evaluated to obtain the most severe loading.

(3) Positive coefficients denote forces towards the surface, whereas negative coefficients denote forces away from the surface. Each structural element must be designed to withstand forces of both signs.

(4) For α ≤ 10°, the coefficients given in Figure 4.1.7.6.-C apply, but for cases where α > than 7°, use α = 7°.

Figure 4.1.7.6.-G

External peak values of CgCp on monoslope roofs for the design of structural components and cladding

Forming Part of Sentence 4.1.7.6.(8)

Notes to Figure 4.1.7.6.-G:

(1) End-zone width z is the lesser of 10% of the least horizontal dimension and 40% of height, H, but not less than 4% of the least horizontal dimension or 1 m.

(2) Combinations of external and internal pressures must be evaluated to obtain the most severe loading.

(3) Positive coefficients denote forces towards the surface, whereas negative coefficients denote forces away from the surface. Each structural element must be designed to withstand forces of both signs.

(4) For α ≤ 3°, the coefficients given in Figure 4.1.7.6.-C apply.

Figure 4.1.7.6.-H

External peak values of CgCp on sawtooth roofs with a slope greater than 10° for the design of structural components and cladding

Forming Part of Sentence 4.1.7.6.(9)

Notes to Figure 4.1.7.6.-H:

(1) End-zone width z is the lesser of 10% of the least horizontal dimension and 40% of height, H, but not less than 4% of the least horizontal dimension or 1 m.

(2) Combinations of external and internal pressures must be evaluated to obtain the most severe loading.

(3) Positive coefficients denote forces towards the surface, whereas negative coefficients denote forces away from the surface. Each structural element must be designed to withstand forces of both signs.

(4) Negative coefficients on the corner zones of Span A differ from those on Spans B, C and D.

(5) For α ≤ 10°, the coefficients given in Figure 4.1.7.6.-C apply, but for cases where α > than 7°, use α = 7°.

4.1.7.7. Internal Pressure Coefficient

1)   The internal pressure coefficient, Cpi, for buildings shall be as prescribed in Table 4.1.7.7.

Table 4.1.7.7.

Internal Pressure Coefficients

Forming Part of Sentence 4.1.7.7.(1)

| Building Openings | Values for Cpi |
| --- | --- |
| Uniformly distributed small openings amounting to less than 0.1% of the total surface area of the building | –0.15 to 0.0 |
| Non-uniformly distributed openings of which none is significant or significant openings that are wind-resistant and closed during storms | –0.45 to +0.30 |
| Large openings likely to remain open during storms | –0.70 to +0.70 |

2)   The internal pressure coefficient, Cpi, for cladding on parapets shall be –0.70 to +0.70. (See Note A-4.1.7.7.(2).)

4.1.7.8. Dynamic Procedure

1)   For the application of the Dynamic Procedure, the provisions of Article 4.1.7.3. shall be followed, except that the exposure factor, Ce, shall be as prescribed in Sentences (2) and (3), and the gust effect factor, Cg, shall be as prescribed in Sentence (4), when determining the wind loads on the main structural system.

2)   For buildings in open terrain, as defined in Clause 4.1.7.3.(5)(a), the value of Ce for the design of the main structural system shall be calculated as follows:

(See Note A-4.1.7.8.(2) and (3).)

3)   For buildings in rough terrain, as defined in Clause 4.1.7.3.(5)(b), the value of Ce for the design of the main structural system shall be calculated as follows:

(See Note A-4.1.7.8.(2) and (3).)

4)   For the design of the main structural system, Cg shall be calculated as follows:

where

gp   = peak factor calculated as , and

σ/μ

where

ν   = average fluctuation rate calculated as ,

T   = 3 600 s,

K   = 0.08 for open terrain and 0.10 for rough terrain,

CeH   = exposure factor evaluated at reference height h = H,

B   = background turbulence factor, a function of w/H determined from Figure 4.1.7.8.,

s   = size reduction factor calculated as ,

F   = gust energy ratio calculated as , where x0 = (1 220fnD/VH), and

β   = damping ratio, which shall be determined by a rational method, or may be taken to be 0.01 for steel structures, 0.02 for concrete structures, and 0.015 for composite structures,

where

fnD   = natural frequency of vibration of the building in the along-wind direction, in Hz,

H   = height of the building,

w   = effective width of windward face of the building calculated as , where wi = width normal to wind direction at height hi, and

VH   = mean wind speed at the top of the structure, in m/s, calculated as ,

where

= reference wind speed at a height of 10 m, in m/s, calculated as ,

where

IW   = importance factor for wind load, as provided in Table 4.1.7.3.,

q   = reference velocity pressure, in Pa, and

ρ   = air density = 1.2929 kg/m3.

(See Note A-4.1.7.8.(4).)

Figure 4.1.7.8.

Background turbulence factor, B

Forming Part of Sentence 4.1.7.8.(4)

4.1.7.9. Full and Partial Wind Loading

1)   Except where the wind loads are derived from the combined CgCp values determined in accordance with Article 4.1.7.6., buildings and structural members shall be capable of withstanding the effects of the following loads:

a)   the full wind loads acting along each of the 2 principal horizontal axes considered separately,

b)   75% of the wind loads described in Clause (a) but offset from the central geometric axis of the building by 15% of its width normal to the direction of the force to produce the worst load effect,

c)   75% of the wind loads described in Clause (a) but with both axes considered simultaneously, and

d)   56% of the wind loads described in Clause (a) but with both axes considered simultaneously and offset from the central geometric axis of the building by 15% of its width normal to the direction of the force.

(See Note A-4.1.7.9.(1).)

4.1.7.10. Interior Walls and Partitions

1)   In the design of interior walls and partitions, due consideration shall be given to differences in air pressure on opposite sides of the wall or partition which may result from

a)   pressure differences between the windward and leeward sides of a building,

b)   stack effects due to a difference in air temperature between the exterior and interior of the building, and

c)   air pressurization by the mechanical services of the building.

4.1.7.11. Exterior Ornamentations, Equipment and Appendages

(See Note A-4.1.7.11.)

1)   The effects of wind loads on exterior ornamentations, equipment and appendages, including the increase in exposed area as a result of ice buildup as prescribed in CAN/CSA-S37, “Antennas, towers, and antenna-supporting structures,” shall be considered in the structural design of the connections and the building.

2)   Where there are a number of similar components, the net increase in force is permitted to be based on the total area for all similar components as opposed to the summation of forces of individual elements.

4.1.7.12. Attached Canopies on Low Buildings with a Height H ≤ 20 m

(See Note A-4.1.7.12.)

1)   For the purposes of this Article, “attached canopy” shall mean a horizontal canopy with a maximum slope of 2% that is attached to a building wall at any height, hc, above ground level.

2)   The specified external wind pressure, p, and the specified net external wind pressure, pnet, for attached canopies on exterior walls of low buildings with a height H ≤ 20 m shall be determined as follows:

where

p   = specified external wind pressure acting statically and in a direction normal to the upper or lower surface of the canopy, considered positive when acting towards the surface and negative when acting away from the surface,

pnet   = specified net external wind pressure acting statically on the canopy, considered positive when acting in a downward direction and negative when acting in an upward direction,

IW, q, Ce, Ct   = as defined in Sentence 4.1.7.3.(1),

CgCp   = gust pressure coefficient on the upper or lower surface of the canopy, as given in Figure 4.1.7.12.-A, and

(CgCp)net   = net gust pressure coefficient on the canopy, considering simultaneous contributions from the upper and lower surfaces of the canopy, as given in Figure 4.1.7.12.-B.

Figure 4.1.7.12.-A

Gust pressure coefficients on the upper and lower surfaces of attached canopies with no gap between the canopy and the building

Forming Part of Sentence 4.1.7.12.(2)

Notes to Figure 4.1.7.12.-A:

(1) The coefficients apply for any roof slope, α.

(2) The reference height, h, is the mid-height of the roof or 6 m, whichever is greater.

(3) Positive CgCp values denote forces acting towards the upper or lower surface of the canopy, whereas negative CgCp values denote forces acting away from the surface. Each structural element must be designed to resist both the positive and negative forces.

Figure 4.1.7.12.-B

Net gust pressure coefficients on attached canopies, considering simultaneous contributions from the upper and lower surfaces of the canopy

Forming Part of Sentence 4.1.7.12.(2)

Notes to Figure 4.1.7.12.-B:

(1) The coefficients apply for any roof slope, α.

(2) The reference height, h, is the mid-height of the roof or 6 m, whichever is greater.

(3) Positive (CgCp)net values denote net forces acting in a downward direction on the canopy, whereas negative (CgCp)net values denote net forces acting in an upward direction on the canopy. The canopy must be designed to resist both the positive and negative net forces.

4.1.7.13. Roof-Mounted Solar Panels on Buildings of Any Height

(See Note A-4.1.7.13.)

1)   Where solar panels are installed on a roof, the roof wind loads shall account for the wind loads on the solar panels, as determined in accordance with Sentences (2) to (7), or shall be determined in the same way as for the roof without solar panels, whichever approach results in the most critical effect.

2)   For an array of solar panels where the panels are installed close and parallel to the roof surface with their upper surface not more than 250 mm above the roof surface and with gaps around the panels of not less than 6 mm, the net positive or negative pressure difference between the upper and lower surfaces of a panel or the array shall be calculated as follows:

where

IW, q, Ce, Ct, Cg, Cp   = as defined in Sentence 4.1.7.3.(1), determined in the same manner as for the roof cladding,

E   = edge factor, as provided in Sentence (4), and

γa   = pressure equalization factor, as provided in Sentence (3).

3)   The pressure equalization factor, γa, in Sentence (2) shall be

a)   for a panel or an array where the panel chord length, Lp, is greater than 2 m or for a panel or an array that is within a distance of 2h2 from the roof edge or ridge, where h2 is the height of the panel's highest point above the roof surface, taken as 1.0, and

b)   for other panels or arrays, determined from Figure 4.1.7.13.-A based on the area of the panel or array over which the wind load is being calculated.

Figure 4.1.7.13.-A

Pressure equalization factor, γa, for solar panels or arrays mounted on roofs of buildings of any height

Forming Part of Clause 4.1.7.13.(3)(b)

4)   The edge factor, E, in Sentence (2) shall be taken as

a)   1.5 within a distance of 1.5Lp from an exposed edge of the array of solar panels, as defined in Sentence (5), and

b)   1.0 elsewhere.

5)   For the purposes of Clause (4)(a), an exposed edge of the array of solar panels shall be considered to occur

a)   where the distance to the next row of panels or the distance across a gap in the same row of panels exceeds 4h2 or 1.2 m, whichever is greater, or

b)   where the distance to the roof edge exceeds 4h2 or 1.2 m, whichever is greater, and exceeds 0.5h, where h is the reference height of the roof.

6)   For an array of solar panels mounted on a roof with a slope, α, less than or equal to 7°, where the panels are tilted relative to the roof surface, have a chord length, Lp, not greater than 2 m, and are installed such that the height of their lowest point above the roof surface, h1, is not greater than 0.6 m, the height of their highest point above the roof surface, h2, is not greater than 1.2 m, and their tilt angle relative to the roof surface, ω, is not greater than 35°, or where the panels are installed parallel to the roof surface with their upper surface greater than 250 mm above the roof surface and with gaps not less than 6 mm between the panels, the net positive or negative pressure difference between the upper and the lower surfaces of a panel or the array shall be calculated as follows:

where

IW, q, Ce, Ct   = as defined in Sentence 4.1.7.3.(1), determined in the same manner as for the roof cladding, and

(CgCp)net   = net gust pressure coefficient, as provided in Sentence (7).

7)   The net gust pressure coefficient, (CgCp)net, in Sentence (6) shall be calculated as follows:

where

γp   = parapet factor, determined as the lesser of 1.2 and (0.9 + hpt/h),

γc   = chord factor, determined as the greater of (0.6 + 0.2Lp) and 0.8,

E   = as defined in Sentence (2), and

(CgCp)n    = normalized gust pressure coefficient, determined from Figure 4.1.7.13.-B based on ω and AN,

where

hpt   = height of the parapet above the roof surface, in m,

h   = reference height of the roof, in m,

Lp   = panel chord length, in m,

ω   = panel tilt angle relative to the roof surface, and

AN   = normalized panel or array area, calculated as

where

A   = panel or array area over which the wind load is being calculated, in m2, and

Lb   = normalized building length, in m, determined as the lesser of , h and WS,

where

WL   = longest horizontal dimension of the building, in m, and

WS   = smallest horizontal dimension of the building, in m.

Figure 4.1.7.13.-B

Normalized gust pressure coefficient, (CgCp)n, for solar panels or arrays mounted on low-sloped roofs of buildings of any height

Forming Part of Sentence 4.1.7.13.(7)

Notes to Figure 4.1.7.13.-B:

(1) H = height of the building.

(2) h = reference height of the roof.

(3) (CgCp)n values are for both positive and negative values.

(4) For panels with 5° < ω <15°, linear interpolation is permitted.

4.1.7.14. Wind Tunnel Procedure

1)   Except as provided in Sentences (2) and (3), wind tunnel tests on scale models to determine wind loads on buildings shall be conducted in accordance with ASCE/SEI 49, “Wind Tunnel Testing for Buildings and Other Structures.”

2)   Where an adjacent building provides substantial sheltering effect, the wind loads for the main structural system shall be no lower than 80% of the loads determined from tests referred to in Sentence (1) with the effect of the sheltering building removed as applied to

a)   the base shear force for buildings with a ratio of height to minimum effective width, as defined in Sentence 4.1.7.2.(2), less than or equal to 1.0, or

b)   the base moment for buildings with a ratio of height to minimum effective width greater than 1.0.

3)   For the design of cladding and secondary structural members, the exterior wind loads determined from the wind tunnel tests shall be no less onerous than those determined by analysis in accordance with Article 4.1.7.3. using the following assumptions:

a)   Cg = 2.5 and Cp = ±0.72, where the building's height is greater than 20 m or greater than its minimum effective width, and

b)   CgCp = 80% of the values for zones w and r provided in Article 4.1.7.6., where the building's height is less than or equal to 20 m and no greater than its minimum effective width.

4.1.8. Earthquake Load and Effects

4.1.8.1. Analysis

1)   Except as permitted in Sentence (2), the deflections and specified loading due to earthquake motions shall be determined according to the requirements of Articles 4.1.8.2. to 4.1.8.23.

2)   Where IEFsSa(0.2,X450) and IEFsSa(2.0,X450) are less than 0.16 and 0.03 respectively, the deflections and specified loading due to earthquake motions are permitted to be determined in accordance with Sentences (3) to (15), where

a)   IE is the earthquake importance factor and has a value of 0.8, 1.0, 1.3 and 1.5 for buildings in the Low, Normal, High and Post-disaster Importance Categories respectively,

b)   Fs is the site coefficient based on the average 60 or , as defined in Article 4.1.8.2., for the top 30 m of soil below the footings, pile caps, or mat foundations and has a value of

i)   1.0 for rock sites or when 60 > 50 or > 100 kPa,

ii)   1.6 when 15 ≤ 60 ≤ 50 or 50 kPa ≤ ≤ 100 kPa, and

iii)   2.8 for all other cases, and

c)   Sa(T,X450) is the 5%-damped spectral acceleration value at period T for site designation X450, as defined in Article 4.1.8.2., determined in accordance with Subsection 1.1.3. and corresponding to a 2% probability of exceedance in 50 years.

3)   The structure shall have a clearly defined

a)   seismic force resisting system (SFRS) to resist the earthquake loads and their effects, and

b)   load path (or paths) that will transfer the inertial forces generated in an earthquake to the supporting ground.

4)   An unreinforced masonry SFRS shall not be permitted where

a)   IE is greater than 1.0, or

b)   the height above grade is greater than or equal to 30 m.

5)   The height above grade of an SFRS designed in accordance with CSA S136, “North American Specification for the Design of Cold-Formed Steel Structural Members (using the Appendix B provisions applicable to Canada),” shall be less than 15 m.

6)   Earthquake forces shall be assumed to act horizontally and independently about any two orthogonal axes.

7)   The specified lateral earthquake force, Vs, at the base of the structure in the direction under consideration shall be calculated as follows:

where

Sa(Ts,X450)   = value of Sa(Ts,X450) determined by linear interpolation between the values of Sa(0.2,X450 ), Sa(0.5,X450) and Sa(1.0,X450),

= Sa(0.2,X450) for Ts ≤ 0.2 s, and

= Sa(1.0,X450) for Ts ≥ 1.0 s,

W   = sum of Wi over the height of the building, where Wi is defined in Article 4.1.8.2., and

Rs   = 1.5, except Rs = 1.0 for structures where the storey strength is less than that in the storey above and for an unreinforced masonry SFRS,

where

Ts   = fundamental lateral period of vibration of the building, as defined in Article 4.1.8.2.,

= 0.085(hn)¾ for steel moment frames,

= 0.075(hn)¾ for concrete moment frames,

= 0.1N for other moment frames,

= 0.025hn for braced frames, and

= 0.05(hn)¾ for shear walls and other structures,

where

hn   = height, in m, above the base to level n, as defined in Article 4.1.8.2., and

N   = total number of storeys above exterior grade to level n, as defined in Article 4.1.8.2.,

except that, in cases where Rs = 1.5, Vs need not be greater than FsSa(0.5,X450)IEW/Rs.

8)   The specified lateral earthquake force, Vs, shall be distributed over the height of the building in accordance with the following formula:

where

Fx   = force applied through the centre of mass at level x,

Wx, Wi   = portion of W that is located at or is assigned to level x or i respectively, and

hx, hi   = height, in m, above the base to level x or i respectively, as defined in Article 4.1.8.2.

9)   Accidental torsional effects applied concurrently with Fx shall be considered by applying torsional moments about the vertical axis at each level for each of the following cases considered separately:

a)   +0.1DnxFx, and

b)   −0.1DnxFx.

10)   Deflections obtained from a linear analysis shall include the effects of torsion and be multiplied by Rs/IE to get realistic values of expected deflections.

11)   The deflections referred to in Sentence (10) shall be used to calculate the largest interstorey deflection, which shall not exceed

a)   0.01hs for post-disaster buildings,

b)   0.02hs for High Importance Category buildings, and

c)   0.025hs for all other buildings,

where hs is the interstorey height as defined in Article 4.1.8.2.

12)   When earthquake forces are calculated using Rs = 1.5, the following elements in the SFRS shall have their design forces due to earthquake effects increased by 33%:

a)   diaphragms and their chords, connections, struts and collectors,

b)   tie downs in wood or drywall shear walls,

c)   connections and anchor bolts in steel- and wood-braced frames,

d)   connections in precast concrete, and

e)   connections in steel moment frames.

13)   Except as provided in Sentence (14), where cantilever parapet walls, other cantilever walls, exterior ornamentation and appendages, towers, chimneys or penthouses are connected to or form part of a building, they shall be designed, along with their connections, for a lateral force, Vsp, distributed according to the distribution of mass of the element and acting in the lateral direction that results in the most critical loading for design using the following equation:

where

Wp   = weight of a portion of a structure as defined in Article 4.1.8.2.

14)   The value of Vsp shall be doubled for unreinforced masonry elements.

15)   Structures designed in accordance with this Article need not comply with the seismic requirements stated in the applicable design standard referenced in Section 4.3.

4.1.8.2. Notation

1)   In this Subsection

Ar   = element or component force amplification factor to account for type of attachment, as defined in Sentence 4.1.8.18.(1),

Ax   = height factor at level x to account for variation of response of an element or component with elevation within the building, as defined in Sentence 4.1.8.18.(1),

Bx   = ratio at level x used to determine torsional sensitivity, as defined in Sentence 4.1.8.11.(10),

B   = maximum value of Bx, as defined in Sentence 4.1.8.11.(10),

Cp   = seismic coefficient for an element or component, as defined in Sentence 4.1.8.18.(1),

Dnx   = plan dimension of the building at level x perpendicular to the direction of seismic loading being considered,

ex   = distance measured perpendicular to the direction of earthquake loading between centre of mass and centre of rigidity at the level being considered (see Note A-4.1.8.2.(1)),

Fa   = acceleration-based site coefficient for application in standards referenced in Subsection 4.1.8., as defined in Sentence 4.1.8.4.(7),

Fs   = site coefficient as defined in Sentence 4.1.8.1.(2) for application in Article 4.1.8.1.,

Ft   = portion of V to be concentrated at the top of the structure, as defined in Sentence 4.1.8.11.(7),

Fv   = velocity-based site coefficient for application in standards referenced in Subsection 4.1.8., as defined in Sentence 4.1.8.4.(7),

Fx   = lateral force applied to level x, as defined in Sentence 4.1.8.11.(7),

hi, hn, hx   = height, in m, above the base (i = 0) to level i, n, or x respectively, where the base of the structure is the level at which horizontal earthquake motions are considered to be imparted to the structure,

hs   = interstorey height (hi − hi−1),

IE   = earthquake importance factor of the structure, as described in Sentence 4.1.8.5.(1),

J   = numerical reduction coefficient for base overturning moment, as defined in Sentence 4.1.8.11.(6),

Jx   = numerical reduction coefficient for overturning moment at level x, as defined in Sentence 4.1.8.11.(8),

Level i   = any level in the building, i = 1 for first level above the base,

Level n   = level that is uppermost in the main portion of the structure,

Level x   = level that is under design consideration,

Mv   = factor to account for higher mode effects on base shear, as defined in Sentence 4.1.8.11.(6),

Mx   = overturning moment at level x, as defined in Sentence 4.1.8.11.(8),

N   = total number of storeys above exterior grade to level n,

= average standard penetration resistance, in blows per 0.3 m, in the top 30 m of soil, corrected to a rod energy efficiency of 60% of the theoretical maximum,

PGA(X)   = peak ground acceleration, expressed as a ratio to gravitational acceleration, for site designation X, as defined in Sentence 4.1.8.4.(1),

PGV(X)   = peak ground velocity, in m/s, for site designation X, as defined in Sentence 4.1.8.4.(1),

PI   = plasticity index for soil,

Rd   = ductility-related force modification factor reflecting the capability of a structure to dissipate energy through reversed cyclic inelastic behaviour, as defined in Article 4.1.8.9.,

Ro   = overstrength-related force modification factor accounting for the dependable portion of reserve strength in a structure designed according to these provisions, as defined in Article 4.1.8.9.,

Rp   = element or component response modification factor, as defined in Sentence 4.1.8.18.(1),

Rs   = combined overstrength and ductility-related modification factor, as defined in Sentence 4.1.8.1.(7), for application in Article 4.1.8.1.,

Sa(T,X)   = 5%-damped spectral acceleration, expressed as a ratio to gravitational acceleration, at period T for site designation X, as defined in Sentence 4.1.8.4.(1),

SC   = Seismic Category assigned to a building based on its Importance Category and the design spectral acceleration values at periods of 0.2 s and 1.0 s, as defined in Article 4.1.8.5.,

SFRS   = seismic force resisting system, that part of the structural system that has been considered in the design to provide the required resistance to the earthquake forces and effects defined in Subsection 4.1.8.,

Sp   = horizontal force factor for part or portion of a building and its anchorage, as given in Sentence 4.1.8.18.(1),

S(T)   = design spectral acceleration, expressed as a ratio to gravitational acceleration, at period T, as defined in Sentence 4.1.8.4.(6),

= average undrained shear strength, in kPa, in the top 30 m of soil,

T   = period, in s,

Ta   = fundamental lateral period of vibration of the building or structure, in s, in the direction under consideration, as defined in Sentence 4.1.8.11.(3),

TDD   = total design displacement of any point in a seismically isolated structure, within or above the isolation system, obtained by calculating the mean + (IE × the standard deviation) of the peak horizontal displacements from all sets of ground motion time histories analyzed, but not less than √IE × the mean, where the peak horizontal displacement is based on the vector sum of the two orthogonal horizontal displacements considered for each time step,

Ts   = fundamental lateral period of vibration of the building or structure, in s, in the direction under consideration, as defined in Sentence 4.1.8.1.(7),

Tx   = floor torque at level x, as defined in Sentence 4.1.8.11.(11),

V   = specified lateral earthquake force at the base of the structure, as determined in Article 4.1.8.11.,

Vd   = specified lateral earthquake force at the base of the structure, as determined in Article 4.1.8.12.,

Ve   = lateral earthquake elastic force at the base of the structure, as determined in Article 4.1.8.12.,

Ved   = adjusted lateral earthquake elastic force at the base of the structure, as determined in Article 4.1.8.12.,

Vp   = specified lateral earthquake force on an element or component, as determined in Article 4.1.8.18.,

Vs   = specified lateral earthquake force at the base of the structure, as determined in Sentence 4.1.8.1.(7), for application in Article 4.1.8.1.,

Vs30   = average shear wave velocity, in m/s, in the top 30 m of soil or rock,

W   = specified dead load, as defined in Article 4.1.4.1., except that the minimum partition weight as defined in Sentence 4.1.4.1.(3) need not exceed 0.5 kPa, plus 25% of the specified snow load as defined in Subsection 4.1.6., plus 60% of the storage load for areas used for storage, except that storage garages need not be considered storage areas, and the full contents of any tanks (see Note A-4.1.8.2.(1)),

Wi, Wx   = portion of W that is located at or is assigned to level i or x respectively,

Wp   = weight of a part or portion of a structure, e.g., cladding, partitions and appendages,

X   = site designation, either XV or XS,

XS   = site designation in terms of Site Class, where S is the Site Class determined in accordance with Sentence 4.1.8.4.(3),

XV   = site designation in terms of Vs30, where V is the Vs30 value calculated from in situ measurements of shear wave velocity,

X450   = site designation XV with Vs30 = 450 m/s,

δave   = average displacement of the structure at level x, as defined in Sentence 4.1.8.11.(10), and

δmax   = maximum displacement of the structure at level x, as defined in Sentence 4.1.8.11.(10).

4.1.8.3. General Requirements

1)   The building shall be designed to meet the requirements of this Subsection and of the design standards referenced in Section 4.3.

2)   Structures shall be designed with a clearly defined load path, or paths, that will transfer the inertial forces generated in an earthquake to the supporting ground.

3)   The structure shall have a clearly defined SFRS, as defined in Article 4.1.8.2.

4)   The SFRS shall be designed to resist 100% of the earthquake loads and their effects. (See Note A-4.1.8.3.(4).)

5)   All structural framing elements not considered to be part of the SFRS must be investigated and shown to behave elastically or to have sufficient non-linear capacity to support their gravity loads while undergoing earthquake-induced deformations calculated from the deflections determined in Article 4.1.8.13.

6)   Stiff elements that are not considered part of the SFRS, such as concrete, masonry, brick or precast walls or panels, shall be

a)   separated from all structural elements of the building such that no interaction takes place as the building undergoes deflections due to earthquake effects as calculated in this Subsection, or

b)   made part of the SFRS and satisfy the requirements of this Subsection.

(See Note A-4.1.8.3.(6).)

7)   Stiffness imparted to the structure from elements not part of the SFRS, other than those described in Sentence (6), shall not be used to resist earthquake deflections but shall be accounted for

a)   in calculating the period of the structure for determining forces if the added stiffness decreases the fundamental lateral period by more than 15%,

b)   in determining the irregularity of the structure, except the additional stiffness shall not be used to make an irregular SFRS regular or to reduce the effects of torsion (see Note A-4.1.8.3.(7)(b) and (c)), and

c)   in designing the SFRS if inclusion of the elements not part of the SFRS in the analysis has an adverse effect on the SFRS (see Note A-4.1.8.3.(7)(b) and (c)).

8)   Structural modeling shall be representative of the magnitude and spatial distribution of the mass of the building and of the stiffness of all elements of the SFRS, including stiff elements that are not separated in accordance with Sentence 4.1.8.3.(6), and shall account for

a)   the effect of cracked sections in reinforced concrete and reinforced masonry elements,

b)   the effect of the finite size of members and joints,

c)   sway effects arising from the interaction of gravity loads with the displaced configuration of the structure, and

d)   other effects that influence the lateral stiffness of the building.

(See Note A-4.1.8.3.(8).)

4.1.8.4. Site Properties

1)   For site designation X, as determined in accordance with Sentence (2) or (3), the peak ground acceleration, PGA(X), the peak ground velocity, PGV(X), and the 5%-damped spectral acceleration values, Sa(T,X), at periods T of 0.2 s, 0.5 s, 1.0 s, 2.0 s, 5.0 s and 10.0 s shall

a)   except as provided in Sentence (4), be determined in accordance with Subsection 1.1.3., and

b)   except as provided in Article 4.1.8.23., correspond to a 2% probability of exceedance in 50 years.

2)   Except as provided in Sentence (3), the site designation referred to in Sentence (1) shall be determined using the average shear wave velocity, Vs30, calculated from in situ measurements of shear wave velocity, as follows:

a)   for the ground profiles described in Table 4.1.8.4.-A, the site designation shall be determined in accordance with the Table, and

b)   for all other ground profiles, the site designation shall be XV, where V is the value of Vs30.

(See Note A-4.1.8.4.(2) and (3).)

Table 4.1.8.4.-A

Exceptions for Site Designation Using Vs30 Calculated from In Situ Measurements

Forming Part of Sentence 4.1.8.4.(2)

| Ground Profile Characteristics |  | Site Designation |
| --- | --- | --- |
| Average Shear Wave Velocity in Top 30 m, Vs30, Calculated from In Situ Measurements, in m/s | Additional Characteristics |  |
| Vs30 > 760 | Ground profile contains more than 3 m of softer materials between rock and the underside of footing or mat foundations | X760 |
| Vs30 > 140 | Ground profile contains more than 3 m of soil with all the following characteristics: • plasticity index, PI > 20, • moisture content, w ≥ 40%, and • undrained shear strength, su < 25 kPa | XE |
| Vs30 > 140 | Ground profile contains • liquefiable soil, quick and highly sensitive clay, collapsible weakly cemented soil, or other soil susceptible to failure or collapse under seismic loading, • more than 3 m of peat and/or highly organic clay, • more than 8 m of highly plastic soil (with PI > 75), or • more than 30 m of soft to medium-stiff clay | XF |
| Vs30 ≤ 140 | n/a | XF |

3)   Where Vs30 calculated from in situ measurements is not available, the site designation referred to in Sentence (1) shall be XS, where S is the Site Class determined using the energy-corrected average standard penetration resistance, 60, or the average undrained shear strength, , in accordance with Table 4.1.8.4.-B, 60 and being calculated based on rational analysis. (See Notes A-4.1.8.4.(3) and A-4.1.8.4.(2) and (3).)

Table 4.1.8.4.-B

Site Classes, S, for Site Designation XS

Forming Part of Sentence 4.1.8.4.(3)

| Site Class, S | Ground Profile | Ground Profile Characteristics |  |  |
| --- | --- | --- | --- | --- |
|  |  | Average Shear Wave Velocity in Top 30 m, Vs30, in m/s(1) | Average Standard Penetration Resistance in Top 30 m, 60, in Blows per 0.3 m | Average Undrained Shear Strength in Top 30 m, , in kPa |
| A | Hard rock(2) | Vs30 > 1 500 | n/a | n/a |
| B | Rock(2) | 760 < Vs30 ≤ 1 500 | n/a | n/a |
| C | Very dense soil and soft rock | 360 < Vs30 ≤ 760 | 60 > 50 | > 100 |
| D | Stiff soil | 180 < Vs30 ≤ 360 | 15 < 60 ≤ 50 | 50 < ≤ 100 |
| E | Soft soil | 140 < Vs30 ≤ 180 | 10 < 60 ≤ 15 | 40 < ≤ 50 |
|  |  | Any ground profile other than Site Class F that contains more than 3 m of soil with all the following characteristics: • plasticity index, PI > 20, • moisture content, w ≥ 40%, and • undrained shear strength, su < 25 kPa |  |  |
| F | Other soils(3) | Vs30 ≤ 140 | 60 ≤ 10 | ≤ 40 |
|  |  | Any ground profile that contains • liquefiable soil, quick and highly sensitive clay, collapsible weakly cemented soil, or other soil susceptible to failure or collapse under seismic loading, • more than 3 m of peat and/or highly organic clay, • more than 8 m of highly plastic soil (with PI > 75), or • more than 30 m of soft to medium-stiff clay |  |  |

Notes to Table 4.1.8.4.-B:

(1) See Note A-4.1.8.4.(2) and (3).

(2) Site designations XA and XB, corresponding to Site Classes A and B, are not to be used in cases where the ground profile contains more than 3 m of softer materials between rock and the underside of footing or mat foundations. The appropriate site designation for such cases is X760.

(3) Site-specific geotechnical evaluation is required.

4)   Site-specific geotechnical evaluation is required to determine the values of PGA(XF), PGV(XF) and Sa(T,XF) for site designation XF.

5)   Where structures on liquefiable soils have a fundamental lateral period, Ta, of 0.5 s or less, the site designation X and the corresponding values of Sa(T,X) and PGA(X) are permitted to be determined in accordance with Sentence (1) by assuming that the soils are not liquefiable.

6)   The design spectral acceleration, S(T), shall be determined in accordance with Table 4.1.8.4.-C, using log–log or linear interpolation for intermediate values of T. (See Note A-4.1.8.4.(6).)

Table 4.1.8.4.-C

Design Spectral Acceleration

Forming Part of Sentence 4.1.8.4.(6)

| Period, T, in s | Design Spectral Acceleration, S(T) |
| --- | --- |
| ≤ 0.2 | Sa(0.2,X) or Sa(0.5,X), whichever is greater |
| 0.5 | Sa(0.5,X) |
| 1.0 | Sa(1.0,X) |
| 2.0 | Sa(2.0,X) |
| 5.0 | Sa(5.0,X) |
| 10.0 | Sa(10.0,X) |

7)   Where required for the application of a standard referenced in this Subsection, the acceleration-based site coefficient, Fa, for site designation X shall be taken as S(0.2)/Sa(0.2,X450) and the velocity-based site coefficient, Fv, for site designation X shall be taken as S(1.0)/Sa(1.0,X450).

4.1.8.5. Importance Factor and Seismic Category

1)   The earthquake importance factor, IE, shall be determined according to Table 4.1.8.5.-A

Table 4.1.8.5.-A

Importance Factor for Earthquake Loads and Effects, IE

Forming Part of Sentence 4.1.8.5.(1)

| Importance Category | Importance Factor, IE |  |
| --- | --- | --- |
|  | ULS | SLS(1) |
| Low | 0.8 | (2) |
| Normal | 1.0 |  |
| High | 1.3 |  |
| Post-disaster | 1.5 |  |

Notes to Table 4.1.8.5.-A:

(1) See Article 4.1.8.13.

(2) See Note A-Table 4.1.8.5.-A.

2)   Buildings shall be assigned a Seismic Category in accordance with Table 4.1.8.5.-B.

Table 4.1.8.5.-B

Seismic Categories for Buildings

Forming Part of Sentence 4.1.8.5.(2)

| Seismic Category(1) | IES(0.2) | IES(1.0) |
| --- | --- | --- |
| SC1 | IES(0.2) < 0.2 | IES(1.0) < 0.1 |
| SC2 | 0.2 ≤ IES(0.2) < 0.35 | 0.1 ≤ IES(1.0) < 0.2 |
| SC3 | 0.35 ≤ IES(0.2) ≤ 0.75 | 0.2 ≤ IES(1.0) ≤ 0.3 |
| SC4 | IES(0.2) > 0.75 | IES(1.0) > 0.3 |

Notes to Table 4.1.8.5.-B:

(1) The Seismic Category of a building shall be taken as the more severe of the categories determined on the basis of IES(0.2) and IES(1.0), irrespective of the fundamental lateral period of the building, Ta.

4.1.8.6. Structural Configuration

1)   Structures having any of the features listed in Table 4.1.8.6. shall be designated irregular.

2)   Structures not classified as irregular according to Sentence (1) may be considered regular.

3)   Except as required by Article 4.1.8.10., where the Seismic Category is SC3 or SC4, structures designated as irregular must satisfy the provisions referenced in Table 4.1.8.6.

Table 4.1.8.6.

Structural Irregularities(1)(2)

Forming Part of Sentences 4.1.8.6.(1) and (3), Clause 4.1.8.7.(1)(c) and Article 4.1.8.10.

| Type | Irregularity Type and Definition | Notes |
| --- | --- | --- |
| 1 | Vertical Stiffness Irregularity For concrete and masonry shear walls, vertical stiffness irregularity shall be considered to exist where the lateral stiffness of the SFRS in any storey is less than 70% of the stiffness in an adjacent storey, or less than 80% of the average stiffness in the three storeys above or below. For all other types of SFRS, vertical stiffness irregularity shall be considered to exist where the interstorey deflection under lateral earthquake forces divided by the interstorey height, hs, of any storey is greater than 130% of that of an adjacent storey. | (3)(4)(5) |
| 2 | Weight (mass) Irregularity Weight irregularity shall be considered to exist where the weight, Wi, of any storey is more than 150% of the weight of an adjacent storey. A roof that is lighter than the floor below need not be considered. | (3) |
| 3 | Vertical Geometric Irregularity Vertical geometric irregularity shall be considered to exist where the horizontal dimension of the SFRS in any storey is more than 130% of that in an adjacent storey. | (3)(4)(6) |
| 4 | In-Plane Discontinuity in Vertical Lateral-Force-Resisting Element Except for braced frames and moment-resisting frames, an in-plane discontinuity shall be considered to exist where there is an offset of a lateral-force-resisting element of the SFRS or a reduction in lateral stiffness of the resisting element in the storey below. | (3)(4)(6) |
| 5 | Out-of-Plane Offsets Discontinuities in a lateral force path, such as out-of-plane offsets of the vertical elements of the SFRS. | (3)(4)(6) |
| 6 | Discontinuity in Capacity – Weak Storey A weak storey is one in which the storey shear strength is less than that in the storey above. The storey shear strength is the total strength of all seismic-resisting elements of the SFRS sharing the storey shear for the direction under consideration. | (3)(4) |
| 7 | Torsional Sensitivity (to be considered when diaphragms are not flexible) Torsional sensitivity shall be considered to exist when the ratio B calculated according to Sentence 4.1.8.11.(10) exceeds 1.7. | (3)(4)(7) |
| 8 | Non-orthogonal Systems A non-orthogonal system irregularity shall be considered to exist when the SFRS is not oriented along a set of orthogonal axes. | (3)(8) |
| 9 | Gravity-Induced Lateral Demand Irregularity Gravity-induced lateral demand irregularity on the SFRS shall be considered to exist where the ratio α calculated in accordance with Sentence 4.1.8.10.(7) exceeds 0.1 for an SFRS with self-centering characteristics and 0.03 for other systems. | (3)(4)(8) |
| 10 | Sloped Column Irregularity Sloped column irregularity shall be considered to exist where a vertical member that is inclined more than 2° from the vertical supports a portion of the weight of the building in axial compression. | (4) |

Notes to Table 4.1.8.6.:

(1) One-storey penthouses with a weight of less than 10% of the level below need not be considered in the application of this Table.

(2) See Note A-Table 4.1.8.6.

(3) See Article 4.1.8.7.

(4) See Article 4.1.8.10.

(5) Increased stiffness in storeys below grade need not be considered in the determination of vertical stiffness irregularity.

(6) See Article 4.1.8.15.

(7) See Sentences 4.1.8.11.(10) and (11), and 4.1.8.12.(4).

(8) See Article 4.1.8.8.

4.1.8.7. Methods of Analysis

1)   Analysis for earthquake actions shall be carried out in accordance with the Dynamic Analysis Procedure described in Article 4.1.8.12. (see Note A-4.1.8.7.(1)), except that the Equivalent Static Force Procedure described in Article 4.1.8.11. may be used for structures that meet any of the following criteria:

a)   where the Seismic Category is SC1 or SC2,

b)   regular structures that are less than 60 m in height and have a fundamental lateral period, Ta, less than 2 s in each of two orthogonal directions as defined in Article 4.1.8.8., or

c)   structures with a structural irregularity of Type 2, 3, 4, 5, 6 or 8 as defined in Table 4.1.8.6. that are less than 20 m in height and have a fundamental lateral period, Ta, less than 0.5 s in each of two orthogonal directions as defined in Article 4.1.8.8.

4.1.8.8. Direction of Loading

1)   Earthquake forces shall be assumed to act in any horizontal direction, except that the following shall be considered to provide adequate design force levels in the structure:

a)   where components of the SFRS are oriented along a set of orthogonal axes, independent analyses about each of the principal axes of the structure shall be performed,

b)   where the components of the SFRS are not oriented along a set of orthogonal axes and the Seismic Category is SC1 or SC2, independent analyses about any two orthogonal axes is permitted, or

c)   where the components of the SFRS are not oriented along a set of orthogonal axes and the Seismic Category is SC3 or SC4, analysis of the structure independently in any two orthogonal directions for 100% of the specified earthquake loads applied in one direction plus 30% of the specified earthquake loads in the perpendicular direction, with the combination requiring the greater element strength being used in the design.

4.1.8.9. SFRS Force Modification Factors and General Restrictions

1)   Except as provided in Articles 4.1.8.20. and 4.1.8.22., the values of Rd and Ro and the corresponding system restrictions shall conform to Table 4.1.8.9. and the requirements of this Subsection.

2)   When a particular value of Rd is required by this Article, the corresponding Ro shall be used.

3)   For combinations of different types of SFRS acting in the same direction in the same storey, RdRo shall be taken as the lowest value of RdRo corresponding to these systems.

4)   For vertical variations of RdRo, excluding rooftop structures not exceeding two storeys in height whose weight is less than the greater of 10% of W and 30% of Wi of the level below, the value of RdRo used in the design of any storey shall be less than or equal to the lowest value of RdRo used in the given direction for the storeys above, and the requirements of Sentence 4.1.8.15.(6) must be satisfied. (See Note A-4.1.8.9.(4).)

5)   If it can be demonstrated through testing, research and analysis that the seismic performance of a structural system is at least equivalent to one of the types of SFRS defined in Table 4.1.8.9., then such a structural system will qualify for values of Rd and Ro corresponding to the equivalent type in that Table. (See Note A-4.1.8.9.(5).)

Table 4.1.8.9.

SFRS Ductility-Related Force Modification Factors, Rd, Overstrength-Related Force Modification Factors, Ro, and General Restrictions(1)

Forming Part of Sentences 4.1.8.9.(1) and (5), 4.1.8.10.(5) and (6), 4.1.8.11.(12), 4.1.8.15.(9) and 4.1.8.20.(8)

| Type of SFRS | Rd | Ro | Restrictions(2) |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Seismic Category |  |  |  |
|  |  |  | SC1 | SC2 | SC3 | SC4 |
| Steel Structures Designed and Detailed According to CSA S16(3)(4) |  |  |  |  |  |  |
| Ductile moment-resisting frames | 5.0 | 1.5 | NL | NL | NL | NL |
| Moderately ductile moment-resisting frames | 3.5 | 1.5 | NL | NL | NL | NL |
| Limited ductility moment-resisting frames | 2.0 | 1.3 | NL | NL | 60 | 30 |
| Moderately ductile truss moment-resisting frames | 3.5 | 1.6 | NL | NL | 50 | 30 |
| Moderately ductile concentrically braced frames |  |  |  |  |  |  |
| Tension-compression braces | 3.0 | 1.3 | NL | NL | 40 | 40 |
| Tension only braces | 3.0 | 1.3 | NL | NL | 20 | 20 |
| Limited ductility concentrically braced frames |  |  |  |  |  |  |
| Tension-compression braces | 2.0 | 1.3 | NL | NL | 60 | 60 |
| Tension only braces | 2.0 | 1.3 | NL | NL | 40 | 40 |
| Ductile buckling-restrained braced frames | 4.0 | 1.2 | NL | NL | 40 | 40 |
| Ductile eccentrically braced frames | 4.0 | 1.5 | NL | NL | NL | NL |
| Ductile plate walls | 5.0 | 1.6 | NL | NL | NL | NL |
| Moderately ductile plate walls | 3.5 | 1.3 | NL | NL | 40 | 40 |
| Limited ductility plate walls | 2.0 | 1.3 | NL | NL | 60 | 60 |
| Conventional construction of moment-resisting frames, braced frames or plate walls |  |  |  |  |  |  |
| Assembly occupancies | 1.5 | 1.3 | NL | NL | 15 | 15 |
| Other occupancies | 1.5 | 1.3 | NL | NL | 60 | 40 |
| Other steel SFRSs not defined above | 1.0 | 1.0 | 15 | 15 | NP | NP |
| Concrete Structures Designed and Detailed According to CSA A23.3 |  |  |  |  |  |  |
| Ductile moment-resisting frames | 4.0 | 1.7 | NL | NL | NL | NL |
| Moderately ductile moment-resisting frames | 2.5 | 1.4 | NL | NL | 60 | 40 |
| Ductile coupled walls | 4.0 | 1.7 | NL | NL | NL | NL |
| Moderately ductile coupled walls | 2.5 | 1.4 | NL | NL | NL | 60 |
| Ductile partially coupled walls | 3.5 | 1.7 | NL | NL | NL | NL |
| Moderately ductile partially coupled walls | 2.0 | 1.4 | NL | NL | NL | 60 |
| Ductile shear walls | 3.5 | 1.6 | NL | NL | NL | NL |
| Moderately ductile shear walls | 2.0 | 1.4 | NL | NL | NL | 60 |
| Conventional construction |  |  |  |  |  |  |
| Moment-resisting frames | 1.5 | 1.3 | NL | NL | 20 | 10(5)(6) |
| Shear walls | 1.5 | 1.3 | NL | NL | 40 | 30 |
| Two-way slabs without beams | 1.3 | 1.3 | 20 | 15 | NP | NP |
| Tilt-up construction |  |  |  |  |  |  |
| Moderately ductile walls and frames | 2.0 | 1.3 | 30 | 25 | 25 | 25 |
| Limited ductility walls and frames | 1.5 | 1.3 | 30 | 25 | 20 | 20(7) |
| Conventional walls and frames | 1.3 | 1.3 | 25 | 20 | NP | NP |
| Other concrete SFRSs not listed above | 1.0 | 1.0 | 15 | 15 | NP | NP |
| Timber Structures Designed and Detailed According to CSA O86 |  |  |  |  |  |  |
| Shear walls |  |  |  |  |  |  |
| Nailed shear walls: wood-based panel | 3.0 | 1.7 | NL | NL | 30 | 20 |
| Shear walls: wood-based and gypsum panels in combination | 2.0 | 1.7 | NL | NL | 20 | 20 |
| Moderately ductile cross-laminated timber shear walls: platform-type construction | 2.0 | 1.5 | 30 | 30 | 30 | 20 |
| Limited ductility cross-laminated timber shear walls: platform-type construction | 1.0 | 1.3 | 30 | 30 | 30 | 20 |
| Braced or moment-resisting frames with ductile connections |  |  |  |  |  |  |
| Moderately ductile | 2.0 | 1.5 | NL | NL | 20 | 20 |
| Limited ductility | 1.5 | 1.5 | NL | NL | 15 | 15 |
| Other wood- or gypsum-based SFRSs not listed above | 1.0 | 1.0 | 15 | 15 | NP | NP |
| Masonry Structures Designed and Detailed According to CSA S304 |  |  |  |  |  |  |
| Ductile shear walls | 3.0 | 1.5 | NL | NL | 60 | 40 |
| Moderately ductile shear walls | 2.0 | 1.5 | NL | NL | 60 | 40 |
| Conventional construction |  |  |  |  |  |  |
| Shear walls | 1.5 | 1.5 | NL | 60 | 30 | 15 |
| Moment-resisting frames | 1.5 | 1.5 | NL | 30 | NP | NP |
| Unreinforced masonry | 1.0 | 1.0 | 30 | 15 | NP | NP |
| Other masonry SFRSs not listed above | 1.0 | 1.0 | 15 | NP | NP | NP |
| Cold-Formed Steel Structures Designed and Detailed According to CSA S136 |  |  |  |  |  |  |
| Shear walls |  |  |  |  |  |  |
| Screw-connected shear walls – wood-based panels | 2.5 | 1.7 | 20 | 20 | 20 | 20 |
| Screw-connected shear walls – wood-based and gypsum panels in combination | 1.5 | 1.7 | 20 | 20 | 20 | 20 |
| Diagonal strap concentrically braced walls |  |  |  |  |  |  |
| Limited ductility | 1.9 | 1.3 | 20 | 20 | 20 | 20 |
| Conventional construction | 1.2 | 1.3 | 15 | 15 | NP | NP |
| Other cold-formed SFRSs not defined above | 1.0 | 1.0 | 15 | 15 | NP | NP |

Notes to Table 4.1.8.9.:

(1) See Article 4.1.8.10.

(2) NP = system is not permitted.

NL = system is permitted and not limited in height as an SFRS.

Numbers in this Table are maximum height limits above grade, in m.

Height may be limited in other Parts of the Code.

The most stringent requirement governs.

(3) Higher design force levels are prescribed in CSA S16 for some heights of buildings.

(4) See Note A-Table 4.1.8.9.

(5) Frames are limited to a maximum of 2 storeys.

(6) The maximum height limit is permitted to be increased to 15 m where IES(1.0) ≤ 0.3.

(7) Frames are limited to a maximum of 3 storeys.

4.1.8.10. Additional System Restrictions

1)   Except as required by Clause (2)(b), structures with a Type 6 irregularity, Discontinuity in Capacity - Weak Storey, as described in Table 4.1.8.6., are not permitted unless the Seismic Category is SC1 and the forces used for design of the SFRS are multiplied by RdRo.

2)   Post-disaster buildings shall

a)   not have Type 1, 3, 4, 5, 7, 9 or 10 irregularities as described in Table 4.1.8.6., where the Seismic Category is SC3 or SC4,

b)   not have a Type 6 irregularity as described in Table 4.1.8.6.,

c)   have an SFRS with an Rd of 2.0 or greater,

d)   where they are constructed with concrete or masonry shear walls, have no storey with a lateral stiffness that is less than that of the storey above it, and

e)   where they are constructed with other types of SFRS, have no storey for which the interstorey deflection under lateral earthquake forces divided by the interstorey height, hs, is greater than that of the storey above it.

3)   High Importance Category buildings shall

a)   not have Type 1, 3, 4, 5, 7, 9 or 10 irregularities as described in Table 4.1.8.6., where the Seismic Category is SC4,

b)   not have a Type 6 irregularity as described in Table 4.1.8.6.,

c)   have an SFRS with an Rd of at least

i)   2.0 where the Seismic Category is SC4, and

ii)   1.5 otherwise,

d)   where they are constructed with concrete or masonry shear walls, have no storey with a lateral stiffness that is less than that of the storey above it, and

e)   where they are constructed with other types of SFRS, have no storey for which the interstorey deflection under lateral earthquake forces divided by the interstorey height, hs, is greater than that of the storey above it.

4)   Where the fundamental lateral period, Ta, is greater than or equal to 1.0 s and IES(1.0) is greater than 0.25, shear walls that are other than wood-based and form part of the SFRS shall be continuous from their top to the foundation and shall not have Type 4 or 5 irregularities as described in Table 4.1.8.6.

5)   For buildings in Seismic Category SC3 or SC4 that are constructed with more than 4 storeys of continuous wood construction, timber SFRSs consisting of shear walls with wood-based panels or of braced or moment-resisting frames as defined in Table 4.1.8.9. within the continuous wood construction shall not have Type 4 or 5 irregularities as described in Table 4.1.8.6. (See Note A-4.1.8.10.(5) and (6).)

6)   For buildings in Seismic Category SC3 or SC4 that are constructed with more than 4 storeys of continuous wood construction, timber SFRSs consisting of moderately ductile or limited ductility cross-laminated timber shear walls, platform-type construction, as defined in Table 4.1.8.9. within the continuous wood construction shall not have Type 4, 5, 6, 8, 9 or 10 irregularities as described in Table 4.1.8.6. (See Note A-4.1.8.10.(5) and (6).)

7)   The ratio α for a Type 9 irregularity as described in Table 4.1.8.6. shall be determined independently for each orthogonal direction using the following equation:

where

QG   = gravity-induced lateral demand on the SFRS at the critical level of the yielding system, and

Qy   = the resistance of the yielding mechanism required to resist the earthquake loads, which need not be taken as less than Ro multiplied by the specified lateral earthquake force as determined in Article 4.1.8.11. or 4.1.8.12., as appropriate.

(See Note A-4.1.8.10.(7).)

8)   For buildings with a Type 9 irregularity as described in Table 4.1.8.6. and where IES(0.2) is equal to or greater than 0.5, deflections determined in accordance with Article 4.1.8.13. shall be multiplied by 1.2.

9)   For buildings where the value of α, as determined in accordance with Sentence (7), exceeds twice the appropriate limit specified in Table 4.1.8.6. for a Type 9 irregularity and where IES(0.2) is equal to or greater than 0.5, a Non-linear Dynamic Analysis of the structure shall be carried out in accordance with Article 4.1.8.12. and the following criteria:

a)   the analysis shall account for the effects of the vertical response of the building mass,

b)   the analysis shall account for the effects of the vertical response of building components that undergo a vertical displacement when displaced laterally,

c)   the analysis shall use vertical ground motion time histories that are compatible with horizontal ground motion time histories scaled to the target response spectrum and that are applied concurrently with the horizontal ground motion time histories,

d)   the largest interstorey deflection at any level of the building as determined from the analysis shall not be greater than 60% of the appropriate limit stated in Sentence 4.1.8.13.(3), and

e)   the results of an analysis using the ground motion time histories in Clause (c) multiplied by 1.5 shall satisfy the non-linear acceptance criteria.

(See Note A-4.1.8.10.(9).)

10)   The design of buildings in Seismic Category SC3 or SC4 with a Type 10 irregularity as described in Table 4.1.8.6. shall satisfy the following requirements:

a)    the structure shall be designed to resist the additional earthquake forces due to the vertical accelerations of the mass supported by inclined vertical members (see Note A-4.1.8.10.(10)(a)), and

b)   the effects of the horizontal and vertical movements of inclined vertical members, while undergoing earthquake-induced deformations, on the floor systems they support shall be considered in the design of the building and accounted for in the application of Sentence 4.1.8.3.(5).

4.1.8.11. Equivalent Static Force Procedure for Structures Satisfying the Conditions of Article 4.1.8.7.

1)   The static loading due to earthquake motion shall be determined according to the procedures given in this Article.

2)   Except as provided in Sentence (12), the specified lateral earthquake force, V, shall be calculated using the following formula:

except

a)   for walls, coupled walls and wall-frame systems, V shall not be less than

b)   for moment-resisting frames, braced frames, and other systems, V shall not be less than

c)   for buildings located on a site designated as other than XF and having an SFRS with an Rd equal to or greater than 1.5, V need not be greater than the larger of

3)   Except as provided in Sentence (4), the fundamental lateral period, Ta, in the direction under consideration in Sentence (2), shall be determined as:

a)   for moment-resisting frames that resist 100% of the lateral earthquake forces and where the frame is not enclosed by or adjoined by more rigid elements that would tend to prevent the frame from resisting lateral forces:

i)   0.085(hn)3/4 for steel moment frames,

ii)   0.075(hn)3/4 for concrete moment frames, or

iii)   0.1N for other moment frames,

b)   0.025hn for braced frames,

c)   0.05(hn)3/4 for shear wall and other structures, or

d)   other established methods of mechanics using a structural model that complies with the requirements of Sentence 4.1.8.3.(8), except that

i)   for moment-resisting frames, Ta shall not be taken as greater than 1.5 times that determined in Clause (a),

ii)   for braced frames, Ta shall not be taken as greater than 2.0 times that determined in Clause (b),

iii)   for shear wall structures, Ta shall not be taken as greater than 2.0 times that determined in Clause (c),

iv)   for other structures, Ta shall not be taken as greater than that determined in Clause (c), and

v)   for the purpose of calculating the deflections, the period without the upper limit specified in Subclauses (d)(i) to (d)(iv) may be used, except that, for walls, coupled walls and wall-frame systems, Ta shall not exceed 4.0 s, and for moment-resisting frames, braced frames, and other systems, Ta shall not exceed 2.0 s.

(See Note A-4.1.8.11.(3).)

4)   For single-storey buildings with steel deck or wood roof diaphragms, the fundamental lateral period, Ta, in the direction under consideration is permitted to be taken as

a)   0.05(hn)3/4 + 0.004L for shear walls,

b)   0.035hn + 0.004L for steel moment frames and steel braced frames, or

c)   the value obtained from methods of mechanics using a structural model that complies with the requirements of Sentence 4.1.8.3.(8), except that Ta shall not be greater than 1.5 times the value determined in Clause (a) or (b), as applicable,

where L is the shortest length of the diaphragm, in m, between adjacent vertical elements of the SFRS in the direction perpendicular to the direction under consideration.

5)   The weight, W, of the building shall be calculated using the following formula:

6)   The higher mode factor, Mv, and its associated base overturning moment reduction factor, J, shall conform to Table 4.1.8.11.

7)   The specified lateral earthquake force, V, shall be distributed such that

a)   a portion, Ft, is concentrated at the top of the building, where Ft is equal to 0.07TaV but need not exceed 0.25V and may be considered as zero where the fundamental lateral period, Ta, does not exceed 0.7 s, and

b)   the remainder, V − Ft, is distributed along the height of the building, including the top level, in accordance with the following formula:

Table 4.1.8.11.

Higher Mode Factor, Mv, and Base Overturning Moment Reduction Factor, J(1)(2)(3)(4)

Forming Part of Sentence 4.1.8.11.(6)

| S(0.2)/S(5.0) | Mv for Ta ≤ 0.5 | Mv for Ta = 1.0 | Mv for Ta = 2.0 | Mv for Ta ≥ 5.0 | J for Ta ≤ 0.5 | J for Ta = 1.0 | J for Ta = 2.0 | J for Ta ≥ 5.0 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Moment-Resisting Frames |  |  |  |  |  |  |  |  |
| 5 | 1 | 1 | 1 | (5) | 1 | 1 | 0.95 | (5) |
| 20 | 1 | 1 | 1 | (5) | 1 | 0.97 | 0.88 | (5) |
| 40 | 1 | 1 | 1 | (5) | 1 | 0.90 | 0.79 | (5) |
| 70 | 1 | 1 | 1 | (5) | 0.98 | 0.88 | 0.70 | (5) |
| Coupled Walls(6) |  |  |  |  |  |  |  |  |
| 5 | 1 | 1 | 1 | 1(7) | 1 | 1 | 0.95 | 0.80(8) |
| 20 | 1 | 1 | 1 | 1.09(7) | 1 | 0.97 | 0.88 | 0.66(8) |
| 40 | 1 | 1 | 1 | 1.33(7) | 1 | 0.90 | 0.79 | 0.52(8) |
| 70 | 1 | 1 | 1 | 1.90(7) | 0.98 | 0.88 | 0.70 | 0.40(8) |
| Braced Frames |  |  |  |  |  |  |  |  |
| 5 | 1 | 1 | 1 | (5) | 1 | 0.98 | 0.93 | (5) |
| 20 | 1 | 1 | 1 | (5) | 1 | 0.91 | 0.80 | (5) |
| 40 | 1 | 1 | 1 | (5) | 0.91 | 0.82 | 0.72 | (5) |
| 70 | 1 | 1 | 1.19 | (5) | 0.91 | 0.77 | 0.61 | (5) |
| Walls, Wall-Frame Systems |  |  |  |  |  |  |  |  |
| 5 | 1 | 1 | 1 | 1.30(7) | 1 | 1 | 0.85 | 0.59(8) |
| 20 | 1 | 1 | 1.18 | 2.50(7) | 1 | 0.80 | 0.60 | 0.35(8) |
| 40 | 1 | 1.25 | 1.85 | 4.10(7) | 0.80 | 0.59 | 0.42 | 0.23(8) |
| 70 | 1 | 1.25 | 2.30 | 6.40(7) | 0.80 | 0.56 | 0.30 | 0.18(8) |
| Other Systems |  |  |  |  |  |  |  |  |
| 5 | 1 | 1 | 1 | (5) | 1 | 1 | 0.85 | (5) |
| 20 | 1 | 1 | 1.18 | (5) | 1 | 0.80 | 0.60 | (5) |
| 40 | 1 | 1.25 | 1.85 | (5) | 0.80 | 0.59 | 0.44 | (5) |
| 70 | 1 | 1.37 | 2.30 | (5) | 0.80 | 0.56 | 0.30 | (5) |

Notes to Table 4.1.8.11.:

(1) For intermediate values of the spectral ratio S(0.2)/S(5.0), Mv and J shall be obtained by linear interpolation. For spectral ratios less than 5, Mv and J shall be obtained by linear interpolation with their values at a spectral ratio of 0 taken as equal to 1. For spectral ratios greater than 70, Mv and J shall be taken as equal to their values at a spectral ratio of 70.

(2) For intermediate values of the fundamental lateral period, Ta, in cases where S(Ta) is obtained by log–log interpolation, Mv shall be obtained by linear interpolation using the values of Mv obtained in accordance with Note (1). In cases where S(Ta) is obtained by linear interpolation, the product S(Ta)Mv shall be obtained by linear interpolation using the values of Mv obtained in accordance with Note (1).

(3) For intermediate values of the fundamental lateral period, Ta, J shall be obtained by linear interpolation using the values of J obtained in accordance with Note (1).

(4) For a combination of different SFRSs not given in Table 4.1.8.11. that are in the same direction under consideration, use the highest Mv factor of all the SFRSs and the corresponding value of J.

(5) For fundamental lateral periods, Ta , greater than 2.0 s, use the 2.0 s values obtained in accordance with Note (1). See Clause 4.1.8.11.(2)(b).

(6) A “coupled” wall is a wall system with coupling beams, where at least 66% of the base overturning moment resisted by the wall system is carried by the axial tension and compression forces resulting from shear in the coupling beams.

(7) For fundamental lateral periods, Ta, greater than 4.0 s, use the 4.0 s values of S(Ta)Mv obtained by interpolation between 2.0 s and 5.0 s using the value of Mv obtained in accordance with Note (1). See Clause 4.1.8.11.(2)(a).

(8) For fundamental lateral periods, Ta, greater than 4.0 s, use the 4.0 s values of J obtained by interpolation between 2.0 s and 5.0 s using the value of J obtained in accordance with Note (1). See Clause 4.1.8.11.(2)(a).

8)   The structure shall be designed to resist overturning effects caused by the earthquake forces determined in Sentence (7) and the overturning moment at level x, Mx, shall be determined using the following equation:

where

Jx   = 1.0 for hx ≥ 0.6hn, and

Jx   = J + (1 − J)(hx/0.6hn) for hx < 0.6hn,

where

J   = base overturning moment reduction factor conforming to Table 4.1.8.11.

9)   Torsional effects that are concurrent with the effects of the forces determined in Sentence (7) and are caused by the simultaneous actions of the following torsional moments shall be considered in the design of the structure according to Sentence (11):

a)   torsional moments introduced by eccentricity between the centres of mass and resistance and their dynamic amplification, and

b)   torsional moments due to accidental eccentricities.

10)   Torsional sensitivity shall be determined by calculating the ratio Bx for each level x according to the following equation for each orthogonal direction determined independently:

where

B   = maximum of all values of Bx in both orthogonal directions, except that the Bx for one-storey penthouses with a weight less than 10% of the level below need not be considered,

δmax   = maximum storey displacement at the extreme points of the structure at level x in the direction of the earthquake induced by the forces determined in Sentence (7) acting at distances ±0.10Dnx from the centres of mass at each floor, and

δave   = average of the displacements at the extreme points of the structure at level x produced by the forces determined in Sentence (7).

11)   Torsional effects shall be accounted for as follows:

a)   for a building with B ≤ 1.7 or in Seismic Category SC1 or SC2, by applying torsional moments about a vertical axis at each level throughout the building, derived for each of the following load cases considered separately:

i)   Tx = Fx(ex + 0.10Dnx), and

ii)   Tx = Fx(ex − 0.10Dnx)

where Fx is determined in accordance with Sentence (7) and where each element of the building is designed for the most severe effect of the above load cases, or

b)   for a building with B > 1.7 in Seismic Category SC3 or SC4, by a Dynamic Analysis Procedure as specified in Article 4.1.8.12.

12)   Where the fundamental lateral period, Ta, is determined in accordance with Clause (3)(d) and the building is constructed with more than 4 storeys of continuous wood construction and has a timber SFRS consisting of shear walls with wood-based panels or of braced or moment-resisting frames as defined in Table 4.1.8.9., the specified lateral earthquake force, V, as determined in Sentence (2) shall be multiplied by 1.2 but need not exceed the value determined by using Clause (2)(c). (See Note A-4.1.8.10.(5) and (6).)

4.1.8.12. Dynamic Analysis Procedure

1)   Except as provided in Articles 4.1.8.19. and 4.1.8.21., the Dynamic Analysis Procedure shall be in accordance with one of the following methods:

a)   Linear Dynamic Analysis by either the Modal Response Spectrum Method or the Numerical Integration Linear Time History Method using a structural model that complies with the requirements of Sentence 4.1.8.3.(8) (see Note A-4.1.8.12.(1)(a)), or

b)   Non-linear Dynamic Analysis, in which case a special study shall be performed (see Note A-4.1.8.12.(1)(b)).

2)   The spectral acceleration values used in the Modal Response Spectrum Method shall be the design spectral acceleration values, S(T), defined in Sentence 4.1.8.4.(6).

3)   The ground motion time histories used in the Numerical Integration Linear Time History Method shall be compatible with a response spectrum constructed from the design spectral acceleration values, S(T), defined in Sentence 4.1.8.4.(6). (See Note A-4.1.8.12.(3).)

4)   The effects of accidental torsional moments acting concurrently with the lateral earthquake forces that cause them shall be accounted for by the following methods:

a)   the static effects of torsional moments due to (±0.10Dnx)Fx at each level x, where Fx is either determined from the elastic dynamic analysis or determined from Sentence 4.1.8.11.(7) multiplied by RdRo/IE, shall be combined with the effects determined by dynamic analysis (see Note A-4.1.8.12.(4)(a)), or

b)   if B, as defined in Sentence 4.1.8.11.(10), is less than 1.7, it is permitted to use a three-dimensional dynamic analysis with the centres of mass shifted by a distance of −0.05Dnx and +0.05Dnx.

5)   Except as provided in Sentence (6), the adjusted elastic base shear, Ved, shall be equal to the elastic base shear, Ve, obtained from a Linear Dynamic Analysis.

6)   For buildings located on a site designated as other than XF that have an SFRS with Rd equal to or greater than 1.5, the elastic base shear, Ve, obtained from a Linear Dynamic Analysis may be multiplied by the larger of the following factors to obtain Ved:

7)   Ved shall be multiplied by the earthquake importance factor, IE, as determined in Article 4.1.8.5., and shall be divided by RdRo, as determined in Article 4.1.8.9., to obtain the specified lateral earthquake force, Vd.

8)   Except as required by Sentence (9) or (12), if Vd, as determined in Sentence (7), is less than 80% of V, as determined in Article 4.1.8.11., Vd shall be taken as 0.8V.

9)   For irregular structures requiring dynamic analysis in accordance with Article 4.1.8.7., Vd shall be taken as the larger of Vd, as determined in Sentence (7), and 100% of V, as determined in Article 4.1.8.11.

10)   Except as required by Sentence (11), the values of elastic storey shears, storey forces, member forces, and deflections obtained from the Linear Dynamic Analysis, including the effect of accidental torsion determined in Sentence (4), shall be multiplied by Vd/Ve to determine their design values.

11)   For the purpose of calculating deflections, it is permitted to use a value of V based on the value of Ta determined in Clause 4.1.8.11.(3)(d) to obtain Vd in Sentences (8) and (9).

12)   For buildings constructed with more than 4 storeys of continuous wood construction, having a timber SFRS consisting of shear walls with wood-based panels or braced or moment-resisting frames as defined in Table 4.1.8.9., and whose fundamental lateral period, Ta, is determined in accordance with Clause 4.1.8.11.(3)(d), Vd shall be taken as the larger of Vd, as determined in Sentence (7), and 100% of V, as determined in Article 4.1.8.11. (See Note A-4.1.8.10.(5) and (6).)

4.1.8.13. Deflections and Drift Limits

1)   Except as provided in Sentences (5) and (6), lateral deflections of a structure shall be calculated in accordance with the loads and requirements defined in this Subsection.

2)   Lateral deflections obtained from a linear elastic analysis using the methods given in Articles 4.1.8.11. and 4.1.8.12. and incorporating the effects of torsion, including accidental torsional moments, shall be multiplied by RdRo/IE and increased as required in Sentences 4.1.8.10.(8) and 4.1.8.16.(1) to give realistic values of anticipated deflections.

3)   Based on the lateral deflections calculated in Sentences (2), (5) and (6), the largest interstorey deflection at any level shall be limited to 0.01hs for post-disaster buildings, 0.02hs for High Importance Category buildings, and 0.025hs for all other buildings.

4)   The deflections calculated in Sentence (2) shall be used to account for sway effects as required by Sentence 4.1.3.2.(12). (See Note A-4.1.8.13.(4).)

5)   The lateral deflections of a seismically isolated structure shall be calculated in accordance with Article 4.1.8.20.

6)   The lateral deflections of a structure with supplemental energy dissipation shall be calculated in accordance with Article 4.1.8.22.

4.1.8.14. Structural Separation

1)   Adjacent structures shall be

a)   separated by a distance equal to at least the square root of the sum of the squares of their individual deflections calculated in Sentence 4.1.8.13.(2), or

b)   connected to each other.

2)   The method of connection required in Sentence (1) shall take into account the mass, stiffness, strength, ductility and anticipated motion of the connected buildings and the character of the connection.

3)   Rigidly connected buildings shall be assumed to have the lowest RdRo value of the buildings connected.

4)   Buildings with non-rigid or energy-dissipating connections require special studies.

4.1.8.15. Design Provisions

1)   Except as provided in Sentences (2) and (3), diaphragms, collectors, chords, struts and connections shall be designed so as not to yield, and the design shall account for the shape of the diaphragm, including openings, and for the forces generated in the diaphragm due to the following cases, whichever one governs:

a)   forces determined in Article 4.1.8.11. or 4.1.8.12. applied to the diaphragm are increased to reflect the lateral load capacity of the SFRS, plus forces in the diaphragm due to the transfer of forces between elements of the SFRS associated with the lateral load capacity of such elements and accounting for discontinuities and changes in stiffness in these elements, or

b)   a minimum force corresponding to the specified lateral earthquake force, V, divided by N for the diaphragm at level x.

(See Note A-4.1.8.15.(1).)

2)   Steel deck roof diaphragms in buildings of less than 4 storeys or wood diaphragms that are designed and detailed according to the applicable referenced design standards to exhibit ductile behaviour shall meet the requirements of Sentence (1), except that they may yield and the forces shall be

a)   for wood diaphragms acting in combination with vertical wood shear walls, equal to the specified lateral earthquake force, V,

b)   for wood diaphragms acting in combination with other SFRSs, not less than the force corresponding to RdRo = 2.0, and

c)   for steel deck roof diaphragms, not less than the force corresponding to RdRo = 2.0.

3)   Where diaphragms are designed in accordance with Sentence (2), the struts shall be designed in accordance with Clause (1)(a), and the collectors, chords and connections between the diaphragms and the vertical elements of the SFRS shall be designed for forces corresponding to the capacity of the diaphragms in accordance with the applicable CSA standards. (See Note A-4.1.8.15.(3).)

4)   For single-storey buildings with steel deck or wood roof diaphragms designed with a value of Rd greater than 1.5 and where the calculated maximum relative deflection, ΔD, of the diaphragm under lateral loads exceeds 50% of the average storey drift, ΔB, of the adjoining vertical elements of the SFRS, dynamic magnification of the inelastic response due to the in-plane diaphragm deformations shall be accounted for in the design as follows:

a)   the vertical elements of the SFRS shall be designed and detailed to any one of the following:

i)   to accommodate the anticipated magnified lateral deformations taken as RoRd(ΔB + ΔD) − RoΔD,

ii)   to resist the forces magnified by Rd(1 + ΔD/ΔB)/(Rd + ΔD/ΔB), or

iii)   by a special study, and

b)   the roof diaphragm and chords shall be designed for in-plane shears and moments determined while taking into consideration the inelastic higher mode response of the structure.

(See Note A-4.1.8.15.(4).)

5)   Where the Seismic Category is SC3 or SC4, the elements supporting any discontinuous wall, column or braced frame shall be designed for the lateral load capacity of the components of the SFRS they support. (See Note A-4.1.8.15.(5).)

6)   Where structures have vertical variations of RdRo satisfying Sentence 4.1.8.9.(4), the elements of the SFRS below the level where the change in RdRo occurs shall be designed for the forces associated with the lateral load capacity of the SFRS above that level. (See Note A-4.1.8.15.(6).)

7)   Where earthquake effects can produce forces in a column or wall due to lateral loading along both orthogonal axes, account shall be taken of the effects of potential concurrent yielding of other elements framing into the column or wall from all directions at the level under consideration and as appropriate at other levels. (See Note A-4.1.8.15.(7).)

8)   The design forces associated with the lateral capacity of the SFRS need not exceed the forces determined in accordance with Sentence 4.1.8.7.(1) with RdRo taken as 1.0, unless otherwise provided by the applicable referenced design standards for elements, in which case the design forces associated with the lateral capacity of the SFRS need not exceed the forces determined in accordance with Sentence 4.1.8.7.(1) with RdRo taken as less than or equal to 1.3. (See Note A-4.1.8.15.(8).)

9)   Foundations need not be designed to resist the lateral load overturning capacity of the SFRS, provided the design and the Rd and Ro for the type of SFRS used conform to Table 4.1.8.9. and that the foundation is designed in accordance with Sentence 4.1.8.16.(4).

10)   Foundation displacements and rotations shall be considered as required by Sentence 4.1.8.16.(1).

4.1.8.16. Foundation Provisions

1)   The increased displacements of the structure resulting from foundation movement shall be shown to be within acceptable limits for both the SFRS and the structural framing elements not considered to be part of the SFRS. (See Note A-4.1.8.16.(1).)

2)   Except as provided in Sentences (3) and (4), foundations shall be designed to have factored shear and overturning resistances greater than the lateral load capacity of the SFRS. (See Note A-4.1.8.16.(2).)

3)   The shear and overturning resistances of the foundation determined using a bearing stress equal to 1.5 times the factored bearing strength of the soil or rock and all other resistances equal to 1.3 times the factored resistances need not exceed the forces determined in Sentence 4.1.8.7.(1) using RdRo = 1.0, except that the factor of 1.3 shall not apply to the portion of the resistance to uplift or overturning resulting from gravity loads.

4)   A foundation is permitted to have a factored overturning resistance less than the lateral load overturning capacity of the supported SFRS, provided the following requirements are met:

a)   neither the foundation nor the supported SFRS are constrained against rotation, and

b)   the design overturning moment of the foundation is

i)   not less than 75% of the overturning capacity of the supported SFRS, and

ii)   not less than that determined in Sentence 4.1.8.7.(1) using RdRo = 2.0.

(See Note A-4.1.8.16.(4).)

5)   The design of foundations shall be such that they are capable of transferring earthquake loads and effects between the building and the ground without exceeding the capacities of the soil and rock.

6)   Where the Seismic Category is SC3 or SC4, the following requirements shall be satisfied:

a)   piles or pile caps, drilled piers, and caissons shall be interconnected by continuous ties in not less than two directions (see Note A-4.1.8.16.(6)(a)),

b)   piles, drilled piers, and caissons shall be embedded a minimum of 100 mm into the pile cap or structure, and

c)   piles, drilled piers, and caissons, other than wood piles, shall be connected to the pile cap or structure for a minimum tension force equal to 0.15 times the factored compression load on the pile.

7)   Where the Seismic Category is SC3 or SC4, basement walls shall be designed to resist earthquake lateral pressures from backfill or natural ground. (See Note A-4.1.8.16.(7).)

8)   Where the Seismic Category is SC4, the following requirements shall be satisfied:

a)   piles, drilled piers, or caissons shall be designed and detailed to accommodate cyclic inelastic behaviour when the design moment in the element due to earthquake effects is greater than 75% of its moment capacity (see Note A-4.1.8.16.(8)(a)), and

b)   spread footings founded on soil designated as XV, where Vs30 is less than or equal to 180 m/s, XE or XF shall be interconnected by continuous ties in not less than two directions.

9)   Each segment of a tie between elements that is required by Clause (6)(a) or (8)(b) shall be designed to carry by tension or compression a horizontal force at least equal to the greatest factored pile cap or column vertical load in the elements it connects, multiplied by a factor of 0.1IES(0.2), unless it can be demonstrated that equivalent restraints can be provided by other means. (See Note A-4.1.8.16.(9).)

10)   The potential for liquefaction of the soil and its consequences, such as significant ground displacement and loss of soil strength and stiffness, shall be evaluated based on the ground motion parameters referenced in Subsection 1.1.3., as modified by Article 4.1.8.4., and shall be taken into account in the design of the structure and its foundations. (See Note A-4.1.8.16.(10).)

4.1.8.17. Site Stability

1)   The potential for slope instability and its consequences, such as slope displacement, shall be evaluated based on site-specific material properties and ground motion parameters referenced in Subsection 1.1.3., as modified by Article 4.1.8.4., and shall be taken into account in the design of the structure and its foundations. (See Note A-4.1.8.17.(1).)

4.1.8.18. Elements of Structures, Non-structural Components and Equipment

(See Note A-4.1.8.18.)

1)   Except as provided in Sentences (2), (7) and (16), elements and components of buildings described in Table 4.1.8.18. and their connections to the structure shall be designed to accommodate the building deflections calculated in accordance with Article 4.1.8.13. and the element or component deflections calculated in accordance with Sentence (9), and shall be designed for a specified lateral earthquake force, Vp, distributed according to the distribution of mass:

where

S(0.2)   = design spectral acceleration value at a period of 0.2 s, as defined in Sentence 4.1.8.4.(6),

IE   = earthquake importance factor for the building, as defined in Article 4.1.8.5.,

Sp   = CpArAx/Rp (the maximum value of Sp shall be taken as 4.0 and the minimum value of Sp shall be taken as 0.7), where

Cp = element or component factor from Table 4.1.8.18.,

Ar = element or component force amplification factor from Table 4.1.8.18.,

Ax = height factor (1 + 2hx/hn),

Rp = element or component response modification factor from Table 4.1.8.18., and

Wp   = weight of the component or element.

Table 4.1.8.18.

Elements of Structures and Non-structural Components and Equipment(1)

Forming Part of Sentences 4.1.8.18.(1) to (3), (6), (7) and (16), and Clauses 4.1.8.23.(2)(c) and (3)(c)

| Category | Part or Portion of Building | Cp | Ar | Rp |
| --- | --- | --- | --- | --- |
| Architectural and Structural Components |  |  |  |  |
| 1 | All exterior and interior walls, and cladding panels, except those in Category 2 or 3 | 1.00 | 1.00 | 2.50 |
| 2 | Cantilever parapet and other cantilever walls, including cantilever cladding panels, except retaining walls | 1.00 | 2.50 | 2.50 |
| 3 | Exterior and interior ornamentations and appendages | 1.00 | 2.50 | 2.50 |
| 4 | Floors and roofs acting as diaphragms(2) | – | – | – |
| 5 | Towers, chimneys, smokestacks and penthouses when connected to or forming part of a building | 1.00 | 2.50 | 2.50 |
| 6 | Horizontally cantilevered floors, balconies, beams, etc. | 1.00 | 1.00 | 2.50 |
| 7 | Suspended ceilings, light fixtures and other attachments to ceilings with independent vertical support | 1.00 | 1.00 | 2.50 |
| 8 | Masonry veneer connections | 1.00 | 1.00 | 1.50 |
| 9 | Access floors | 1.00 | 1.00 | 2.50 |
| 10 | Masonry or concrete fences more than 1.8 m tall | 1.00 | 1.00 | 2.50 |
| Mechanical and Electrical Components |  |  |  |  |
| 11 | Machinery, fixtures, equipment and tanks (including contents) |  |  |  |
|  | that are rigid and rigidly connected | 1.00 | 1.00 | 1.25 |
|  | that are flexible or flexibly connected | 1.00 | 2.50 | 2.50 |
| 12 | Machinery, fixtures, equipment and tanks (including contents) containing toxic or explosive materials, materials having a flash point below 38°C or firefighting fluids |  |  |  |
|  | that are rigid and rigidly connected | 1.50 | 1.00 | 1.25 |
|  | that are flexible or flexibly connected | 1.50 | 2.50 | 2.50 |
| 13 | Flat bottom tanks (including contents) attached directly to a floor at or below grade within a building | 0.70 | 1.00 | 2.50 |
| 14 | Flat bottom tanks (including contents) attached directly to a floor at or below grade within a building containing toxic or explosive materials, materials having a flash point below 38°C or firefighting fluids | 1.00 | 1.00 | 2.50 |
| 15 | Pipes, ducts (including contents) | 1.00 | 1.00 | 3.00 |
| 16 | Pipes, ducts (including contents) containing toxic or explosive materials | 1.50 | 1.00 | 3.00 |
| 17 | Electrical cable trays, bus ducts, conduits | 1.00 | 2.50 | 5.00 |
| Other System Components |  |  |  |  |
| 18 | Rigid components with ductile material and connections | 1.00 | 1.00 | 2.50 |
| 19 | Rigid components with non-ductile material or connections | 1.00 | 1.00 | 1.00 |
| 20 | Flexible components with ductile material and connections | 1.00 | 2.50 | 2.50 |
| 21 | Flexible components with non-ductile material or connections | 1.00 | 2.50 | 1.00 |
| 22 | Elevators and escalators(3) |  |  |  |
|  | machinery and equipment | as per Category 11 |  |  |
|  | elevator rails | 1.00 | 1.00 | 2.50 |
| 23 | Floor-mounted steel pallet storage racks(4) | 1.00 | 2.50 | 2.50 |
| 24 | Floor-mounted steel pallet storage racks on which are stored toxic or explosive materials or materials having a flash point below 38°C(4) | 1.50 | 2.50 | 2.50 |

Notes to Table 4.1.8.18.:

(1) See Note A-Table 4.1.8.18.

(2) See Sentence (8).

(3) See also the Safety Standards Act and pursuant regulations.

(4) See Sentence (13) and Note A-Table 4.1.8.18.

2)   For buildings in Seismic Category SC1 or SC2, other than post-disaster buildings, seismically isolated buildings, and buildings with supplemental energy dissipation systems, the requirements of Sentence (1) need not apply to Categories 6 through 22 of Table 4.1.8.18.

3)   For the purpose of applying Sentence (1) for Categories 11 and 12 of Table 4.1.8.18., elements or components shall be assumed to be flexible or flexibly connected unless it can be shown that the fundamental period of the element or component and its connection is less than or equal to 0.06 s, in which case the element or component is classified as being rigid and rigidly connected.

4)   The weight of access floors shall include the dead load of the access floor and the weight of permanent equipment, which shall not be taken as less than 25% of the floor live load.

5)   When the mass of a tank plus its contents or the mass of a flexible or flexibly connected piece of machinery, fixture or equipment is greater than 10% of the mass of the supporting floor, the lateral forces shall be determined by rational analysis.

6)   Forces shall be applied in the horizontal direction that results in the most critical loading for design, except for Category 6 of Table 4.1.8.18., where the forces shall be applied up and down vertically.

7)   Connections to the structure of elements and components listed in Table 4.1.8.18. shall be designed to support the component or element for gravity loads, shall conform to the requirements of Sentence (1), and shall also satisfy these additional requirements:

a)   except as provided in Sentence (17), friction due to gravity loads shall not be considered to provide resistance to earthquake forces,

b)   Rp for non-ductile connections, such as adhesives or power-actuated fasteners, shall be taken as 1.0,

c)   Rp for shallow post-installed mechanical, post-installed adhesive, and cast-in-place anchors in concrete shall be 1.5, where shallow anchors are those with a ratio of embedment length to diameter of less than 8,

d)   post-installed mechanical, drop-in and adhesive anchors in concrete shall be pre-qualified for seismic applications by cyclic load testing in accordance with

i)   CSA A23.3, “Design of concrete structures,” and

ii)   ACI 355.2, “Qualification of Post-Installed Mechanical Anchors in Concrete (ACI 355.2-19) and Commentary,” or ACI 355.4, “Qualification of Post-Installed Adhesive Anchors in Concrete (ACI 355.4-19) and Commentary,” as applicable,

e)   post-installed mechanical and adhesive anchors in masonry and post-installed mechanical anchors in structural steel shall be pre-qualified for seismic applications by cyclic tension load testing (see Note A-4.1.8.18.(7)(e)),

f)   power-actuated fasteners shall not be used for cyclic tension loads,

g)   connections for non-structural elements or components of Category 1, 2 or 3 of Table 4.1.8.18. attached to the side of a building and above the first level above grade shall satisfy the following requirements:

i)   for connections where the body of the connection is ductile, the body shall be designed for values of Cp, Ar and Rp given in Table 4.1.8.18., and all of the other parts of the connection, such as anchors, welds, bolts and inserts, shall be capable of developing 2.0 times the nominal yield resistance of the body of the connection, and

ii)   connections where the body of the connection is not ductile shall be designed for values of Cp = 2.0, Rp = 1.0 and Ar given in Table 4.1.8.18., and

h)   a ductile connection is one where the body of the connection is capable of dissipating energy through cyclic inelastic behaviour.

8)   Floors and roofs acting as diaphragms shall satisfy the requirements for diaphragms stated in Article 4.1.8.15.

9)   Lateral deflections of elements or components shall be based on the loads defined in Sentence (1) and lateral deflections obtained from an elastic analysis shall be multiplied by Rp/IE to give realistic values of the anticipated deflections.

10)   The elements or components shall be designed so as not to transfer to the structure any forces unaccounted for in the design, and rigid elements such as walls or panels shall satisfy the requirements of Sentence 4.1.8.3.(6).

11)   Seismic restraint for suspended equipment, pipes, ducts, electrical cable trays, etc. shall be designed to meet the force and displacement requirements of this Article and be constructed in a manner that will not subject hanger rods to bending.

12)   Isolated suspended equipment and components, such as pendent lights, may be designed as a pendulum system provided that adequate chains or cables capable of supporting 2.0 times the weight of the suspended component are provided and the deflection requirements of Sentence (10) are satisfied.

13)   Free-standing steel pallet storage racks are permitted to be designed according to CSA A344.2, “Standard for the design and construction of steel storage racks,” and to resist earthquake effects using rational analysis, provided the design achieves the minimum performance level required by Subsection 4.1.8. (See Note A-4.1.8.18.(13) and 4.4.3.1.(1).)

14)   Except as provided in Sentence (15), the relative displacement of glass in glazing systems, Dfallout, shall be equal to the greater of

a)   Dfallout ≥ 1.25IEDp, where

Dfallout   = relative displacement at which glass fallout occurs, and

Dp   = relative earthquake displacement that the component must be designed to accommodate, calculated in accordance with Article 4.1.8.13. and applied over the height of the glass component, or

b)   13 mm.

(See Note A-4.1.8.18.(14) and (15).)

15)   Glass need not comply with Sentence (14), provided at least one of the following conditions is met:

a)   the Seismic Category is SC1 or SC2,

b)   the glass has sufficient clearance from its frame such that Dclear ≥ 1.25Dp calculated as follows:

where

Dclear   = relative horizontal displacement measured over the height of the glass panel, which causes initial glass-to-frame contact,

C1   = average of the clearances on both sides between the vertical glass edges and the frame,

hp   = height of the rectangular glass panel,

C2   = averages of the top and bottom clearances between the horizontal glass edges and the frame, and

bp   = width of the rectangular glass panel,

c)   the glass is fully tempered, monolithic, installed in a non-post-disaster building, and no part of the glass is located more than 3 m above a walking surface, or

d)   the glass is annealed or heat-strengthened laminated glass in a single thickness with an interlayer no less than 0.76 mm and captured mechanically in a wall system glazing pocket with the perimeter secured to the frame by a wet, glazed, gunable, curing, elastomeric sealant perimeter bead of 13 mm minimum glass contact width.

(See Note A-4.1.8.18.(14) and (15).)

16)   For structures with supplemental energy dissipation, elements and components of buildings described in Table 4.1.8.18. and their connections to the structure shall be designed for a specified lateral earthquake force, Vp, determined at each floor level as follows:

where

Ssed   = peak spectral acceleration, Sa(T,X), in the period range of T = 0 s to T = 0.5 s determined from the mean 5%-damped floor spectral acceleration values by averaging the individual 5%-damped floor response spectra at the centroid of the floor area at that floor level determined using Non-linear Dynamic Analysis, and

IE, Cp, Ar, Rp, Wp   = as defined in Sentence (1).

(See Note A-4.1.8.18.(16).)

17)   For a ballasted array of interconnected solar panels mounted on a roof, where IES(0.2) is less than or equal to 1.0, friction due to gravity loads is permitted to be considered to provide resistance to seismic forces, provided

a)   the roof is not normally occupied,

b)   the roof is surrounded by a parapet extending from the roof surface to not less than the greater of

i)   150 mm above the centre of mass of the array, and

ii)   400 mm above the roof surface,

c)   the height of the centre of mass of the array above the roof surface is less than the lesser of

i)   900 mm, and

ii)   one half of the smallest plan dimension of the supporting base of the array,

d)   the roof slope at the location of the array is less than or equal to 3°,

e)   the factored friction resistance calculated using the kinetic friction coefficient determined in accordance with Sentence (18) and a resistance factor of 0.7 is greater than or equal to the specified lateral earthquake force, Vp, on the array determined in accordance with Sentence (1) using values of Ar = 1.0, Ax = 3.0, Cp = 1.0, and Rp = 1.25,

f)   the minimum clearance between the array and other arrays or fixed objects is the greater of

i)   225 mm, and

ii)   1 500(IES(0.2) − 0.4)2, in mm, and

g)   the minimum clearance between the array and the roof parapet is the greater of

i)   450 mm, and

ii)   3 000(IES(0.2) − 0.4)2, in mm.

18)   For the purpose of Clause (17)(e), the kinetic friction coefficient shall be determined in accordance with ASTM G115, “Standard Guide for Measuring and Reporting Friction Coefficients,” through experimental testing that

a)   is carried out by an accredited laboratory on a full-scale array or a prototype of the array,

b)   models the interface between the supporting base of the array and the roof surface, and

c)   accounts for the adverse effects of anticipated climatic conditions on the friction resistance.

(See Note A-4.1.8.18.(18).)

4.1.8.19. Seismic Isolation

1)   For the purposes of this Article and Article 4.1.8.20., the following terms shall have the meanings stated herein:

a)   “seismic isolation” is an alternative seismic design concept that consists of installing an isolation system with low horizontal stiffness, thereby substantially increasing the fundamental period of the structure;

b)   “isolation system” is a collection of structural elements at the level of the isolation interface that includes all individual isolator units, all structural elements that transfer force between elements of the isolation system, all connections to other structural elements, and may also include a wind-restraint system, energy-dissipation devices, and a displacement restraint system;

c)   “seismically isolated structure” includes the upper portion of the structure above the isolation system, the isolation system, and the portion of the structure below the isolation system;

d)   “isolator unit” is a structural element of the isolation system that permits large lateral deformations under lateral earthquake forces and is characterized by vertical-load-carrying capability combined with increased horizontal flexibility and high vertical stiffness, energy dissipation (hysteretic or viscous), self-centering capability, and lateral restraint (sufficient elastic stiffness) under non-seismic service lateral loads;

e)   “isolation interface” is the boundary between the isolated upper portion of the structure above the isolation system and the lower portion of the structure below the isolation system; and

f)   “wind-restraint system” is the collection of structural elements of the isolation system that provides restraint of the seismically isolated structure for wind loads and is permitted to be either an integral part of the isolator units or a separate device.

2)   Every seismically isolated structure and every portion thereof shall be analyzed and designed in accordance with

a)   this Article and Article 4.1.8.20.,

b)   other applicable requirements of this Subsection, and

c)   appropriate engineering principles and current engineering practice.

(See Note A-4.1.8.19.(2))

3)   For the analysis and modeling of the seismically isolated structure, the following criteria shall apply:

a)   a three-dimensional Non-linear Dynamic Analysis of the structure shall be performed in accordance with Article 4.1.8.12. (see Note A-4.1.8.19.(3)(a)),

b)   unless verified from rational analysis, the inherent equivalent viscous damping—excluding the hysteretic damping provided by the isolation system or supplemental energy dissipation devices—used in the analysis shall not be taken as more than 2.5% of the critical damping at the significant modes of vibration,

c)   all individual isolator units shall be modeled with sufficient detail to account for their non-linear force-deformation characteristics, including effects of the relevant loads, and with consideration of variations in material properties over the design life of the structure, and

d)   except for elements of the isolation system, other components of the seismically isolated structure shall be modeled using elastic material properties in accordance with Sentence 4.1.8.3.(8).

4)   The ground motion time histories used in Sentence (3) shall be

a)   appropriately selected and scaled following good engineering practice,

b)   compatible with

i)   a response spectrum derived from the design spectral acceleration values, S(T), defined in Sentence 4.1.8.4.(6) for site designations XV, where Vs30 is greater than 360 m/s, XA, XB and XC, and

ii)   a 5%-damped response spectrum based on a site-specific evaluation for site designations XV, where Vs30 is less than or equal to 360 m/s, XD, XE and XF, and

c)   amplitude-scaled in an appropriate manner over the period range of 0.2T1 to 1.5T1, where T1 is the period of the isolated structure determined using the post-yield stiffness of the isolation system in the horizontal direction under consideration, or the period specified in Sentence 4.1.8.20.(1) if the post-yield stiffness of the isolation system is not well defined.

(See Note A-4.1.8.19.(4) and 4.1.8.21.(5).)

4.1.8.20. Seismic Isolation Design Provisions

1)   The period of the isolated structure, determined using the post-yield stiffness of the isolation system in the horizontal direction under consideration, shall be greater than three times the period of the structure above the isolation interface calculated as a fixed base.

2)   The isolation system shall be configured to produce a restoring force such that the lateral force at the TDD at the centre of mass of the isolated structure above the isolation interface is at least 0.025Wb greater than the lateral force at 50% of the TDD at the same location, in each horizontal direction, where Wb is the portion of W above the isolation interface.

3)   The values of storey shears, storey forces, member forces, and deflections used in the design of all structural framing elements and components of the isolation system shall be obtained from analysis conforming to Sentence 4.1.8.19.(3) using one of the following values, whichever produces the most critical effect:

a)   mean plus IE times the standard deviation of results of all Non-linear Dynamic Analyses, or

b)   √IE times the mean of the results of all Non-linear Dynamic Analyses.

4)   The force-deformation and damping characteristics of the isolation system used in the analysis and design of seismically isolated structures shall be validated by testing at least two full-size specimens of each predominant type and size of isolator unit of the isolation system, which shall include

a)   the individual isolator units,

b)   separate supplemental damping devices, if used, and

c)   separate sacrificial wind-restraint systems, if used.

5)   The force-deformation characteristics and damping value of a representative sample of the isolator units installed in the building shall be validated by tests prior to their installation.

6)   A diaphragm or horizontal structural elements shall provide continuity immediately above the isolation interface to transmit forces due to non-uniform ground motions from one part of the structure to another.

7)   All structural framing elements shall be designed for the forces described in Sentence (3) with RdRo = 1.0, except

a)   for structures with IE < 1.5, all SFRSs shall be detailed in accordance with the requirements for Rd ≥ 1.5 and the applicable referenced design standards, and

b)   for structures with IE = 1.5, all SFRSs shall be detailed in accordance with the requirements for Rd ≥ 2.0 and the applicable referenced design standards.

8)   The height restrictions noted in Table 4.1.8.9. need not apply to seismically isolated structures.

9)   All isolator units shall be

a)   designed for the forces described in Sentence (3), and

b)   able to accommodate the TDD determined at the specific location of each isolator unit.

10)   The isolation system, including a separate wind-restraint system if used, shall limit lateral displacement due to wind loads across the isolation interface to a value equal to that required for the least storey height in accordance with Sentence 4.1.3.5.(3).

4.1.8.21. Supplemental Energy Dissipation

1)   For the purposes of this Article and Article 4.1.8.22., the following terms shall have the meanings stated herein:

a)   “supplemental energy dissipation device” is a dedicated structural element of the supplemental energy dissipation system that dissipates energy due to relative motion of each of its ends or by alternative means, and includes all pins, bolts, gusset plates, brace extensions and other components required to connect it to the other elements of the structure; a device may be classified as either displacement-dependent or velocity-dependent, or a combination thereof, and may be configured to act in either a linear or non-linear manner; and

b)   “supplemental energy dissipation system” is a collection of energy dissipation devices installed in a structure that supplement the energy dissipation of the SFRS.

2)   Every structure with a supplemental energy dissipation system and every portion thereof shall be designed and constructed in accordance with

a)   this Article and Article 4.1.8.22.,

b)   other applicable requirements of this Subsection, and

c)   appropriate engineering principles and current engineering practice.

(See Note A-4.1.8.21.(2).)

3)   Where supplemental energy dissipation devices are used across the isolation interface of a seismically isolated structure, displacements, velocities, and accelerations shall be determined in accordance with Article 4.1.8.20.

4)   For the analysis and modeling of structures with supplemental energy dissipation devices, the following criteria shall apply:

a)   a three-dimensional Non-linear Dynamic Analysis of the structure shall be performed in accordance with Article 4.1.8.12. (see Note A-4.1.8.21.(4)(a)),

b)   for an SFRS with Rd > 1.0, the non-linear hysteretic behaviour of the SFRS shall be explicitly—with sufficient detail—accounted for in the modeling and analysis of the structure,

c)   unless verified from rational analysis, the inherent equivalent viscous damping—excluding the damping provided by the supplemental energy dissipation devices—used in the analysis shall not be taken as more than 2.5% of the critical damping at the significant modes of vibration,

d)   all supplemental energy dissipation devices shall be modeled with sufficient detail to account for their non-linear force deformation characteristics, including effects of the relevant loads, and with consideration of variations in their properties over the design life of the structure, and

e)   except for the SFRS and elements of the supplemental energy dissipation system, other components of the structure shall be modeled using elastic material properties in accordance with Sentence 4.1.8.3.(8).

5)   The ground motion time histories used in Sentence (4) shall be

a)   appropriately selected and scaled following good engineering practice,

b)   compatible with a 5%-damped response spectrum derived from the design spectral acceleration values, S(T), defined in Sentence 4.1.8.4.(6), and

c)   amplitude-scaled in an appropriate manner over the period range of 0.2T1 to 1.5T1, where T1 is the fundamental lateral period of the structure with the supplemental energy dissipation system.

(See Note A-4.1.8.19.(4) and 4.1.8.21.(5).)

4.1.8.22. Supplemental Energy Dissipation Design Considerations

1)   The values of storey shears, storey forces, member forces, and deflections for the design of all structural framing elements and all supplemental energy dissipation devices shall be obtained from analysis conforming to Sentence 4.1.8.21.(4) using one of the following values, whichever produces the most critical effect:

a)   mean plus IE times the standard deviation of the results of all Non-linear Dynamic Analyses, or

b)   √IE times the mean of the results of all Non-linear Dynamic Analyses.

2)   The largest interstorey deflection at any level of the structure as determined in accordance with Sentence (1) shall conform to the limits stated in Sentence 4.1.8.13.(3).

3)   The force-deformation and force-velocity characteristics of the supplemental energy dissipation devices used in the analysis and design of structures with supplemental energy dissipation systems shall be validated by testing at least two full-size specimens of each type of supplementary energy dissipation device.

4)   The force-deformation and force-velocity characteristics and damping values of a representative sample of the supplemental energy dissipation devices installed in the building shall be validated by tests prior to their installation.

5)   All components of a supplemental energy dissipation device, except that portion of the device that dissipates energy, shall be designed to remain elastic.

6)   All structural framing elements shall be designed

a)   for an SFRS with Rd = 1.0, using the forces referred to in Sentence (1) with RdRo = 1.0, except that the SFRS shall be detailed in accordance with the requirements for Rd ≥ 1.5 and the applicable referenced design standards, or

b)   for an SFRS with Rd > 1.0, using the forces referred to in Sentence (1) with RdRo = 1.0, except that the SFRS shall be detailed in accordance with the requirements for the selected Rd and the applicable referenced design standards.

7)   Supplemental energy dissipation devices and other components of the supplemental energy dissipation system shall be designed in accordance with Sentence (1) with consideration of the following:

a)   low-cycle, large-displacement degradation due to earthquake loads,

b)   high-cycle, small-displacement degradation due to wind, thermal, or other cyclic loads,

c)   forces or displacements due to gravity loads,

d)   adhesion of device parts due to corrosion or abrasion, biodegradation, moisture, or chemical exposure,

e)   exposure to environmental conditions, including, but not limited to, temperature, humidity, moisture, radiation (e.g., ultraviolet light), and reactive or corrosive substances (e.g., salt water),

f)   devices subject to failure due to low-cycle fatigue must resist wind forces without slip, movement, or inelastic cycling,

g)   the range of thermal conditions, device wear, manufacturing tolerances, and other effects that cause device properties to vary during the design life of the device, and

h)   connection points of devices must provide sufficient articulation to accommodate simultaneous longitudinal, lateral, and vertical displacements of the supplemental energy dissipation system.

8)   Means of access for inspection and removal for replacement of all supplemental energy dissipation devices shall be provided.

4.1.8.23. Additional Performance Requirements for Post-disaster Buildings, High Importance Category Buildings, and a Subset of Normal Importance Category Buildings

1)   Buildings designed in accordance with Articles 4.1.8.19. to 4.1.8.22. need not comply with this Article.

2)   The design of post-disaster buildings in Seismic Category SC2, SC3 or SC4 shall be verified using 5%-damped spectral acceleration values based on a 5% probability of exceedance in 50 years and shall satisfy the following requirements:

a)   the building shall be shown to behave elastically for a specified lateral earthquake force, V, determined in accordance with Sentence 4.1.8.11.(2) using IE = 1.0 and RdRo = 1.3,

b)   the largest interstorey deflection at any level of the building, as determined in accordance with Sentence 4.1.8.13.(2) using IE = 1.0 and RdRo = 1.0, shall not exceed 0.005hs, and

c)   the connections of elements and components of the building described in Table 4.1.8.18. with Rp > 1.5 shall be shown to behave elastically for a specified lateral earthquake force, Vp, determined in accordance with Sentence 4.1.8.18.(1) using Rp = 1.5.

3)   The design of High Importance Category buildings in Seismic Category SC3 or SC4 shall be verified using 5%-damped spectral acceleration values based on a 10% probability of exceedance in 50 years and shall satisfy the following requirements:

a)   the building shall be shown to behave elastically for a specified lateral earthquake force, V, determined in accordance with Sentence 4.1.8.11.(2) using IE = 1.0 and RdRo = 1.3,

b)   the largest interstorey deflection at any level of the building, as determined in accordance with Sentence 4.1.8.13.(2) using IE = 1.0 and RdRo = 1.0, shall not exceed 0.005hs, and

c)   the connections of elements and components of the building described in Table 4.1.8.18. with Rp > 1.3 shall be shown to behave elastically for a specified lateral earthquake force, Vp, determined in accordance with Sentence 4.1.8.18.(1) using Rp = 1.3.

4)   For Normal Importance Category buildings in Seismic Category SC4 with a height above grade of more than 30 m, the structural framing elements not considered to be part of the SFRS shall be designed to behave elastically for a specified lateral earthquake force, V, determined in accordance with Sentence 4.1.8.11.(2) using spectral acceleration values based on a 10% probability of exceedance in 50 years and RdRo = 1.3.

5)   For the purposes of applying Sentences (2) to (4), torsional moments due to accidental eccentricities need not be considered if B, as determined in accordance with Sentence 4.1.8.11.(10), does not exceed 1.7.

6)   For the purposes of applying Sentences (2) to (4), elements of the SFRS and structural framing elements not considered to be part of the SFRS, when included in the analysis, shall be modeled in accordance with Sentence 4.1.8.3.(8) using elastic properties.

7)   All other requirements of Articles 4.1.8.2. to 4.1.8.18. shall be satisfied in meeting the additional requirements of this Article.

Section  4.2.   Foundations

4.2.1. General

4.2.1.1. Application

1)   This Section applies to excavations and foundation systems for buildings.

4.2.2. Subsurface Investigations, Drawings and Reviews

4.2.2.1. Subsurface Investigation

1)   A subsurface investigation, including groundwater conditions, shall be carried out by or under the direction of a professional engineer having knowledge and experience in planning and executing such investigations to a degree appropriate for the building and its use, the ground and the surrounding site conditions. (See Note A-4.2.2.1.(1).)

4.2.2.2. Drawings

1)   Drawings associated with foundations and excavations shall conform to the appropriate requirements of Section 2.2. of Division C. (See Article 2.2.4.6. of Division C.)

4.2.2.3. Field Review

1)   A field review shall be carried out by the designer or by another suitably qualified person to ascertain that the subsurface conditions are consistent with the design and that construction is carried out in accordance with the design and good engineering practice. (See Note A-4.2.2.3.(1).)

2)   The review required by Sentence (1) shall be carried out

a)   on a continuous basis

i)   during the construction of all deep foundation units with all pertinent information recorded for each foundation unit,

ii)   during the installation and removal of retaining structures and related backfilling operations, and

iii)   during the placement of engineered fills that are to be used to support the foundation units, and

b)   as required, unless otherwise directed by the authority having jurisdiction,

i)   in the construction of all shallow foundation units, and

ii)   in excavating, dewatering and other related works.

4.2.2.4. Altered Subsurface Condition

1)   If, during construction, the soil, rock or groundwater is found not to be of the type or in the condition used in design and as indicated on the drawings, the design shall be reassessed by the designer.

2)   If, during construction, climatic or any other conditions change the properties of the soil, rock or groundwater, the design shall be reassessed by the designer.

4.2.3. Materials Used in Foundations

4.2.3.1. Wood

1)   Wood used in foundations or in support of soil or rock shall conform with the appropriate requirements of Subsection 4.3.1.

4.2.3.2. Preservation Treatment of Wood

1)   Wood exposed to soil, rock or air above the lowest anticipated groundwater table shall be treated with preservative in conformance with CAN/CSA-O80 Series, “Wood preservation,” and the requirements of the appropriate standard as follows:

a)   CAN/CSA-O80.1, “Specification of treated wood,”

b)   CAN/CSA-O80.2, “Processing and treatment,” or

c)   CAN/CSA-O80.3, “Preservative formulations.”

2)   Wood treated as required in Sentence (1) shall be cared for as provided in Clause 4 of CAN/CSA-O80.0, “General requirements for wood preservation.”

4.2.3.3. Plain and Reinforced Masonry

1)   Plain or reinforced masonry used in foundations or in support of soil or rock shall conform with the requirements of Subsection 4.3.2.

4.2.3.4. Prevention of Deterioration of Masonry

1)   Where plain or reinforced masonry in foundations or in structures supporting soil or rock may be subject to conditions conducive to deterioration, protection shall be provided to prevent such deterioration.

4.2.3.5. Concrete

1)   Plain, reinforced or pre-stressed concrete used in foundations or in support of soil or rock shall conform with the requirements of Subsection 4.3.3.

4.2.3.6. Protection Against Chemical Attack

1)   Where concrete in foundations may be subject to chemical attack, it shall be treated in conformance with the requirements in CSA A23.1, “Concrete materials and methods of concrete construction.”

4.2.3.7. Steel

1)   Steel used in foundations or in support of soil or rock shall conform with the appropriate requirements of Subsection 4.3.3. or 4.3.4., unless otherwise specified in this Section.

4.2.3.8. Steel Piles

1)   Where steel piles are used in deep foundations and act as permanent load-carrying members, the steel shall conform with one of the following standards:

a)   ASTM A252, “Standard Specification for Welded and Seamless Steel Pipe Piles,”

b)   ASTM A283/A283M, “Standard Specification for Low and Intermediate Tensile Strength Carbon Steel Plates,”

c)   ASTM A1008/A1008M, “Standard Specification for Steel, Sheet, Cold-Rolled, Carbon, Structural, High-Strength Low-Alloy, High-Strength Low-Alloy with Improved Formability, Solution Hardened, and Bake Hardenable,”

d)   ASTM A1011/A1011M, “Standard Specification for Steel, Sheet and Strip, Hot-Rolled, Carbon, Structural, High-Strength Low-Alloy, High-Strength Low-Alloy with Improved Formability, and Ultra-High Strength,” or

e)   CSA G40.21, “Structural quality steel.”

4.2.3.9. High Strength Steel Tendons

1)   Where high strength steel is used for tendons in anchor systems used for the permanent support of a foundation or in the erection of temporary support of soil or rock adjacent to an excavation, it shall conform with the requirements of CSA A23.1, “Concrete materials and methods of concrete construction.”

4.2.3.10. Corrosion of Steel

1)   Where conditions are corrosive to steel, adequate protection of exposed steel shall be provided. (See Article 1.2.1.1. of Division A for use of other materials.)

4.2.4. Design Requirements

4.2.4.1. Design Basis

1)   The design of foundations, excavations and soil- and rock-retaining structures shall be based on a subsurface investigation carried out in conformance with the requirements of this Section, and on any of the following, as appropriate:

a)   application of generally accepted geotechnical and civil engineering principles by a professional engineer especially qualified in this field of work, as provided in this Section and other Sections of Part 4,

b)   established local practice, where such practice includes successful experience both with soils and rocks of similar type and condition and with a foundation or excavation of similar type, construction method, size and depth, or

c)   in situ testing of foundation units, such as the load testing of piles, anchors or footings, carried out by a person competent in this field of work.

(See Note A-4.2.4.1.(1).)

2)   The foundations of a building shall be capable of resisting all the loads stipulated in Section 4.1., in accordance with limit states design in Subsection 4.1.3.

3)   For the purpose of the application of the load combinations given in Table 4.1.3.2.-A, the geotechnical components of loads and the factored geotechnical resistances at ULS shall be determined by a suitably qualified and experienced professional engineer. (See Note A-4.2.4.1.(3).)

4)   Geotechnical components of service loads and geotechnical reactions for SLS shall be determined by a suitably qualified and experienced professional engineer.

5)   The foundation of a building shall be designed to satisfy SLS requirements within the limits that the building is designed to accommodate, including total settlement and differential settlement, heave, lateral movement, tilt or rotation. (See Note A-4.2.4.1.(5).)

6)   Communication, interaction and coordination between the designer and the professional engineer responsible for the geotechnical aspects of the project shall take place to a degree commensurate with the complexity and requirements of the project.

4.2.4.2. Subsurface Investigation

1)   A subsurface investigation shall be carried out to the depth and extent to which the building or excavation will significantly change the stress in the soil or rock, or to such a depth and extent as to provide all the necessary information for the design and construction of the excavation or the foundations.

4.2.4.3. Identification

1)   The identification and classification of soil, rock and groundwater and descriptions of their engineering and physical properties shall be in accordance with a widely accepted system.

4.2.4.4. Depth of Foundations

1)   Except as permitted in Sentence (2), the bearing surface of a foundation shall be below the level of potential damage, including damage resulting from frost action, and the foundation shall be designed to prevent damage resulting from adfreezing and frost jacking. (See Note A-4.2.4.4.(1).)

2)   The bearing surface of a foundation need not be below the level of potential damage from frost where the foundation

a)   is designed against frost action, or

b)   overlies material not susceptible to frost action.

4.2.4.5. Sloping Ground

1)   Where a foundation is to rest on, in or near sloping ground, this particular condition shall be provided for in the design.

4.2.4.6. Eccentric and Inclined Loads

1)   Where there is eccentricity or inclination of loading in foundation units, this effect shall be fully investigated and provided for in the design.

4.2.4.7. Dynamic Loading

1)   Where dynamic loading conditions apply, the effects shall be assessed by a special investigation of these conditions and provided for in the design.

4.2.4.8. Hydrostatic Uplift

1)   Where a foundation or any part of a building is subject to hydrostatic uplift, the effects shall be provided for in the design.

4.2.4.9. Groundwater Level Change

1)   Where proposed construction will result in a temporary or permanent change in the groundwater level, the effects of this change on adjacent buildings shall be fully investigated and provided for in the design.

4.2.4.10. Permafrost

1)   Where conditions of permafrost are encountered or proven to exist, the design of the foundation shall be based upon analysis of these conditions by a person especially qualified in that field of work.

4.2.4.11. Swelling and Shrinking Soils

1)   Where swelling or shrinking soils, in which movements resulting from moisture content changes may be sufficient to cause damage to a structure, are encountered or known to exist, such a condition shall be fully investigated and provided for in the design.

4.2.4.12. Expanding and Deteriorating Rock

1)   Where rock that expands or deteriorates when subjected to unfavourable environmental conditions or to stress release is known to exist, this condition shall be fully investigated and provided for in the design.

4.2.4.13. Construction on Fill

1)   Buildings may be placed on fill if it can be shown by subsurface investigation that

a)   the fill is or can be made capable of safely supporting the building,

b)   detrimental movement of the building or of services leading to the building will not occur, and

c)   explosive gases can be controlled or do not exist.

4.2.4.14. Structural Design

1)   The structural design of the foundation of a building, the procedures and construction practices shall conform with the appropriate Sections of this Code unless otherwise specified in this Section.

4.2.5. Excavations

4.2.5.1. Design of Excavations

1)   The design of excavations and of supports for the sides of excavations shall conform with Subsection 4.2.4. and with this Subsection. (See Note A-4.2.5.1.(1).)

4.2.5.2. Excavation Construction

1)   Every excavation shall be undertaken in such a manner as to

a)   prevent movement that would cause damage to adjacent buildings at all phases of construction, and

b)   comply with the appropriate requirements of Part 8.

2)   Material shall not be placed nor shall equipment be operated or placed in or adjacent to an excavation in a manner that may endanger the integrity of the excavation or its supports.

4.2.5.3. Supported Excavations

1)   The sides of an excavation in soil or rock shall be supported by a retaining structure conforming with the requirements of Articles 4.2.5.1. and 4.2.5.2., except as permitted in Article 4.2.5.4.

4.2.5.4. Unsupported Excavations

1)   The sides of an excavation in soil or rock may be unsupported where a design is prepared in conformance with the requirements of Articles 4.2.5.1. and 4.2.5.2.

4.2.5.5. Control of Water around Excavations

1)   Surface water, all groundwater, perched groundwater and in particular artesian groundwater shall be kept under control at all phases of excavation and construction.

4.2.5.6. Loss of Ground

1)   At all phases of excavation and construction, loss of ground due to water or any other cause shall be prevented.

4.2.5.7. Protection and Maintenance at Excavations

1)   All sides of an excavation, supported and unsupported, shall be continuously maintained and protected from possible deterioration by construction activity or by the action of frost, rain and wind.

4.2.5.8. Backfilling

1)   Where an excavation is backfilled, the backfill shall be placed so as to

a)   provide lateral support to the soil adjacent to the excavation, and

b)   prevent detrimental movements.

2)   The material used as backfill or fill supporting a footing, foundation or a floor on grade shall be of a type that is not subject to detrimental volume change with changes in moisture content and temperature.

4.2.6. Shallow Foundations

4.2.6.1. Design of Shallow Foundations

1)   The design of shallow foundations shall be in conformance with Subsection 4.2.4. and the requirements of this Subsection. (See Note A-4.2.6.1.(1).)

4.2.6.2. Support of Shallow Foundations

1)   Where a shallow foundation is to be placed on soil or rock, the soil or rock shall be cleaned of loose and unsound material and shall be adequate to support the design load taking into account temperature, precipitation, construction activities and other factors that may lead to changes in the properties of soil or rock.

4.2.6.3. Incorrect Placement of Shallow Foundations

1)   Where a shallow foundation unit has not been placed or located as indicated on the drawings,

a)   the error shall be corrected, or

b)   the design of the foundation unit shall be recalculated for the altered conditions by the designer and action taken as required in Article 2.2.4.7. of Division C.

4.2.6.4. Damaged Shallow Foundations

1)   If a shallow foundation unit is damaged,

a)   it shall be repaired, or

b)   the design of the foundation unit shall be recalculated for the damaged condition by the designer and action taken as required in Article 2.2.4.7. of Division C.

4.2.7. Deep Foundations

4.2.7.1. General

1)   A deep foundation shall provide support for a building by transferring loads by end-bearing to a competent stratum at considerable depth below the structure, or by mobilizing resistance by adhesion or friction, or both, in the soil or rock in which it is placed. (See Note A-4.2.7.1.(1).)

4.2.7.2. Design of Deep Foundations

1)   Deep foundations shall be designed in conformance with Subsection 4.2.4. and this Subsection. (See Note A-4.2.7.2.(1).)

2)   Where deep foundation units are load tested, as required in Clause 4.2.4.1.(1)(c), the determination of the number and type of load test and the interpretation of the results shall be carried out by a professional engineer especially qualified in this field of work. (See Note A-4.2.7.2.(2).)

3)   The design of deep foundations shall be determined on the basis of geotechnical considerations taking into account

a)   the method of installation,

b)   the degree of inspection,

c)   the spacing of foundation units and group effects,

d)   other requirements in this Subsection, and

e)   the appropriate structural requirements in Section 4.1. and Subsections 4.3.1., 4.3.3. and 4.3.4.

4)   The portion of a deep foundation unit permanently in contact with soil or rock shall be structurally designed as a laterally supported compression member.

5)   The portion of a deep foundation unit that is not permanently in contact with soil or rock shall be structurally designed as a laterally unsupported compression member.

6)   The structural design of prefabricated deep foundation units shall allow for all stresses resulting from driving, handling and testing.

4.2.7.3. Tolerance in Alignment and Location

1)   Permissible deviations from the design alignment and the location of the top of deep foundation units shall be determined by design analysis and shall be indicated on the drawings.

4.2.7.4. Incorrect Alignment and Location

1)   Where a deep foundation unit has not been placed within the permissible deviations referred to in Article 4.2.7.3., the condition of the foundation shall be assessed by the designer, any necessary changes made and action taken as required in Article 2.2.4.7. of Division C.

4.2.7.5. Installation of Deep Foundations

1)   Deep foundation units shall be installed in such a manner as not to impair

a)   the strength of the deep foundation units and the properties of the soil or rock on or in which they are placed beyond the calculated or anticipated limits,

b)   the integrity of previously installed deep foundation units, or

c)   the integrity of neighbouring buildings.

4.2.7.6. Damaged Deep Foundation Units

1)   Where inspection shows that a deep foundation unit is damaged or not consistent with design or good engineering practice,

a)   such a unit shall be reassessed by the designer,

b)   any necessary changes shall be made, and

c)   action shall be taken as required in Article 2.2.4.7. of Division C.

4.2.8. Special Foundations

4.2.8.1. General

1)   Where special foundation systems are used, such systems shall conform to Subsection 4.2.4., Sentence 4.1.1.5.(2) and Article 1.2.1.1. of Division A.

4.2.8.2. Use of Existing Foundations

1)   Existing foundations may be used to support new or altered buildings provided they comply with all pertinent requirements of this Section.

Section  4.3.   Design Requirements for Structural Materials

4.3.1. Wood

4.3.1.1. Design Basis for Wood

1)   Buildings and their structural members made of wood shall conform to CSA O86, “Engineering design in wood.”

4.3.1.2. Glued-Laminated Members

1)   Glued-laminated members shall be fabricated in plants conforming to CSA O177, “Qualification Code for Manufacturers of Structural Glued-Laminated Timber.”

4.3.1.3. Termites

1)   In areas known to be infested by termites, the requirements in Articles 9.3.2.9., 9.12.1.1. and 9.15.5.1. shall apply.

4.3.2. Plain and Reinforced Masonry

4.3.2.1. Design Basis for Plain and Reinforced Masonry

1)   Buildings and their structural members made of plain and reinforced masonry shall conform to CSA S304, “Design of masonry structures.”

4.3.3. Plain, Reinforced and Pre-stressed Concrete

4.3.3.1. Design Basis for Plain, Reinforced and Pre-stressed Concrete

1)   Buildings and their structural members made of plain, reinforced and pre-stressed concrete shall conform to CSA A23.3, “Design of concrete structures.” (See Note A-4.3.3.1.(1).)

4.3.4. Steel

4.3.4.1. Design Basis for Structural Steel

1)   Buildings and their structural members made of structural steel shall conform to CSA S16, “Design of steel structures.” (See Note A-4.3.4.1.(1).)

4.3.4.2. Design Basis for Cold-Formed Steel

1)   Buildings and their structural members made of cold-formed steel shall conform to CSA S136, “North American Specification for the Design of Cold-Formed Steel Structural Members (using the Appendix B provisions applicable to Canada).” (See Note A-4.3.4.2.(1).)

4.3.4.3. Steel Building Systems

1)   Steel building systems shall be manufactured by companies certified in accordance with the requirements of CSA A660, “Certification of manufacturers of steel building systems.”

4.3.5. Aluminum

4.3.5.1. Design Basis for Aluminum

1)   Buildings and their structural members made of aluminum shall conform to CSA S157/S157.1, “Strength design in aluminum/Commentary on CSA S157-17, Strength design in aluminum,” using the loads stipulated in Section 4.1., in accordance with limit states design in Subsection 4.1.3.

4.3.6. Glass

4.3.6.1. Design Basis for Glass

1)   Glass used in buildings shall be designed in conformance with

a)   CAN/CGSB-12.20-M, “Structural Design of Glass for Buildings,” using an adjustment factor on the wind load, W, of not less than 0.75, or

b)   ASTM E1300, “Standard Practice for Determining Load Resistance of Glass in Buildings,” using an adjustment factor on the wind load, W, of not less than 1.0.

(See Note A-4.3.6.1.(1).)

Section  4.4.   Design Requirements for Special Structures

4.4.1. Air-, Cable- and Frame-Supported Membrane Structures

4.4.1.1. Design Basis for Air-, Cable- and Frame-Supported Membrane Structures

1)   The structural design of air-, cable- and frame-supported membrane structures shall conform to CSA S367, “Air-, cable-, and frame-supported membrane structures,” using the loads stipulated in Section 4.1., in accordance with limit states design in Subsection 4.1.3.

4.4.2. Parking Structures

4.4.2.1. Design Basis for Storage Garages and Repair Garages

1)   Storage garages and repair garages, including associated ramps and pedestrian areas, shall be designed in conformance with the performance requirements of CSA S413, “Parking structures.” (See Note A-4.4.2.1.(1).)

4.4.3. Storage Racks

4.4.3.1. Design Basis for Storage Racks

1)   Storage racks, including anchorage of racks, shall be designed for loads in accordance with this Part. (See Note A-4.1.8.18.(13) and 4.4.3.1.(1).)

Section  4.5.   Objectives and Functional Statements

4.5.1. Objectives and Functional Statements

4.5.1.1. Attributions to Acceptable Solutions

1)   For the purpose of compliance with this Code as required in Clause 1.2.1.1.(1)(b) of Division A, the objectives and functional statements attributed to the acceptable solutions in this Part shall be the objectives and functional statements listed in Table 4.5.1.1. (See Note A-1.1.2.1.(1).)

Table 4.5.1.1.

Objectives and Functional Statements Attributed to the Acceptable Solutions in Part 4

Forming Part of Sentence 4.5.1.1.(1)

| Provision | Functional Statements and Objectives(1) |
| --- | --- |
| 4.1.1.3. Design Requirements |  |
| (1) | [F20-OS2.1] |
| (2) | [F22-OP2.4] |
|  | [F22-OH4] |
| (3) | [F20-OS2.1] Applies to structural members where temporary overloading during construction may result in impairment of that or any other member. |
| (4) | [F20,F80,F82-OS2.1] |
| (5) | [F20-OP2.1] [F22-OP2.4] |
|  | [F20-OS2.3,OS2.4] |
| 4.1.1.5. Design Basis |  |
| (2) | [F20-OS2.1] [F22-OS2.4,OS2.5] |
|  | [F20-OP2.1] [F22-OP2.4,OP2.5] |
|  | [F22-OH4] |
| 4.1.2.1. Loads and Effects |  |
| (1) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
|  | [F22-OH4] |
| (2) | [F20-OS2.1] |
| (3) | [F20-OS2.1] |
| 4.1.2.2. Loads Not Listed |  |
| (1) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
|  | [F22-OH4] |
| 4.1.3.2. Strength and Stability |  |
| (1) | [F20-OP2.1] [F22-OP2.4] |
|  | [F20-OS2.1] |
| (2) | [F20-OS2.1] [F22-OS2.4,OS2.5] Applies to the stabilizing resistance of the dead load. |
|  | [F20-OP2.1] [F22-OP2.4,OP2.5] |
| (3) | [F20-OS2.1] [F22-OS2.4,OS2.5] Applies to the stabilizing resistance of the dead load. |
|  | [F20-OP2.1] [F22-OP2.4,OP2.5] |
| (4) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| (5) | [F20-OS2.1] [F22-OS2.4,OS2.5] |
|  | [F20-OP2.1] [F22-OP2.4,OP2.5] |
| (8) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| (9) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| (11) | [F20-OS2.1] [F22-OS2.4,OS2.5] |
| (12) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| 4.1.3.3. Fatigue |  |
| (1) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| (2) | [F20-OS2.1] |
|  | [F20-OP2.1,OP2.4] [F22-OP2.4] |
|  | [F22-OH4] |
| 4.1.3.4. Serviceability |  |
| (1) | [F22-OP2.4] |
|  | [F22-OH4] |
| (2) | [F22-OP2.4] |
|  | [F22-OH4] |
| (3) | [F22-OP2.4] |
|  | [F22-OH4] |
| (4) | [F22-OP2.4] |
|  | [F22-OH4] |
| (5) | (b),(c),(d) [F22-OP2.4] |
|  | [F22-OP2.4] |
|  | [F22-OH4] |
| (6) | [F21-OS2.5] |
|  | [F21-OP2.4,OP2.5] |
|  | [F22-OH4] |
| 4.1.3.5. Deflection |  |
| (1) | (b),(c),(d) [F22-OP2.4] |
|  | [F22-OP2.4] |
|  | [F22-OH4] |
| (2) | [F22-OS2.3,OS2.4] |
|  | [F22-OP2.4] |
| (3) | [F22-OP2.4] |
| (5) | [F22-OS2.3,OS2.4] |
|  | [F22-OP2.3,OP2.4] |
| 4.1.3.6. Vibration |  |
| (1) | [F22-OP2.4] |
|  | [F22-OH4] |
| (2) | [F20-OS2.1] |
|  | [F20-OP2.1,OP2.4] [F22-OP2.4] |
|  | [F22-OH4] |
| (3) | [F20-OS2.1] |
|  | [F20-OP2.1,OP2.4] [F22-OP2.4] |
|  | [F22-OH4] |
| 4.1.4.1. Dead Loads |  |
| (2) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| (3) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| (5) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| (6) | [F20-OS2.1] [F22-OS2.4,OS2.5] |
| 4.1.5.1. Loads Due to Use of Floors and Roofs |  |
| (1) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
|  | [F22-OH4] |
| 4.1.5.2. Uses Not Stipulated |  |
| (1) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
|  | [F22-OH4] |
| 4.1.5.3. Full and Partial Loading |  |
| (1) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
|  | [F22-OH4] |
| 4.1.5.4. Loads for Occupancy Served |  |
| (1) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
|  | [F22-OH4] |
| 4.1.5.5. Loads on Exterior Areas |  |
| (1) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
|  | [F22-OH4] |
| (2) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
|  | [F22-OH4] |
| (3) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
|  | [F22-OH4] |
| (4) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
|  | [F22-OH4] |
| (5) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
|  | [F22-OH4] |
| 4.1.5.7. More Than One Occupancy |  |
| (1) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
|  | [F22-OH4] |
| 4.1.5.8. Variation with Tributary Area |  |
| (1) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
|  | [F22-OH4] |
| (2) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
|  | [F22-OH4] |
| 4.1.5.9. Concentrated Loads |  |
| (1) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| 4.1.5.10. Sway Forces in Assembly Occupancies |  |
| (1) | [F20-OS2.1] |
|  | [F20-OP2.1,OP2.4] |
| 4.1.5.11. Crane-Supporting Structures and Impact of Machinery and Equipment |  |
| (1) | [F20-OS2.1] |
|  | [F20-OP2.1,OP2.4] [F22-OP2.4] |
| (3) | [F20-OS2.1] |
|  | [F20-OP2.1,OP2.4] |
| (4) | [F20-OS2.1] |
|  | [F20-OP2.1,OP2.4] |
| (5) | [F20-OS2.1] |
|  | [F20-OP2.1,OP2.4] |
| 4.1.5.12. Bleachers |  |
| (1) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| (3) | [F20-OS2.4] |
| 4.1.5.13. Helicopter Landing Areas |  |
| (1) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| 4.1.5.14. Loads on Guards and Handrails |  |
| (1) | [F20-OS2.1] |
| (2) | [F20-OS2.1] |
| (3) | [F20-OS2.1,OS2.4] |
| (4) | [F22-OS2.4] |
| (6) | [F20-OS2.1] |
| (7) | [F20-OS2.1] |
| 4.1.5.15. Loads on Vehicle Guardrails |  |
| (1) | [F20-OS2.1] |
| 4.1.5.16. Loads on Walls Acting As Guards |  |
| (1) | [F20-OS2.1] |
| 4.1.5.17. Firewalls |  |
| (1) | [F20-OS1.2] |
|  | [F20-OP1.2] |
|  | [F20-OP3.1] |
| (2) | [F04-OS1.2] |
|  | [F04-OP1.2] |
|  | [F04-OP3.1] |
| 4.1.6.2. Specified Snow Load |  |
| (1) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| (2) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| (3) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| (5) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| (6) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| (7) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| (8) | [F20-OS2.1] Applies to portion of Code text: “The accumulation factor, Ca, shall be 1.0, …” |
|  | [F20-OP2.1] [F22-OP2.4] Applies to portion of Code text: “The accumulation factor, Ca, shall be 1.0, …” |
|  | (a) to (f) [F20-OS2.1] Applies to roof shapes and configurations that call for a higher accumulation factor. |
|  | (a) to (f) [F20-OP2.1] [F22-OP2.4] Applies to roof shapes and configurations that call for a higher accumulation factor. |
| (9) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| 4.1.6.3. Full and Partial Loading |  |
| (1) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| (2) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| 4.1.6.4. Specified Rain Load |  |
| (1) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| (2) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| (4) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| 4.1.6.5. Multi-level Roofs |  |
| (1) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| (2) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| (3) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| (4) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| (5) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| 4.1.6.6. Horizontal Gap between a Roof and a Higher Roof |  |
| (1) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| 4.1.6.7. Areas Adjacent to Roof Projections |  |
| (1) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| 4.1.6.8. Snow Drift at Corners |  |
| (1) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| (2) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| 4.1.6.9. Gable Roofs |  |
| (1) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| (2) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| (4) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| 4.1.6.10. Arch Roofs, Curved Roofs and Domes |  |
| (1) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| (2) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| (3) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| (4) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| (5) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| (6) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| (7) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| (9) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| 4.1.6.11. Snow Loads Due to Sliding |  |
| (1) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| (3) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| 4.1.6.12. Valleys in Curved or Sloped Roofs |  |
| (1) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| (2) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| (3) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| 4.1.6.13. Specific Weight of Snow |  |
| (1) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| 4.1.6.14. Snow Removal |  |
| (1) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| 4.1.6.15. Ice Loading of Structures |  |
| (1) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| 4.1.6.16. Roofs with Solar Panels |  |
| (1) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| (3) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| (4) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| (5) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| (6) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| 4.1.7.1. Specified Wind Load |  |
| (2) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
|  | [F22-OH4] |
| (3) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
|  | [F22-OH4] |
| (4) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
|  | [F22-OH4] |
| (5) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| (6) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
|  | [F22-OH4] |
| 4.1.7.2. Classification of Buildings |  |
| (1) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
|  | [F22-OH4] |
| (2) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
|  | [F22-OH4] |
| (3) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
|  | [F22-OH4] |
| 4.1.7.3. Static Procedure |  |
| (1) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
|  | [F22-OH4] |
| (2) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
|  | [F22-OH4] |
| (3) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
|  | [F22-OH4] |
| (4) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
|  | [F22-OH4] |
| (5) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
|  | [F22-OH4] |
| (6) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
|  | [F22-OH4] |
| (7) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
|  | [F22-OH4] |
| (8) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
|  | [F22-OH4] |
| (10) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
|  | [F22-OH4] |
| 4.1.7.4. Topographic Factor |  |
| (1) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
|  | [F22-OH4] |
| (2) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
|  | [F22-OH4] |
| 4.1.7.5. External Pressure Coefficients |  |
| (2) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
|  | [F22-OH4] |
| (3) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
|  | [F22-OH4] |
| (4) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
|  | [F22-OH4] |
| (5) | [F20-OS2.1] |
| (6) | [F20-OS2.1] |
| (7) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| (8) | [F20-OS2.1] |
| (9) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| 4.1.7.6. External Pressure Coefficients for Low Buildings |  |
| (2) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
|  | [F22-OH4] |
| (3) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
|  | [F22-OH4] |
| (4) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
|  | [F22-OH4] |
| (5) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
|  | [F22-OH4] |
| (6) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
|  | [F22-OH4] |
| (7) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
|  | [F22-OH4] |
| (8) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
|  | [F22-OH4] |
| (9) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
|  | [F22-OH4] |
| 4.1.7.7. Internal Pressure Coefficient |  |
| (1) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
|  | [F22-OH4] |
| (2) | [F20-OS2.1] |
| 4.1.7.8. Dynamic Procedure |  |
| (1) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
|  | [F22-OH4] |
| (2) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
|  | [F22-OH4] |
| (3) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
|  | [F22-OH4] |
| (4) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
|  | [F22-OH4] |
| 4.1.7.9. Full and Partial Wind Loading |  |
| (1) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
|  | [F22-OH4] |
| 4.1.7.10. Interior Walls and Partitions |  |
| (1) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| 4.1.7.11. Exterior Ornamentations, Equipment and Appendages |  |
| (1) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| 4.1.7.12. Attached Canopies on Low Buildings with a Height H ≤ 20 m |  |
| (2) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| 4.1.7.13. Roof-Mounted Solar Panels on Buildings of Any Height |  |
| (1) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| (2) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| (3) | [F20-OS2.1] |
| (4) | [F20-OS2.1] |
| (5) | [F20-OS2.1] |
| (6) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| (7) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| 4.1.7.14. Wind Tunnel Procedure |  |
| (1) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
|  | [F22-OH4] |
| (2) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
|  | [F22-OH4] |
| (3) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
|  | [F22-OH4] |
| 4.1.8.1. Analysis |  |
| (2) | (a) [F20-OS2.1] |
|  | (a) [F20-OP2.1,OP2.3] [F22-OP2.4] |
|  | (b) [F20-OS2.1] |
|  | (b) [F20-OP2.1] [F22-OP2.4] |
| (3) | [F20-OS2.1] |
|  | [F20-OP2.1,OP2.4] |
| (4) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| (5) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| (6) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| (7) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| (8) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| (9) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| (10) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| (11) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| (12) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| (13) | [F20-OS2.1] |
|  | [F20-OP2.3] [F22-OP2.3,OP2.4] |
| (14) | [F20-OS2.1] |
|  | [F20-OP2.3] [F22-OP2.3,OP2.4] |
| 4.1.8.3. General Requirements |  |
| (2) | [F20-OS2.1] |
|  | [F20-OP2.1,OP2.4] |
| (3) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| (4) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| (5) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| (6) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| (7) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| (8) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| 4.1.8.4. Site Properties |  |
| (1) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| (2) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| (4) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| (6) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| 4.1.8.5. Importance Factor and Seismic Category |  |
| (1) | [F20-OS2.1] |
|  | [F20-OP2.1,OP2.3] [F22-OP2.4] |
| (2) | [F20-OS2.1] |
|  | [F20-OP2.1,OP2.3] [F22-OP2.4] |
| 4.1.8.6. Structural Configuration |  |
| (3) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| 4.1.8.7. Methods of Analysis |  |
| (1) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| 4.1.8.8. Direction of Loading |  |
| (1) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| 4.1.8.9. SFRS Force Modification Factors and General Restrictions |  |
| (1) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| (2) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| (3) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| (4) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| 4.1.8.10. Additional System Restrictions |  |
| (1) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| (2) | (a) [F20-OP2.3] [F22-OP2.4] |
|  | (b) [F20-OP2.3] [F22-OP2.4] |
|  | (c) [F20-OP2.3] [F22-OP2.4] |
|  | (d) [F20-OP2.3] [F22-OP2.4] |
| (3) | (a) [F20-OP2.3] [F22-OP2.4] |
|  | (b) [F20-OP2.3] [F22-OP2.4] |
|  | (c) [F20-OP2.3] [F22-OP2.4] |
|  | (d) [F20-OP2.3] [F22-OP2.4] |
| (4) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| (5) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| (6) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| (8) | [F22-OS2.3,OS2.4] |
|  | [F22-OP2.3,OP2.4] |
| (9) | [F22-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| (10) | (a) [F20-OS2.1] |
|  | (a) [F20-OP2.1] [F22-OP2.4] |
|  | (b) [F20-OS2.1] |
|  | (b) [F20-OP2.1] [F22-OP2.4] |
| 4.1.8.11. Equivalent Static Force Procedure for Structures Satisfying the Conditions of Article 4.1.8.7. |  |
| (2) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| (3) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| (4) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| (5) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| (6) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| (7) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| (8) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| (9) | (a) [F20-OS2.1] |
|  | (a) [F20-OP2.1] [F22-OP2.4] |
|  | (b) [F20-OS2.1] |
|  | (b) [F20-OP2.1] [F22-OP2.4] |
| (10) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| (11) | (a) [F20-OP2.1] [F22-OP2.4] |
|  | (a) [F20-OS2.1] |
|  | (b) [F20-OS2.1] |
|  | (b) [F20-OP2.1] [F22-OP2.4] |
| (12) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| 4.1.8.12. Dynamic Analysis Procedure |  |
| (1) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| (2) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| (3) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| (4) | (a) [F20-OS2.1] |
|  | (a) [F20-OP2.1] [F22-OP2.4] |
| (5) | [F20-OS2.1] |
|  | [F20-OP2.1,OP2.3] [F22-OP2.4] |
| (7) | [F20-OS2.1] |
|  | [F20-OP2.1,OP2.3] [F22-OP2.4] |
| (8) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| (9) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| (10) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| (12) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| 4.1.8.13. Deflections and Drift Limits |  |
| (1) | [F22-OS2.3,OS2.4] |
|  | [F22-OP2.3,OP2.4] |
| (2) | [F22-OS2.3,OS2.4] |
|  | [F22-OP2.3,OP2.4] |
| (3) | [F22-OS2.3,OS2.4] |
|  | [F22-OP2.3,OP2.4] |
| 4.1.8.14. Structural Separation |  |
| (1) | [F22-OS2.3,OS2.4] |
|  | [F22-OP2.3,OP2.4] |
|  | [F22-OP4.3] |
| (2) | [F20-OS2.1,OS2.3,OS2.4] |
|  | [F20-OP2.1,OP2.3,OP2.4] |
|  | [F20-OP4.3] |
| (3) | [F20-OS2.1,OS2.3,OS2.4] |
|  | [F20-OP2.1,OP2.3,OP2.4] |
|  | [F20-OP4.3] |
| (4) | [F20-OS2.1,OS2.3,OS2.4] |
|  | [F20-OP2.1,OP2.3,OP2.4] |
|  | [F20-OP4.3] |
| 4.1.8.15. Design Provisions |  |
| (1) | [F20-OS2.1] |
|  | [F20-OP2.1,OP2.3,OP2.4] |
| (2) | [F20-OS2.1] |
|  | [F20-OP2.1,OP2.3,OP2.4] |
| (3) | [F20-OS2.1] |
|  | [F20-OP2.1,OP2.3,OP2.4] |
| (4) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| (5) | [F20-OS2.1] |
|  | [F20-OP2.1,OP2.4] |
| (6) | [F20-OS2.1,OS2.4] |
|  | [F20-OP2.1,OP2.4] |
| (7) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| 4.1.8.16. Foundation Provisions |  |
| (1) | [F22-OS2.3,OS2.4] |
|  | [F22-OP2.3,OP2.4] |
| (2) | [F20-OS2.1] |
|  | [F20-OP2.1] |
| (5) | [F20-OS2.2,OS2.4] |
|  | [F20-OP2.2,OP2.4] |
| (6) | (a) [F22-OS2.4] |
|  | (a) [F22-OP2.4] |
|  | (b) [F22-OS2.4] |
|  | (b) [F22-OP2.4] |
|  | (c) [F20-OS2.4] |
|  | (c) [F20-OP2.4] |
| (7) | [F20-OS2.1] |
|  | [F20-OP2.1,OP2.4] |
| (8) | (a) [F20-OS2.1] |
|  | (a) [F20-OP2.1] |
|  | (b) [F22-OS2.4] |
|  | (b) [F22-OP2.4] |
| (9) | [F20-OS2.4] |
|  | [F20-OP2.4] |
| (10) | [F20-OS2.2] [F22-OS2.4] |
|  | [F20-OP2.2] [F22-OP2.4] |
| 4.1.8.17. Site Stability |  |
| (1) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| 4.1.8.18. Elements of Structures, Non-structural Components and Equipment |  |
| (1) | [F20,F22-OS2.4] |
|  | [F20-OP2.3] [F22-OP2.3,OP2.4] |
| (4) | [F20,F22-OS2.4] |
|  | [F20,F22-OP2.3,OP2.4] |
| (5) | [F20,F22-OS2.1] |
|  | [F20,F22-OP2.1,OP2.4] |
| (6) | [F20,F22-OS2.4] |
|  | [F20,F22-OP2.3,OP2.4] |
| (7) | [F20,F22-OS2.4] Applies to portion of Code text: “Connections to the structure of elements and components listed in Table 4.1.8.18. shall be designed to support the component or element for gravity loads, shall conform to the requirements of Sentence (1) …” |
|  | [F20,F22-OP2.3,OP2.4] Applies to portion of Code text: “Connections to the structure of elements and components listed in Table 4.1.8.18. shall be designed to support the component or element for gravity loads, shall conform to the requirements of Sentence (1) …” |
|  | (a) [F20,F22-OS2.4] |
|  | (a) [F20,F22-OP2.3,OP2.4] |
|  | (b),(c) [F20,F22-OS2.4] |
|  | (b),(c) [F20,F22-OP2.3,OP2.4] |
|  | (d),(f) [F20,F22-OS2.4] |
|  | (d),(f) [F20,F22-OP2.3,OP2.4] |
|  | (g) [F20,F22-OS2.4] |
|  | (g) [F20,F22-OP2.3,OP2.4] |
| (9) | [F22-OS2.3,OS2.4] |
|  | [F22-OP2.3,OP2.4] |
| (10) | [F22-OS2.1,OS2.3,OS2.4] |
|  | [F22-OP2.1,OP2.3,OP2.4] |
| (11) | [F20-OS2.1] [F22-OS2.4] |
|  | [F20,F22-OP2.3,OP2.4] |
| (12) | [F20-OS2.1] [F22-OS2.3] |
|  | [F20-OP2.1] [F22-OP2.3] |
| (14) | [F22-OS2.4] |
| (16) | [F20,F22-OS2.4] |
|  | [F20-OP2.3] [F22-OP2.3,OP2.4] |
| 4.1.8.19. Seismic Isolation |  |
| (2) | [F20-OS2.1] [F22-OS2.4] |
|  | [F20-OP2.1] [F22-OP2.4] |
| (3) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| (4) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| 4.1.8.20. Seismic Isolation Design Provisions |  |
| (1) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| (2) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| (3) | [F20-OS2.1] [F22-OS2.4] |
|  | [F20-OP2.1] [F22-OP2.4] |
| (4) | [F20-OS2.1] [F22-OS2.4] |
|  | [F20-OP2.1] [F22-OP2.4] |
| (5) | [F20-OS2.1] [F22-OS2.4] |
|  | [F20-OP2.1] [F22-OP2.4] |
| (6) | [F20-OS2.1] [F22-OS2.4] |
|  | [F20-OP2.1] [F22-OP2.4] |
| (7) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| (9) | [F20-OS2.1] [F22-OS2.4] |
|  | [F20-OP2.1] [F22-OP2.4] |
| (10) | [F22-OS2.4] |
|  | [F22-OP2.3,OP2.4] |
| 4.1.8.21. Supplemental Energy Dissipation |  |
| (2) | [F20-OS2.1] [F22-OS2.4] |
|  | [F20-OP2.1] [F22-OP2.4] |
| (4) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| (5) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| 4.1.8.22. Supplemental Energy Dissipation Design Considerations |  |
| (1) | [F20-OS2.1] [F22-OS2.4] |
|  | [F20-OP2.1] [F22-OP2.4] |
| (3) | [F20-OS2.1] [F22-OS2.4] |
|  | [F20-OP2.1] [F22-OP2.4] |
| (4) | [F20-OS2.1] [F22-OS2.4] |
|  | [F20-OP2.1] [F22-OP2.4] |
| (5) | [F20-OS2.1] [F22-OS2.4] |
|  | [F20-OP2.1] [F22-OP2.4] |
| (6) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| (7) | [F20-OS2.1] [F22-OS2.4] |
|  | [F20-OP2.1] [F22-OP2.4] |
| (8) | [F20-OS2.1] [F22-OS2.4] |
|  | [F20-OP2.1] [F22-OP2.4] |
| 4.1.8.23. Additional Performance Requirements for Post-disaster Buildings, High Importance Category Buildings, and a Subset of Normal Importance Category Buildings |  |
| (2) | [F20-OS2.1] |
|  | [F22-OP2.3,OP2.4] |
| (3) | [F20-OS2.1] |
|  | [F22-OP2.3,OP2.4] |
| (4) | [F20-OS2.1] |
| 4.2.2.1. Subsurface Investigation |  |
| (1) | [F20-OS2.2,OS2.6] [F21-OS2.6] |
|  | [F20-OP2.2] [F21-OP2.6] |
|  | [F21-OP4.1,OP4.4] |
| 4.2.2.3. Field Review |  |
| (1) | [F20-OS2.2,OS2.6] [F21-OS2.6] |
|  | [F20-OP2.2] [F21-OP2.5] |
|  | [F21-OP4.1,OP4.4] |
| 4.2.2.4. Altered Subsurface Condition |  |
| (1) | [F20-OS2.2,OS2.6] [F21-OS2.6] |
|  | [F20-OP2.2] [F21-OP2.6] |
|  | [F21-OP4.1,OP4.4] |
| (2) | [F20-OS2.2,OS2.6] [F21-OS2.6] |
|  | [F20-OP2.2] [F21-OP2.6] |
|  | [F21-OP4.1,OP4.4] |
| 4.2.3.2. Preservation Treatment of Wood |  |
| (1) | [F80-OS2.3] |
|  | [F80-OP2.3] |
| (2) | [F82-OS2.3] |
|  | [F82-OP2.3] |
| 4.2.3.4. Prevention of Deterioration of Masonry |  |
| (1) | [F80-OS2.3] |
|  | [F80-OP2.3] |
| 4.2.3.6. Protection Against Chemical Attack |  |
| (1) | [F80-OS2.3] |
|  | [F80-OP2.3] |
| 4.2.3.8. Steel Piles |  |
| (1) | [F20-OS2.3] |
|  | [F20-OP2.3] |
| 4.2.3.9. High Strength Steel Tendons |  |
| (1) | [F20,F80-OS2.5,OS2.6] |
|  | [F20,F80-OP2.6,OP2.5] |
|  | [F20,F80-OP4.1,OP4.4] |
| 4.2.3.10. Corrosion of Steel |  |
| (1) | [F80-OS2.3] |
|  | [F80-OP2.3] |
|  | [F80-OP4.1] |
| 4.2.4.1. Design Basis |  |
| (1) | [F20-OS2.2,OS2.6] [F21-OS2.6] |
|  | [F20-OP2.2] [F21-OP2.5] |
|  | [F21-OP4.1,OP4.4] |
| (5) | [F21-OS2.5] |
|  | [F21-OP2.4,OP2.5] |
| 4.2.4.2. Subsurface Investigation |  |
| (1) | [F20-OS2.2,OS2.6] [F21-OS2.6] |
|  | [F20-OP2.2] [F21-OP2.6] |
|  | [F21-OP4.1,OP4.4] |
| 4.2.4.3. Identification |  |
| (1) | [F20-OS2.2,OS2.6] [F21-OS2.6] |
|  | [F20-OP2.2] [F21-OP2.6] |
|  | [F21-OP4.1,OP4.4] |
| 4.2.4.4. Depth of Foundations |  |
| (1) | [F21-OP2.4] Applies to portion of Code text: “… the bearing surface of a foundation shall be below the level of potential damage, including damage resulting from frost action …” |
|  | [F21-OP2.4] Applies to portion of Code text: “… the foundation shall be designed to prevent damage resulting from adfreezing and frost jacking.” |
| (2) | [F21-OP2.4] |
| 4.2.4.5. Sloping Ground |  |
| (1) | [F21-OS2.2] |
|  | [F21-OP2.2,OP2.6,OP2.4] |
| 4.2.4.6. Eccentric and Inclined Loads |  |
| (1) | [F20-OS2.1,OS2.2] |
|  | [F20-OP2.1,OP2.2,OP2.4] |
| 4.2.4.7. Dynamic Loading |  |
| (1) | [F20-OS2.2] |
|  | [F20-OP2.2,OP2.6,OP2.4] |
|  | [F20-OH4] |
| 4.2.4.8. Hydrostatic Uplift |  |
| (1) | [F22-OP2.1,OP2.4] |
| 4.2.4.9. Groundwater Level Change |  |
| (1) | [F21-OP4.1] |
| 4.2.4.10. Permafrost |  |
| (1) | [F20-OS2.2] [F21-OS2.5] |
|  | [F20-OP2.2,OP2.4] [F21-OP2.6,OP2.4] |
| 4.2.4.11. Swelling and Shrinking Soils |  |
| (1) | [F21-OP2.6,OP2.4] |
| 4.2.4.12. Expanding and Deteriorating Rock |  |
| (1) | [F21-OP2.6,OP2.4] |
| 4.2.4.13. Construction on Fill |  |
| (1) | (a) [F20-OS2.2] [F21-OS2.5] |
|  | (b) [F20-OP2.2,OP2.4] [F21-OP2.6,OP2.4] |
|  | (c) [F01-OS1.1] |
| 4.2.5.2. Excavation Construction |  |
| (1) | [F21-OP4.1] |
| (2) | [F20-OS2.6] |
|  | [F20-OP2.3] |
|  | [F20,F21-OP4.1] |
| 4.2.5.3. Supported Excavations |  |
| (1) | [F20-OS2.6] |
|  | [F21-OP4.1] |
| 4.2.5.4. Unsupported Excavations |  |
| (1) | [F20-OS2.6] |
|  | [F21-OP4.1] |
| 4.2.5.5. Control of Water around Excavations |  |
| (1) | [F60-OS2.6] |
|  | [F60-OP4.1,OP4.4] |
| 4.2.5.6. Loss of Ground |  |
| (1) | [F21-OP4.1] |
| 4.2.5.7. Protection and Maintenance at Excavations |  |
| (1) | [F80-OS2.6] |
|  | [F80-OP4.1] |
| 4.2.5.8. Backfilling |  |
| (1) | (a) [F21-OS2.1] |
|  | (a) [F21-OP2.1,OP2.4] |
|  | [F21-OP4.1] |
| (2) | [F21-OP2.4] |
| 4.2.6.2. Support of Shallow Foundations |  |
| (1) | [F20-OS2.2] |
|  | [F20-OP2.2,OP2.4] [F21-OP2.4] |
| 4.2.6.3. Incorrect Placement of Shallow Foundations |  |
| (1) | [F20-OS2.2] |
|  | [F20-OP2.2,OP2.4] [F21-OP2.4] |
| 4.2.6.4. Damaged Shallow Foundations |  |
| (1) | [F20-OS2.1] |
|  | [F20-OP2.1,OP2.4] [F22-OP2.4] |
| 4.2.7.2. Design of Deep Foundations |  |
| (3) | [F20-OS2.1,OS2.2] [F21-OS2.5] |
|  | [F20-OP2.1,OP2.2] [F21,F22-OP2.4] |
| (5) | [F20-OS2.1] |
|  | [F20-OP2.1,OP2.4] [F22-OP2.4] |
| (6) | [F20-OP2.1,OP2.4] |
| 4.2.7.3. Tolerance in Alignment and Location |  |
| (1) | [F20-OS2.1] |
|  | [F20-OP2.1,OP2.4] [F22-OP2.4] |
| 4.2.7.4. Incorrect Alignment and Location |  |
| (1) | [F20-OS2.1] |
|  | [F20-OP2.1,OP2.4] [F22-OP2.4] |
| 4.2.7.5. Installation of Deep Foundations |  |
| (1) | [F81-OS2.1] [F21-OS2.2,OS2.6] |
|  | (c) [F21-OP4.1] |
|  | (a),(b) [F81-OP2.1,OP2.4] [F21-OP2.2,OP2.4] |
| 4.2.7.6. Damaged Deep Foundation Units |  |
| (1) | [F20-OS2.1] |
|  | [F20-OP2.1] [F22-OP2.4] |
| 4.2.8.2. Use of Existing Foundations |  |
| (1) | [F20-OS2.1,OS2.2] |
|  | [F20-OP2.1,OP2.2] [F22-OP2.4] |
| 4.3.1.1. Design Basis for Wood |  |
| (1) | [F22,F21,F80-OH4] |
|  | [F20-OS2.1] [F80-OS2.3] |
|  | [F20-OP2.1] [F21,F22-OP2.4] [F80-OP2.3,OP2.4] |
| 4.3.1.2. Glued-Laminated Members |  |
| (1) | [F20-OS2.1] |
|  | [F20-OP2.1] [F21,F22-OP2.4] |
|  | [F21,F22-OH4] |
| 4.3.2.1. Design Basis for Plain and Reinforced Masonry |  |
| (1) | [F21,F22,F80-OH4] |
|  | [F20-OS2.1] [F80-OS2.3] |
|  | [F20-OP2.1] [F22,F21-OP2.4] [F80-OP2.3,OP2.4] |
| 4.3.3.1. Design Basis for Plain, Reinforced and Pre-stressed Concrete |  |
| (1) | [F20-OS2.1] [F80,F81-OS2.3] |
|  | [F20-OP2.1] [F21,F22-OP2.4] [F80,F81-OP2.3,OP2.4] |
|  | [F21,F22,F80,F81-OH4] |
| 4.3.4.1. Design Basis for Structural Steel |  |
| (1) | [F20-OS2.1] [F80-OS2.3] |
|  | [F20-OP2.1] [F20,F22-OP2.4] [F80-OP2.3,OP2.4] |
|  | [F22,F80-OH4] |
| 4.3.4.2. Design Basis for Cold-Formed Steel |  |
| (1) | [F20-OS2.1] [F80-OS2.3] |
|  | [F20-OP2.1] [F20,F22-OP2.4] [F80-OP2.3,OP2.4] |
|  | [F22,F80-OH4] |
| 4.3.5.1. Design Basis for Aluminum |  |
| (1) | [F20-OS2.1] [F80-OS2.3] |
|  | [F20-OP2.1] [F20,F22-OP2.4] [F80-OP2.3,OP2.4] |
|  | [F22,F80-OH4] |
| 4.3.6.1. Design Basis for Glass |  |
| (1) | [F20-OS2.1] |
|  | [F20-OP2.1] |
| 4.4.1.1. Design Basis for Air-, Cable- and Frame-Supported Membrane Structures |  |
| (1) | [F20-OS2.1] [F80-OS2.3] |
|  | [F20-OP2.1] [F22-OP2.4] [F80-OP2.3] |
|  | [F22-OH4] |
| 4.4.2.1. Design Basis for Storage Garages and Repair Garages |  |
| (1) | [F21,F61,F80-OS2.3] |
|  | [F21,F61,F80-OP2.3,OP2.4] |
|  | [F21,F61,F80-OH4] |

Notes to Table 4.5.1.1.:

(1) See Parts 2 and 3 of Division A.

Notes to Part 4

Structural Design

A-4.1.1.3.(1)   Structural Integrity. The requirements of Part 4, including the CSA design standards, generally provide a satisfactory level of structural integrity. Additional considerations may, however, be required for building systems made of components of different materials, whose interconnection is not covered by existing CSA design standards, buildings outside the scope of existing CSA design standards, and buildings exposed to severe accidental loads such as vehicle impact or explosion. Further guidance can be found in the Commentary entitled Structural Integrity in the “Structural Commentaries (User's Guide – NBC 2020: Part 4 of Division B).”

A-4.1.1.3.(2)   Serviceability. Information on serviceability can be found in the Commentary entitled Deflection and Vibration Criteria for Serviceability and Fatigue Limit States in the “Structural Commentaries (User's Guide – NBC 2020: Part 4 of Division B).”

A-4.1.1.5.(2)   Structural Equivalents. Sentence 4.1.1.5.(2) provides for the use of design methods not specified in Part 4, including full-scale testing and model analogues. This provision is usually used to permit the acceptance of new and innovative structures or to permit the acceptance of model tests such as those used to determine structural behaviour, or snow or wind loads. Sentence 4.1.1.5.(2) specifically requires that the level of safety and performance be at least equivalent to that provided by design to Part 4 and requires that loads and designs conform to Section 4.1.

Sentence 4.1.1.5.(2) and the provision for alternative solutions stated in Clause 1.2.1.1.(1)(b) of Division A are not intended to allow structural design using design standards other than those listed in Part 4. The acceptance of structures that have been designed to other design standards would require the designer to prove to the appropriate authority that the structure provides the level of safety and performance required by Clause 1.2.1.1.(1)(b) of Division A. The equivalence of safety and performance can only be established by analyzing the structure for the loads and load factors set out in Section 4.1. and by demonstrating that the structure at least meets the requirements of the design standards listed in Sections 4.3. and 4.4.

A-4.1.2.1.   Loads and Effects. Information on the definitions can be found in the Commentary entitled Limit States Design in the “Structural Commentaries (User's Guide – NBC 2020: Part 4 of Division B).”

A-4.1.2.1.(1)   Temperature Changes. Information on effects due to temperature changes can be found in the Commentary entitled Effects of Deformations in Building Components in the “Structural Commentaries (User's Guide – NBC 2020: Part 4 of Division B).”

A-4.1.2.1.(3)   Major Occupancies. In a building containing more than one major occupancy and classified in more than one Importance Category, the classification of each independent structural system shall be the same as for any part of the building that is dependent on that structural system and for the highest usage group according to Table 4.1.2.1.

A-Table 4.1.2.1.   Importance Categories for Buildings.

Low Importance Category

A minor storage building is an example of a Low Importance Category building.

Low-human-occupancy farm buildings with an occupant load of 1 person or less per 40 m2 of floor area are also examples of Low Importance Category buildings.

Normal Importance Category

Most buildings will fall into the Normal Importance Category.

The following types of buildings may be classified in the Normal Importance Category: buildings that are equipped with secondary containment of dangerous goods, including, but not limited to, double-walled tanks, dikes of sufficient size to contain a spill, and other means to contain a spill or a blast within the property boundary of the facility and prevent the release of harmful quantities of contaminants to the air, soil, groundwater, surface water or atmosphere, as the case may be.

High Importance Category

The following buildings may contain sufficient quantities of dangerous goods to be classified in the High Importance Category:

•   petrochemical facilities,

•   fuel storage facilities (other than those required for post-disaster use), and

•   manufacturing or storage facilities containing dangerous goods.

Information on community centres can be found in the Commentary entitled Limit States Design in the “Structural Commentaries (User's Guide – NBC 2020: Part 4 of Division B).”

Post-disaster Importance Category

Before classifying a building as a post-disaster building, Code users should consider the intent of the classification and look beyond the name of the building. For example, a building that is named “ABC Treatment” but is used for emergency care should be considered as a hospital and, as such, classified as a post-disaster building. Conversely, a building named “XYZ Hospital” that is only used for walk-in medical services could be classified as a Normal Importance Category building.

A-4.1.2.2.(1)   Loads Not Listed. The intent of Sentence 4.1.2.2.(1) is to draw attention to the fact that there are loads, forces and effects that need to be considered in addition to those specified in the Code. These loads, forces and effects will vary in need, application, and magnitude for each use and location. Some may result from environmental considerations (e.g., ice accretion, wave and ice action, water flow) while others will result from the use and occupancy of the facility (e.g., dangerous goods storage, manufacturing and mining operations). The reasonable determination of the probability, type and magnitude of project-specific loads must be assessed by a knowledgeable project team that includes the building owner/operator and experienced design professionals, and incorporated into the design where deemed necessary to maintain the safety and integrity of the facility.

In recent years, security issues have prompted the consideration of loads and effects due to improvised explosive devices and other methods of sabotage. Consideration of these loads is driven by operational and public safety requirements, and their incorporation in the design is not considered a mandatory provision of the Code.

A-4.1.3.   Limit States Design. Information on limit states design can be found in the Commentary entitled Limit States Design in the “Structural Commentaries (User's Guide – NBC 2020: Part 4 of Division B).”

A-4.1.3.2.(2)   Load Combinations.

Load Combination Equations

The load combinations in Tables 4.1.3.2.-A and 4.1.3.2.-B apply to most situations for loadbearing building structures. Guidance on special situations such as load combinations for fire resistance and building envelopes is given in the Commentary entitled Limit States Design in the “Structural Commentaries (User's Guide – NBC 2020: Part 4 of Division B).”

Load Cases and Crane Load Effects

The load combinations in Table 4.1.3.2.-A are to be evaluated for structures with crane load effects for the scenario where the crane loads are zero, and for structures without crane loads. The load combinations in Table 4.1.3.2.-B are to be evaluated for structures with crane loads for the scenario where the crane load effects are other than zero.

Crane Loads

Crane-supporting structures that have cranes in multiple parallel bays should be designed for the maximum vertical crane load with the cranes positioned for the most critical effect in conjunction with a lateral load with each crane in turn positioned for the most critical effect. For load combinations that include crane loads, additional guidance can be found in CISC/ICCA 2018, “Crane-Supporting Steel Structures: Design Guide (Third Edition).”

A-4.1.3.2.(4)   Effects of Lateral Earth Pressure, H, Pre-stress, P, and Imposed Deformation, T, in Design Calculations.

Effects of Lateral Earth Pressure, H, in Design Calculations

For common building structures below ground level, such as walls, columns and frames, 1.5H is added to load combinations 2 to 4. For cantilever retaining wall structures, see the Commentary entitled Limit States Design in the “Structural Commentaries (User's Guide – NBC 2020: Part 4 of Division B).”

Effects of Pre-stress, P, and Imposed Deformation, T, in Design Calculations

For structures and building envelopes designed in accordance with the requirements specified in the standards listed in Section 4.3., with the exception of Clauses 8 and 18 of CSA A23.3, “Design of concrete structures,” P and T need not be included in the load combinations of Table 4.1.3.2.-A. For structures not within the scope of the standards listed in Section 4.3., including building envelopes, P and T must be taken into account in the design calculations. For recommended load combinations including T, see the Commentary entitled Limit States Design in the “Structural Commentaries (User's Guide – NBC 2020: Part 4 of Division B).”

A-4.1.3.2.(5)   Overturning, Uplift or Sliding. Information on overturning, uplift and sliding can be found in the Commentary entitled Limit States Design in the “Structural Commentaries (User's Guide – NBC 2020: Part 4 of Division B).”

A-4.1.3.3.(1)   Failure due to Fatigue. Failure due to fatigue of building structures referred to in Section 4.3. and designed for serviceability in accordance with Article 4.1.3.6. is, in general, unlikely except for girders supporting heavily used cranes, on which Article 4.1.5.11. provides guidance.

A-4.1.3.3.(2)   Vibration Effects. Guidance on vibration effects can be found in the Commentary entitled Deflection and Vibration Criteria for Serviceability and Fatigue Limit States in the “Structural Commentaries (User's Guide – NBC 2020: Part 4 of Division B).”

A-4.1.3.4.(1)   Loads and Load Combinations for Serviceability. The loads and load combinations for serviceability depend on the serviceability limit states and on the properties of the structural materials. Information on loads and load combinations for the serviceability limit states, other than those controlled by deflection, can be found in the Commentary entitled Deflection and Vibration Criteria for Serviceability and Fatigue Limit States in the “Structural Commentaries (User's Guide – NBC 2020: Part 4 of Division B).”

A-Table 4.1.3.4.   Acceleration due to Vibrations. Information on the determination of acceleration due to vibrations resulting from loads L and W can be found in the Commentary entitled Wind Load and Effects in the “Structural Commentaries (User's Guide – NBC 2020: Part 4 of Division B).”

A-4.1.3.5.(1)   Deflections. Serviceability criteria for deflections that cause damage to non-structural building components can be found in the standards listed in Section 4.3. Information on deflections can be found in the Commentary entitled Deflection and Vibration Criteria for Serviceability and Fatigue Limit States in the “Structural Commentaries (User's Guide – NBC 2020: Part 4 of Division B).” Information on loads and load combinations for calculating deflection can be found in the Commentary entitled Limit States Design in the “Structural Commentaries (User's Guide – NBC 2020: Part 4 of Division B).”

A-4.1.3.5.(3)   Lateral Deflection of Buildings. The limitation of 1/500 drift per storey may be exceeded if it can be established that the drift as calculated will not result in damage to non-structural elements. Information on lateral deflection can be found in the Commentary entitled Wind Load and Effects in the “Structural Commentaries (User's Guide – NBC 2020: Part 4 of Division B).”

A-4.1.3.6.(1)   Floor Vibration. Information on floor vibration can be found in the Commentary entitled Deflection and Vibration Criteria for Serviceability and Fatigue Limit States in the “Structural Commentaries (User's Guide – NBC 2020: Part 4 of Division B).” Information on loads and load combinations for the calculation of vibration can be found in the Commentary entitled Limit States Design in the “Structural Commentaries (User's Guide – NBC 2020: Part 4 of Division B).”

A-4.1.3.6.(2)   Floor Vibrations Caused by Resonance with Operating Machinery or Equipment. Guidance on floor vibration effects caused by operating machinery and equipment can be found in the Commentary entitled Deflection and Vibration Criteria for Serviceability and Fatigue Limit States in the “Structural Commentaries (User's Guide – NBC 2020: Part 4 of Division B).”

A-4.1.3.6.(3)   Dynamic Analyses of Floor Vibrations. Information on a dynamic analysis of floor vibrations from rhythmic activities can be found in the Commentary entitled Deflection and Vibration Criteria for Serviceability and Fatigue Limit States in the “Structural Commentaries (User's Guide – NBC 2020: Part 4 of Division B).”

A-4.1.3.6.(4)   Lateral Vibration Under Wind Load. Information on lateral vibrations and accelerations under dynamic wind loads can be found in the Commentary entitled Wind Load and Effects in the “Structural Commentaries (User's Guide – NBC 2020: Part 4 of Division B).”

A-4.1.4.1.(2)   Permanent Partitions Fixed to the Structure. Partitions in residential buildings, including condominiums, apartments and hotels, are typically permanent and fixed to the structure. In such cases, the weight of partitions referred to in Clause 4.1.4.1.(1)(c) is the actual weight of the partitions that are shown on the drawings.

A-4.1.4.1.(3)   Partitions Not Shown on the Drawings.  The potential locations of partitions in work areas, such as offices, are not typically shown on the drawings. For such areas, a partition weight allowance must be considered based on the anticipated weight and location of partitions, but not less than 1 kPa over the area of floor being considered.

A-4.1.4.1.(6)   Counteracting Dead Load Due to Soil. Examples of structures that traditionally employ the dead load of soil to resist loadings are pylon signs, tower structures, retaining walls, and deadmen, which resist wind uplift and overturning in light structures.

A-4.1.5.1.(1)   Loads Due to Use of Floors and Roofs. In many areas of buildings, such as equipment areas, service rooms, factories, storage areas, warehouses, museums, and office filing areas, live loads due to their intended use may exceed the minimum specified loads listed in Table 4.1.5.3. In these instances, the probable live load shall be calculated and used as the specified live load for the design of that particular area.

A-Table 4.1.5.3.   Considerations for Live Loads.

Arenas, Grandstands and Stadia

The designer should give special consideration to the effects of vibration.

Attics - Limited Accessibility

Attic live loading is not required when the ceiling below the attic consists of removable panels that permit access to the ceiling space without loading the ceiling supporting members. Attic live loading is not required in any area of the attic where the least dimension of the attic space is less than 500 mm.

Corridors, Aisles and Rows of Seats

The spaces between rows of seats are typically designed for the loads of the occupancy they serve. Rows of seats typically discharge into aisles that are designed for the loads used for the rows of seats. Corridors have a minimum width of 1 100 mm and may serve as collectors for aisles; they are therefore part of the exit system and are required to be designed for a minimum live load of 4.8 kPa.

Floor Areas That Could Be Used As Viewing Areas

Some interior balconies, mezzanines, corridors, lobbies and aisles that are not intended to be used by an assembly of people as viewing areas are sometimes used as such; consequently, they are subject to loadings much higher than those for the occupancies they serve. Floor areas that may be subject to such higher loads must, therefore, be designed for a loading of 4.8 kPa.

Lecture Halls and Classrooms

For the purposes of applying the requirements of Table 4.1.5.3., lecture halls with fixed seats are similar to theatres in configuration (the seats may have a writing tablet affixed to one arm). Classrooms are typically furnished with full-sized desks having separate or integrated seats.

Minimum Roof Live Load

Articles 4.1.5.3. and 4.1.5.10. stipulate a minimum uniform roof live load of 1.0 kPa and a minimum concentrated live load of 1.3 kN. These live loads are “use and occupancy loads” intended to provide for maintenance loadings: they are not reduced as a function of area or as a function of the roof slope due to their variability in distribution and location.

Office Areas

The general minimum specified load for office areas, including mezzanines, is 2.4 kPa.

A minimum specified load of 4.8 kPa applies to office areas in basements, which are normally slab-on-grade, and to office areas in floor areas that may be subject to an increase in loading for brief periods, for example, when tenants temporarily use that floor area to store furniture, equipment and files while moving in or out of the building.

Where an office building is situated on a level site, all floors are uniform in elevation, and there are no mezzanines, allocating the correct loads is straightforward. However, where the site is steeply sloped, the situation is more complex—even more so where there are also mezzanines.

The principle is that floor levels and mezzanines with access to the exterior at ground level could be used as staging areas during a move, and so, must be designed for a minimum of 4.8 kPa. Also, there is usually an area adjacent to the exterior exit that can accommodate trucks.

Vehicle Loads

A special study should be undertaken to determine the distributed loads to be used for the design of floors and areas used by vehicles exceeding 9 000 kg gross weight and of driveways and sidewalks over areaways and basements. Where appropriate, the designer should refer to CSA S6, “Canadian Highway Bridge Design Code.”

A-4.1.5.5.   Loads on Exterior Areas. In Article 4.1.5.5., “accessible” refers to the lack of a physical barrier that prevents or restricts access by vehicles or persons to the site in the context of the specific use.

Information on the design of roof parking decks and exterior areas that are accessible to vehicular traffic can be found in the Commentary entitled Live Loads in the “Structural Commentaries (User's Guide – NBC 2020: Part 4 of Division B).”

A-4.1.5.8.   Tributary Area. Information on tributary area can be found in the Commentary entitled Live Loads in the “Structural Commentaries (User's Guide – NBC 2020: Part 4 of Division B).”

A-Table 4.1.5.9.   Loads Due to Concentrations. Special study is required to determine concentrated loads for the design of floors and areas used by vehicles exceeding 9 000 kg gross weight, and of driveways and sidewalks over areaways and basements. Where appropriate the designer should refer to CSA S6, “Canadian Highway Bridge Design Code.”

A-4.1.5.11.   Crane-Supporting Structures. Guidance on crane-supporting structures can be found in CSA S16, “Design of steel structures.”

A-4.1.5.14. and 4.1.5.15.(1)   Design of Guards. In the design of guards, due consideration should be given to the durability of the members and their connections.

A-4.1.5.17.   Loads on Firewalls. Information on loads on firewalls can be found in the Commentary entitled Structural Integrity of Firewalls in the “Structural Commentaries (User's Guide – NBC 2020: Part 4 of Division B).”

A-4.1.6.1.(1)   Specified Load Due to Rain or to Snow and Associated Rain. The location of a new building or obstruction may affect the snow loads on the roof of an adjacent existing building—on the same property or on an adjacent one—that is lower in height. In such cases, designers should consider Sentence 2.2.2.1.(1) of Division C.

Additional guidance can be found in the Commentary entitled Snow Loads in the “Structural Commentaries (User's Guide – NBC 2020: Part 4 of Division B).”

A-4.1.6.2.   Coefficients for Snow Loads on Roofs. Information on coefficients for snow loads on roofs can be found in the Commentary entitled Snow Loads in the “Structural Commentaries (User's Guide – NBC 2020: Part 4 of Division B).”

A-4.1.6.2.(2)   Basic Roof Snow Load Factor. Figure A-4.1.6.2.(2) shows the basic roof snow load factor, Cb, plotted against .

Figure A-4.1.6.2.(2)

Basic roof snow load factor, Cb

A-4.1.6.3.(2)   Full and Partial Loading under Snow Loads. Information on full and partial snow loading on roofs can be found in the Commentary entitled Snow Loads in the “Structural Commentaries (User's Guide – NBC 2020: Part 4 of Division B).”

A-4.1.6.4.(1)   Rain Loads. Information on rain loads can be found in the Commentary entitled Rain Loads in the “Structural Commentaries (User's Guide – NBC 2020: Part 4 of Division B).”

A-4.1.6.4.(3)   Flow Control Drains. The National Plumbing Code (NPC) contains requirements regarding the use of flow control roof drains. The designer must ensure that the building complies with the BC Building Code Book I and Book II: Plumbing Systems

A-4.1.6.7.(1)   Roof Projections. Elevator, air-conditioning and fan housings, small penthouses and wide chimneys are examples of roof projections.

Figure A-4.1.6.7.(1)

Roof projections

A-4.1.6.7.(2)   Values of Ca for Small Roof Projections. Calculating Ca in accordance with Article 4.1.6.5. rather than Sentence 4.1.6.7.(1) results in lower values for small projections.

A-4.1.6.9.   Snow on Gable Roofs.

Figure A-4.1.6.9.

Load cases for gable roofs

Table A-4.1.6.9.

Wind Exposure, Slope and Accumulation Factors for Load Cases in Figure A-4.1.6.9.

| Load Case | Roof Slope, α | Factors |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  |  | Cw | Cs(1) | Ca |  |
|  |  |  |  | Upwind Side | Downwind Side |
| I | 0° ≤ α ≤ 90° | (2) | f(α) | 1.0 | 1.0 |
| II(3) | 15° < α ≤ 20° | 1.0 | f(α) | 0.0 | 0.25 + α/20 |
|  | 20° < α ≤ 90° |  |  |  | 1.25 |

Notes to Table A-4.1.6.9.:

(1) Cs varies as a function of slope, α, as defined in Sentences 4.1.6.2.(5) and (6).

(2) The value of Cw for load case I is as prescribed in Sentences 4.1.6.2.(3) and (4).

(3) Case II loading does not apply to gable roofs with slopes of 15° or less, to single-sloped (shed) roofs, or to flat roofs.

A-4.1.6.16.   Roofs with Solar Panels. Information on the design of roofs with solar panels can be found in the Commentary entitled Snow Loads in the “Structural Commentaries (User's Guide – NBC 2020: Part 4 of Division B).”

A-4.1.6.16.(3)   Snow Obstructed from Sliding by Solar Panels. Figure A-4.1.6.16.(3) shows the areas on sloped roofs with solar panels where snow is considered to be obstructed from sliding by the solar panels and the slope factor, Cs, must be taken as 1.0.

Figure A-4.1.6.16.(3)

Areas on sloped roofs with solar panels where snow is obstructed from sliding by the solar panels

Note to Figure A-4.1.6.16.(3):

(1) Cs = as specified in Sentences 4.1.6.2.(5) to (7)

A-4.1.6.16.(4)(b)   Snow Loads for a Sloped Roof with Parallel Flush Solar Panels Where 
wg ≥ wp. Figure A-4.1.6.16.(4)(b) shows the snow loads for a sloped roof with Parallel Flush solar panels where the gap width, wg, between the panels is greater than or equal to the panel width, wp.

Figure A-4.1.6.16.(4)(b)

Snow loads for a sloped roof with Parallel Flush solar panels where wg ≥ wp

A-4.1.6.16.(4)(c)   Snow Loads for a Sloped Roof with Parallel Flush Solar Panels Where 
wg < wp. Figure A-4.1.6.16.(4)(c) shows the snow loads for a sloped roof with Parallel Flush solar panels where the gap width, wg, between the panels is less than the panel width, wp.

Figure A-4.1.6.16.(4)(c)

Snow loads for a sloped roof with Parallel Flush solar panels where wg < wp

A-4.1.6.16.(5)(a)   Snow Loads for a Flat Roof with Parallel Raised Solar Panels. Figure A-4.1.6.16.(5)(a) shows the snow loads for a flat roof with Parallel Raised solar panels.

Figure A-4.1.6.16.(5)(a)

Snow loads for a flat roof with Parallel Raised solar panels

A-4.1.6.16.(5)(b)   Snow Loads for a Sloped Roof with Parallel Raised Solar Panels. Figure A-4.1.6.16.(5)(b) shows the snow loads for a sloped roof with Parallel Raised solar panels.

Figure A-4.1.6.16.(5)(b)

Snow loads for a sloped roof with Parallel Raised solar panels

A-4.1.6.16.(6)   Snow Loads for a Flat Roof with Tilted Solar Panels. Figure A-4.1.6.16.(6) shows the snow loads for a flat roof with Tilted solar panels.

Figure A-4.1.6.16.(6)

Snow loads for a flat roof with Tilted solar panels

A-4.1.6.16.(6)(c)   Variation of Ca with hg − CbCwSs/γ. Figure A-4.1.6.16.(6)(c) shows the variation of the accumulation factor, Ca, with the height of the lowest edge of the panels above the surface of the uniform snow load, hg − CbCwSs/γ, for a flat roof with Tilted solar panels.

Figure A-4.1.6.16.(6)(c)

Variation of Ca with hg − CbCwSs/γ for a flat roof with Tilted solar panels

A-4.1.7.1.(6)   Computational Fluid Dynamics (CFD). It is not currently possible to verify the reliability and accuracy of CFD and no standards address it; as such, this method is not permitted to be used to determine specified wind loads.

A-4.1.7.2.(2)   Natural Frequency. Information on calculating the natural frequency of a building can be found in the Commentary entitled Wind Load and Effects in the “Structural Commentaries (User's Guide – NBC 2020: Part 4 of Division B).”

A-4.1.7.3.(5)(c)   Procedure for Calculating Intermediate Ce. Information on calculating intermediate values of Ce between two exposures can be found in the Commentary entitled Wind Load and Effects in the “Structural Commentaries (User's Guide – NBC 2020: Part 4 of Division B).”

A-4.1.7.3.(10)   Internal Gust Effect Factor, Cgi. The effect of building envelope flexibility can be included in the calculation of Cgi. See the Commentary entitled Wind Load and Effects in the “Structural Commentaries (User's Guide – NBC 2020: Part 4 of Division B).”

A-4.1.7.5.(2) and (3)   Pressure Coefficients for Main Structural System on Rectangular Buildings.

Figure A-4.1.7.5.(2) and (3)

Values of Cp for main structural system on rectangular buildings

A-4.1.7.5.(4)   Pressure Coefficients for Roof and Wall Claddings and Secondary Structural Supports of Cladding on Rectangular Buildings.

Figure A-4.1.7.5.(4)

Values of Cp for roof and wall claddings and secondary structural supports of cladding on rectangular buildings

Notes to Figure A-4.1.7.5.(4):

(1) The larger of W or D is to be used.

(2) Where vertical ribs deeper than 1 m are present on the walls, the dimensions 0.1D and 0.1W must be changed to 0.2D and 0.2W and the negative value of Cp must be changed from –1.2 to –1.4.

A-4.1.7.7.(2)   Cladding on Parapets. Information on the design of cladding on parapets can be found in the Commentary entitled Wind Load and Effects in the “Structural Commentaries (User's Guide – NBC 2020: Part 4 of Division B).”

A-4.1.7.8.(2) and (3)   Exposure Factor for Dynamic Procedure.

Figure A-4.1.7.8.(2) and (3)

Exposure factor, Ce, for dynamic procedure

Notes to Figure A-4.1.7.8.(2) and (3):

(1) Curve A represents Ce for open terrain, as defined in Clause 4.1.7.3.(5)(a).

(2) Curve B represents Ce for rough terrain, as defined in Clause 4.1.7.3.(5)(b).

A-4.1.7.8.(4)   Peak Factor, Size Reduction Factor and Gust Energy Ratio.

Figure A-4.1.7.8.(4)-A

Peak factor, gp

Figure A-4.1.7.8.(4)-B

Size reduction factor, s

Figure A-4.1.7.8.(4)-C

Gust energy ratio, F

A-4.1.7.9.(1)   Full and Partial Wind Loading. Information on full and partial loading under wind loads can be found in the Commentary entitled Wind Load and Effects in the “Structural Commentaries (User's Guide – NBC 2020: Part 4 of Division B).”

Figure A-4.1.7.9.(1)

Full and partial wind loading

A-4.1.7.11.   Exterior Ornamentations, Equipment and Appendages. Appendages may increase the overall forces in the design of the building structure and need to be accounted for.

A-4.1.7.12.   Attached Canopies on Low Buildings (H ≤ 20 m). An attached canopy is different from an overhang, which is an extension of the roof surface.

Figure 4.1.7.12.-A, which provides the gust pressure coefficients on the upper and lower surfaces of the canopy, is used to design the cladding for the canopy and the associated fasteners. Figure 4.1.7.12.-B, which provides the net gust pressure coefficients on the canopy, is used to design the structure of the canopy (e.g., joists, posts, building fasteners).

In addition to the external wind pressure addressed in Article 4.1.7.12., the internal pressure addressed in Table 4.1.7.7. should also be considered, where applicable to the canopy.

A-4.1.7.13.   Roof-Mounted Solar Panels on Buildings of Any Height. Article 4.1.7.13. provides procedures for calculating the wind loads on roof-mounted arrays of solar panels that satisfy particular geometrical requirements.

The area of the roof that is covered by a solar array does not need to be designed for the simultaneous application of the solar array wind loads and the roof wind loads. However, the cumulative load effect of all solar panels does need to be accounted for in accordance with Article 4.1.7.11. Furthermore, the roof needs to be designed for the case where the solar array has been removed.

Solar arrays that are mechanically fastened to the underlying roof structure can modify the load distribution on the roof. The loads from such arrays must be applied to the structural components of the roof as concentrated loads at the points of attachment.

The calculations in Article 4.1.7.13. assume that the solar panels and their mounting system are rigid. Therefore, there is no allowance for wind-induced vibration of these components. However, if the panels and their mounting system have a natural frequency less than about 10 Hz, it is possible that loads will be magnified as a result of wind-induced vibration. In such cases, it is recommended that expert opinion be sought and that the dynamic effects be investigated in more detail.

Figure A-4.1.7.13. shows an example of a roof-mounted solar array with exposed and unexposed panels. For the purpose of determining the edge factor, E, to be applied in the calculations of Article 4.1.7.13., a panel is defined as exposed if it is located within a distance of 1.5 times the panel chord length, Lp, from an exposed edge of the array. An exposed edge of the array is considered to occur where the horizontal distance, d1, from the panel edge to the roof edge (ignoring any rooftop equipment) is greater than 0.5h, h being the reference height of the roof, and greater than max(4h2,1.2 m), h2 being the height of the panel's highest point above the roof surface. An exposed edge is also considered to occur where the horizontal distance, d2, from the panel edge to the nearest edge in the next panel row (or across a gap in the same panel row) is greater than max(4h2,1.2 m).

Figure A-4.1.7.13.

Plan view of a roof-mounted solar array with exposed and unexposed panels

A sample calculation of net design wind pressure for roof-mounted solar panels is provided in the Commentary entitled Wind Load and Effects in the “Structural Commentaries (User's Guide – NBC 2020: Part 4 of Division B).”

The installation of solar arrays on a roof can significantly affect the distribution of snow loads on the roof. Designers should be aware that the accumulation of snow and ice around solar panels can influence the calculations described in Article 4.1.7.13. For example, accumulated snow may obstruct the ventilation areas between the roof and the underside of the panels, thereby increasing wind loads on the panels. For the design of the anchorage of a solar array to the roof and of the array itself, the pressure equalization factor, γa, in Sentence 4.1.7.13.(2) should be taken as 1.0, unless it can be shown that the accumulation of snow and ice will not obstruct the gaps between the panels in the array.

A-4.1.8.2.(1)   Notation.

Definition of ex

Information on the calculation of torsional moments can be found in the Commentary entitled Design for Seismic Effects in the “Structural Commentaries (User's Guide – NBC 2020: Part 4 of Division B).”

Definition of W

Information on the definition of specified dead load, W, can be found in the Commentary entitled Design for Seismic Effects in the “Structural Commentaries (User's Guide – NBC 2020: Part 4 of Division B).”

A-4.1.8.3.(4)   General Design of the SFRS. Information on the general design requirements for the SFRS can be found in the Commentary entitled Design for Seismic Effects in the “Structural Commentaries (User's Guide – NBC 2020: Part 4 of Division B).”

A-4.1.8.3.(6)   General Design of Stiff Elements. Information on the general design requirements for stiff elements can be found in the Commentary entitled Design for Seismic Effects in the “Structural Commentaries (User's Guide – NBC 2020: Part 4 of Division B).”

A-4.1.8.3.(7)(b) and (c)   Stiffness Imparted to the Structure from Elements Not Part of the SFRS. Information on stiffness imparted to the structure from elements not part of the SFRS can be found in the Commentary entitled Design for Seismic Effects in the “Structural Commentaries (User's Guide – NBC 2020: Part 4 of Division B).”

A-4.1.8.3.(8)   Structural Modeling. Information on structural modeling can be found in the Commentary entitled Design for Seismic Effects in the “Structural Commentaries (User's Guide – NBC 2020: Part 4 of Division B).”

A-4.1.8.4.(2) and (3)   Site Designation. It is preferable to determine the site designation as XV on the basis of the average shear wave velocity, Vs30, calculated from in situ measurements of shear wave velocity. This site designation will typically result in a lower seismic demand than a site designation XS determined using the energy-corrected average standard penetration resistance, 60, or the average undrained shear strength, . Further information on site designation can be found in the Commentary entitled Design for Seismic Effects in the “Structural Commentaries (User's Guide – NBC 2020: Part 4 of Division B).”

A-4.1.8.4.(3)   Site Class. The Vs30 ranges in Table 4.1.8.4.-B are retained from the NBC 2015. Where required for the application of a standard referenced in Subsection 4.1.8., the Site Class for a particular site designation Xv can be determined from Table 4.1.8.4.-B on the basis of the value of Vs30. Further information on Site Class can be found in the Commentary entitled Design for Seismic Effects in the “Structural Commentaries (User's Guide – NBC 2020: Part 4 of Division B).”

A-4.1.8.4.(6)   Log–Log Interpolation. The value of S(T) for Ti < T < Tj can be determined using log–log interpolation as follows:

where

log   = logarithm to base 10.

A-Table 4.1.8.5.-A   Serviceability Limit States for Earthquake. Information on serviceability limit states for earthquake can be found in the Commentary entitled Design for Seismic Effects in the “Structural Commentaries (User's Guide – NBC 2020: Part 4 of Division B).”

A-Table 4.1.8.6.   Structural Irregularities.

Structural Irregularities

Information on structural irregularities can be found in the Commentary entitled Design for Seismic Effects in the “Structural Commentaries (User's Guide – NBC 2020: Part 4 of Division B).”

Gravity-Induced Lateral Demand – Type 9 Irregularity

Uncoupled concrete and masonry shear walls where a large fraction of the overturning resistance is provided by axial compression, rather than through yielding of the longitudinal reinforcement, are less susceptible to amplified displacements due to gravity-induced lateral demands because the axial loads have a self-centering effect on the shear walls. Walls that are stronger than the foundation and other systems such as coupled walls, braced frames, and moment frames are more susceptible to amplified displacements due to gravity-induced lateral demands. A lower limit on α is thus specified for such systems. Further information on the impacts of gravity-induced lateral demands on the seismic response of buildings can be found in the Commentary entitled Design for Seismic Effects in the “Structural Commentaries (User's Guide – NBC 2020: Part 4 of Division B).”

A-4.1.8.7.(1)   Dynamic Analysis Procedures. Information on dynamic analysis procedures can be found in the Commentary entitled Design for Seismic Effects in the “Structural Commentaries (User's Guide – NBC 2020: Part 4 of Division B).”

A-Table 4.1.8.9.   Industrial-Type Steel Structures. Guidance on the height limits, system restrictions and additional analysis and design requirements for steel SFRSs in industrial-type structures, intended essentially to support equipment, tanks or an industrial process, can be found in Annex M, Seismic Design of Industrial Steel Structures, of CSA S16, “Design of steel structures.”

A-4.1.8.9.(4)   Vertical Variations in RdRo. Information on vertical variations in RdRo can be found in the Commentary entitled Design for Seismic Effects in the “Structural Commentaries (User's Guide – NBC 2020: Part 4 of Division B).”

A-4.1.8.9.(5)   RdRo and Equivalent Systems. Information on the RdRo of equivalent systems can be found in the Commentary entitled Design for Seismic Effects in the “Structural Commentaries (User's Guide – NBC 2020: Part 4 of Division B).”

A-4.1.8.10.(5) and (6)   Mid-rise Timber SFRSs. Information on structural irregularities in mid-rise wood construction and on how to determine the number of storeys for application in Sentences 4.1.8.10.(5) and (6) can be found in the Commentary entitled Design for Seismic Effects in the “Structural Commentaries (User's Guide – NBC 2020: Part 4 of Division B).”

A-4.1.8.10.(7)   Gravity-Induced Lateral Demand – Type 9 Irregularity. Structural systems that include components such as inclined columns or horizontal floor cantilevers can induce lateral force demands on the SFRS under gravity loads. Buildings with such gravity-induced lateral demands on the SFRS are more likely to experience severe damage during strong ground shaking due to their tendency to drift only in one direction, leading to large residual displacements or instability. To determine if a building is susceptible to amplification of displacements due to gravity-induced lateral demands, the lateral resistance of the yielding mechanism to resist earthquake forces alone, Qy, must be compared with the gravity-induced lateral demand, QG, at the same location. The force component selected for this comparison depends on the yielding mechanism for the SFRS. For example, for a coupled wall, the overturning moment resistance at the level of the expected plastic hinges should be compared with the overturning moment demand (at the same level) due to gravity loads alone, whereas for a steel-braced frame, the storey shear at the critical level of the yielding system should be compared with the storey shear demand (at the same level) due to the gravity loads alone. If the gravity-induced lateral demands exceed the limits prescribed in Sentence 4.1.8.10.(9), amplifications in seismic displacements due to gravity-induced lateral demands can only be identified through non-linear dynamic analyses using models that adequately represent the hysteretic behaviour of the SFRS. Further information on the impacts of gravity-induced lateral demands on the seismic response of buildings can be found in the Commentary entitled Design for Seismic Effects in the “Structural Commentaries (User's Guide – NBC 2020: Part 4 of Division B).”

A-4.1.8.10.(9)   Gravity-Induced Lateral Demand – Non-linear Dynamic Analysis. Information on Non-linear Dynamic Analysis, including ground motion time histories, target response spectra and acceptance criteria, can be found in the Commentary entitled Design for Seismic Effects in the “Structural Commentaries (User's Guide – NBC 2020: Part 4 of Division B).”

A-4.1.8.10.(10)(a)   Sloped Column Irregularity. The presence of inclined vertical members in a building leads to a coupling of its horizontal and vertical vibrational modes. As a result of this coupling, horizontal accelerations of the building cause vertical accelerations of the mass supported by the inclined vertical members. Vertical ground motions cause additional vertical accelerations of the mass.

The additional earthquake forces resulting from both the coupling of horizontal and vertical vibrational modes and the vertical ground motions can be determined using the Dynamic Analysis Procedure described in Article 4.1.8.12. with RdRo = 1.0. The structural model used in the analysis must account for the vertical accelerations of all mass supported by inclined vertical members and must include the SFRS, the inclined vertical members, and all structural framing elements that transfer inertial forces generated by the vertical accelerations of the mass supported by the inclined vertical members.

The additional earthquake forces are sensitive to the degree of coupling between the vertical and horizontal vibrational modes of the building. Thus, to determine the maximum additional earthquake forces for design, the range of possible stiffness values for all structural members must be considered.

Further information on the analysis of structures with a sloped column irregularity, including a simple procedure for scaling the analysis results to avoid having to perform multiple analyses with a range of stiffness values and vertical ground motions, can be found in the Commentary entitled Design for Seismic Effects in the “Structural Commentaries (User's Guide – NBC 2020: Part 4 of Division B).”

A-4.1.8.11.(3)   Determination of the Fundamental Period, Ta. Information on the determination of the fundamental period, Ta, can be found in the Commentary entitled Design for Seismic Effects in the “Structural Commentaries (User's Guide – NBC 2020: Part 4 of Division B).”

A-4.1.8.12.(1)(a)   Linear Dynamic Analysis. Information on Linear Dynamic Analysis can be found in the Commentary entitled Design for Seismic Effects in the “Structural Commentaries (User's Guide – NBC 2020: Part 4 of Division B).”

A-4.1.8.12.(1)(b)   Non-linear Dynamic Analysis. Information on Non-linear Dynamic Analysis can be found in the Commentary entitled Design for Seismic Effects in the “Structural Commentaries (User's Guide – NBC 2020: Part 4 of Division B).”

A-4.1.8.12.(3)   Ground Motion Time Histories. Information on ground motion time histories can be found in the Commentary entitled Design for Seismic Effects in the “Structural Commentaries (User's Guide – NBC 2020: Part 4 of Division B).”

A-4.1.8.12.(4)(a)   Accidental Torsional Moments. Information on accidental torsional moments can be found in the Commentary entitled Design for Seismic Effects in the “Structural Commentaries (User's Guide – NBC 2020: Part 4 of Division B).”

A-4.1.8.13.(4)   Deflections and Sway Effects. Information on deflections and sway effects can be found in the Commentary entitled Design for Seismic Effects in the “Structural Commentaries (User's Guide – NBC 2020: Part 4 of Division B).”

A-4.1.8.15.(1)   Diaphragms and Their Connections. Information on diaphragms and their connections can be found in the Commentary entitled Design for Seismic Effects in the “Structural Commentaries (User's Guide – NBC 2020: Part 4 of Division B).”

A-4.1.8.15.(3)   Ductile Diaphragms. Information on the design of struts, collectors, chords and connections for ductile diaphragms can be found in the Commentary entitled Design for Seismic Effects in the “Structural Commentaries (User's Guide – NBC 2020: Part 4 of Division B).”

A-4.1.8.15.(4)   Influence of Dynamic Diaphragm In-Plane Response.

Clause 4.1.8.15.(4)(a)

In lieu of carrying out a special study as stated in Subclause 4.1.8.15.(4)(a)(iii), the anticipated total deformation demand on the vertical elements of the SFRS, including inelastic deformations, may be taken as equal to RoRd(ΔB + ΔD) − RoΔD, i.e., the difference between the total storey drift including inelastic deformation effects and diaphragm deformations, RoRd(ΔB + ΔD), and the diaphragm deformation under Ro times the seismic load, where Ro may be replaced by the actual overstrength of the SFRS vertical elements. The design engineer must verify that the SFRS vertical elements have sufficient deformation capacity to accommodate the computed deformation demand. If the vertical elements of the SFRS do not have sufficient deformation capacity, the design forces for the vertical elements of the SFRS must be magnified by Rd(1 + ΔD/ΔB)/(Rd + ΔD/ΔB). The calculation of the magnified design forces is iterative as the ΔD/ΔB ratio may change when using higher design forces for the vertical elements of the SFRS. Reducing the ΔD/ΔB ratio by increasing the stiffness of the roof diaphragm relative to that of the vertical elements of the SFRS may be considered to reduce the deformation demand on the vertical elements of the SFRS. Additional information can be found in the Commentary entitled Design for Seismic Effects in the “Structural Commentaries (User's Guide – NBC 2020: Part 4 of Division B).”

Clause 4.1.8.15.(4)(b)

The dynamic response of the diaphragm with the vertical elements of the SFRS under seismic excitation involves several modes of vibration that affect both the amplitude and distribution of in-plane shears and bending moments in the roof diaphragm. The shape of the fundamental mode of vibration resembles the deflected shape of the diaphragm/vertical SFRS elements under a distributed lateral load while higher modes involve increasing numbers of zero crossings of the deflected shapes along the length of the diaphragm, similar to the modes of a simply supported beam with distributed mass. Shears and bending moments therefore deviate from the values obtained from the equivalent static force procedure essentially due to higher mode response. Modal contributions to shears and bending moments in the diaphragms can be obtained from a Linear Dynamic Analysis. The contribution from the higher modes is generally more pronounced when the ΔD/ΔB ratio, the period in the first mode, or the ratio S(0.2)/S(2.0) is increased. It also increases when the SFRS is designed with a higher Rd factor as inelastic deformations of the vertical elements of the SFRS attenuate the first mode response. Methods to take into account the inelastic higher mode effects on in-plane diaphragm shears and moments are discussed in the Commentary entitled Design for Seismic Effects in the “Structural Commentaries (User's Guide – NBC 2020: Part 4 of Division B).”

A-4.1.8.15.(5)   Discontinuities. Information on elements supporting discontinuities can be found in the Commentary entitled Design for Seismic Effects in the “Structural Commentaries (User's Guide – NBC 2020: Part 4 of Division B).”

A-4.1.8.15.(6)   Vertical Variations in RdRo. Information on elements of the SFRS below the variation in RdRo can be found in the Commentary entitled Design for Seismic Effects in the “Structural Commentaries (User's Guide – NBC 2020: Part 4 of Division B).”

A-4.1.8.15.(7)   Concurrent Yielding. Information on the effects of concurrent yielding of elements can be found in the Commentary entitled Design for Seismic Effects in the “Structural Commentaries (User's Guide – NBC 2020: Part 4 of Division B).”

A-4.1.8.15.(8)   Design Force in Elements. Information on the design force in elements can be found in the Commentary entitled Design for Seismic Effects in the “Structural Commentaries (User's Guide – NBC 2020: Part 4 of Division B).”

A-4.1.8.16.(1)   Foundation Movement. The bearing stress distribution in soil or rock that is used to determine the factored overturning resistance of the foundation influences the rotation of the foundation, which occurs due to the forces applied by the SFRS. Generally, all foundations will rotate on soil or rock. In particular, footings (a type of foundation unit) often undergo uplift at one end, and if the factored bearing stress at the other end is only over a short length, then the uplift and rotation of the footing can be significant. CSA A23.3, “Design of concrete structures,” contains design requirements for footings that rotate and uplift; see also the Commentary entitled Design for Seismic Effects in the “Structural Commentaries (User's Guide – NBC 2020: Part 4 of Division B)” for guidance and methods to account for foundation movement.

A-4.1.8.16.(2)   Actual Lateral Load Capacity of the SFRS. The actual lateral load capacity of the SFRS includes the effects of member overstrengths similar to those used to determine the Ro factors. The applicable CSA design standards include requirements on calculating the overstrengths and capacities, which may be based on the members' nominal or probable resistance. The actual capacities are larger than the factored loads and factored resistances and, in many cases, can be significantly larger. Note that the foundations designed to develop the capacity of the SFRS will undergo movements and Sentence 4.1.8.16.(1) still applies.

A-4.1.8.16.(4)   Overturning Resistance of the Foundation. For the special case where the foundation is a footing, and where it and the attached SFRS are not constrained against rotation, it is permitted, with certain limitations, to size the footing to have a factored overturning resistance less than the overturning capacity of the supported SFRS. This approach results in a smaller footing, increased footing rotations, increased drifts in the structure, and increased soil stresses, all of which are over and above those associated with footings sized to have a factored overturning resistance equal to or greater than the overturning capacity of the SFRS. The footing itself must have a factored resistance capable of developing the required soil or rock reactions. An example of a footing and SFRS that are not constrained against rotation is an SFRS on a footing near the ground surface such that it can rotate freely and is attached to a gravity-load-resisting system (non-SFRS) that is laterally flexible and provides little lateral resistance. For this case, the SFRS is usually analyzed on its own and the resulting displacements are imposed on the non-SFRS elements in order to assess the effects on them. Cases where the footing and SFRS are attached to a system that has significant lateral stiffness require careful analysis and engineering judgement, or the footing can be capacity-designed.

Limiting the overturning moment on the foundation and the RdRo value provides some control on the increase in lateral displacement, drift and stress in the soil or rock. Cases that exceed these limits require special study.

For the common case where the SFRS and/or the footing are constrained in some way against rotation, the footing's factored resistance must be equal to or greater than the capacity of the supported SFRS. An example of an SFRS constrained against freely rotating with the footing is an SFRS attached to adjacent foundation walls by below-grade diaphragms. Examples of footings constrained against free rotation are footings that use soil anchors to resist overturning, footings on piles, and raft foundations. Note that Sentence 4.1.8.16.(1) still applies.

See CSA A23.3, “Design of concrete structures,” and the Commentary entitled Design for Seismic Effects in the “Structural Commentaries (User's Guide – NBC 2020: Part 4 of Division B).”

A-4.1.8.16.(6)(a)   Interconnection of Foundation Elements. Information on the interconnection of piles or pile caps, drilled piers, and caissons can be found in the Commentary entitled Design for Seismic Effects in the “Structural Commentaries (User's Guide – NBC 2020: Part 4 of Division B).”

A-4.1.8.16.(7)   Earthquake Lateral Pressures from Backfill or Natural Ground. Information on methods of computing the seismic lateral pressures from backfill or natural ground can be found in the Commentary entitled Design for Seismic Effects in the “Structural Commentaries (User's Guide – NBC 2020: Part 4 of Division B).”

A-4.1.8.16.(8)(a)   Cyclic Inelastic Behaviour of Foundation Elements. Information on the cyclic inelastic behaviour of piles or pile caps, drilled piers, and caissons can be found in the Commentary entitled Design for Seismic Effects in the “Structural Commentaries (User's Guide – NBC 2020: Part 4 of Division B).”

A-4.1.8.16.(9)   Alternative Foundation Ties. Alternative methods of tying foundations together, such as a properly reinforced floor slab capable of resisting the required tension and compression forces, may be used. Passive soil pressure against buried pile caps may not be used to resist these forces.

A-4.1.8.16.(10)   Liquefaction. Information on liquefaction can be found in the Commentary entitled Design for Seismic Effects in the “Structural Commentaries (User's Guide – NBC 2020: Part 4 of Division B).”

A-4.1.8.17.(1)   Slope Stability. Information on slope instability can be found in the Commentary entitled Design for Seismic Effects in the “Structural Commentaries (User's Guide – NBC 2020: Part 4 of Division B).”

A-4.1.8.18.   Elements of Structures, Non-structural Components and Equipment. Information on the requirements of Article 4.1.8.18. can be found in the Commentary entitled Design for Seismic Effects in the “Structural Commentaries (User's Guide – NBC 2020: Part 4 of Division B).”

A-Table 4.1.8.18.   Non-structural Components and Equipment. The failure or detachment of non-structural components and equipment during an earthquake can present a major threat to life safety. The design requirements presented in Article 4.1.8.18. are intended to ensure that such components and their connections to the building will retain their integrity during strong ground shaking. Guidelines for the seismic risk reduction of such components are given in CSA S832, “Seismic risk reduction of operational and functional components (OFCs) of buildings.”

A-4.1.8.18.(7)(e)   Post-installed Anchors. Information on the cyclic tension load testing of anchors referred to in Clause 4.1.8.18.(7)(e) can be found in International Code Council Evaluation Service (ICC-ES) Evaluation Reports. Additional information can be found in the Commentary entitled Design for Seismic Effects in the “Structural Commentaries (User's Guide – NBC 2020: Part 4 of Division B).”

A-4.1.8.18.(13) and 4.4.3.1.(1)   Storage Racks. Free-standing storage racks contain materials typically loaded by forklift. Some are designed to store loaded pallets; however, in some cases, the stored material does not sit on a pallet. Information on storage racks can be found in the Commentary entitled Design for Seismic Effects in the “Structural Commentaries (User's Guide – NBC 2020: Part 4 of Division B).”

A-4.1.8.18.(14) and (15)   Glass Fallout and Failure. Information on glass fallout and testing for glass fallout can be found in AAMA 501.6, “Recommended Dynamic Test Method for Determining the Seismic Drift Causing Glass Fallout from a Wall System.” Every surface other than inaccessible areas or areas where occupancy is prevented or access is prevented should be considered a “walking surface.” Additional information can be found in ASCE/SEI 7, “Minimum Design Loads for Buildings and Other Structures,” in FEMA P-750, “NEHRP Recommended Seismic Provisions for New Buildings and Other Structures,” and FEMA 450-1, “NEHRP Recommended Provisions for Seismic Regulations for New Buildings and Other Structures,” and related commentaries, and in the Commentary entitled Design for Seismic Effects in the “Structural Commentaries (User's Guide – NBC 2020: Part 4 of Division B).”

A-4.1.8.18.(16)   Elements of Structures, Non-structural Components and Equipment in Structures with Supplemental Energy Dissipation. Information on the requirements of Sentence 4.1.8.18.(16) can be found in the Commentary entitled Design for Seismic Effects in the “Structural Commentaries (User's Guide – NBC 2020: Part 4 of Division B).”

A-4.1.8.18.(18)   Climatic Conditions. Climatic conditions leading to wetness or frost at the interface between the supporting base of the array and the roof surface may adversely affect the resistance provided by friction due to gravity loads.

A-4.1.8.19.(2)   Design Review. It is strongly recommended that a design review of the seismically isolated structure and its isolation system be carried out by an independent team of professional engineers and geoscientists experienced in seismic analysis methods and the theory and application of seismic isolation. The design review should include, but not be limited to, the following:

(a)   site-specific spectra,

(b)   ground motion time histories,

(c)   modeling and analyses,

(d)   testing program and results, and

(e)   final design of all structural framing elements and isolation system components.

A-4.1.8.19.(3)(a)   Non-linear Dynamic Analysis. Three-dimensional Non-linear Dynamic Analysis is a complex process requiring special expertise. Guidance on Non-linear Dynamic Analysis can be found in the Commentary entitled Design for Seismic Effects in the “Structural Commentaries (User's Guide – NBC 2020: Part 4 of Division B).”

A-4.1.8.19.(4) and 4.1.8.21.(5)   Ground Motion Time Histories. Ground motion time histories and their horizontal and vertical components must be appropriately selected and scaled according to accepted practice. Further information on ground motion time histories can be found in the Commentary entitled Design for Seismic Effects in the “Structural Commentaries (User's Guide – NBC 2020: Part 4 of Division B).”

A-4.1.8.21.(2)   Design Review. It is strongly recommended that a design review of the structure and the supplementary energy dissipation system be carried out by an independent team of professional engineers and geoscientists experienced in seismic analysis methods and the theory and application of supplementary energy dissipation. The design review should include, but not be limited to, the following:

(a)   ground motion time histories,

(b)   modeling and analyses,

(c)   testing program and results, and

(d)   final design of all structural framing elements and supplemental energy dissipation system components.

A-4.1.8.21.(4)(a)   Non-linear Dynamic Analysis. Three-dimensional Non-linear Dynamic Analysis is a complex process requiring special expertise. Guidance on Non-linear Dynamic Analysis can be found in the Commentary entitled Design for Seismic Effects in the “Structural Commentaries (User's Guide – NBC 2020: Part 4 of Division B).”

A-4.2.2.1.(1)   Subsurface Investigation. Where acceptable information on subsurface conditions already exists, the investigation may not require further physical subsurface exploration or testing.

A-4.2.2.3.(1)   Responsibilities of the Designer as Defined in Part 4. In certain situations, such as when the design is highly technical, it may be necessary for the “other suitably qualified person” to be someone responsible to the designer. In such cases the authority having jurisdiction may wish to order that the review be done by the designer.

A-4.2.4.1.(1)   Innovative Designs. It is important that innovative approaches to foundation design be carried out by a person especially qualified in the specific method applied and that the design provide a level of safety and performance at least equivalent to that provided for or implicit in the design carried out by the methods referred to in Part 4. Provision must be made for monitoring the subsequent performance of such structures so that the long-term sufficiency of the design can be evaluated.

A-4.2.4.1.(3)   Ultimate Limit States for Foundations. Information on ultimate limit states for foundations, including terminology and resistance factors, can be found in the Commentary entitled Foundations in the “Structural Commentaries (User's Guide – NBC 2020: Part 4 of Division B).”

A-4.2.4.1.(5)   Design of Foundations for Differential Movements. Information on the design of foundations for differential movements can be found in the Commentary entitled Foundations in the “Structural Commentaries (User's Guide – NBC 2020: Part 4 of Division B).”

A-4.2.4.4.(1)   Depth of Foundations. When adfreezing has occurred and subsequent freezing results in soil expansion beneath this area, the resulting uplift effect is sometimes referred to as frost jacking.

A heated building that is insulated to prevent heat loss through the foundation walls should be considered as an unheated structure unless the effect of the insulation is taken into account in determining the maximum depth of frost penetration.

A-4.2.5.1.(1)   Excavations. Information on excavations can be found in the Commentary entitled Foundations in the “Structural Commentaries (User's Guide – NBC 2020: Part 4 of Division B).”

A-4.2.6.1.(1)   Shallow Foundations. Information on shallow foundations can be found in the Commentary entitled Foundations in the “Structural Commentaries (User's Guide – NBC 2020: Part 4 of Division B).”

A-4.2.7.1.(1)   Deep Foundation Units. A deep foundation unit can be pre-manufactured or cast-in-place; it can be driven, jacked, jetted, screwed, bored or excavated; it can be of wood, concrete, steel or a combination thereof.

A-4.2.7.2.(1)   Deep Foundations. Information on deep foundations can be found in the Commentary entitled Foundations in the “Structural Commentaries (User's Guide – NBC 2020: Part 4 of Division B).”

A-4.2.7.2.(2)   Load Testing of Piles. ASTM D1143/D1143M, “Standard Test Methods for Deep Foundations Under Static Axial Compressive Load,” defines routine load test procedures that have been extensively used.

A-4.3.3.1.(1)   Precast Concrete. CSA A23.3, “Design of concrete structures,” requires precast concrete members to conform to CSA A23.4, “Precast concrete – Materials and construction.”

A-4.3.4.1.(1)   Welded Construction. Qualification for fabricators and erectors of welded construction is found in Clause 24.3 of CSA S16, “Design of steel structures.”

A-4.3.4.2.(1)   Cold-Formed Stainless Steel Members. There is currently no Canadian standard for the design of cold-formed stainless steel structural members. As an interim measure, design may be carried out using the limit states design provisions of ASCE/SEI 8, “Specification for the Design of Cold-Formed Stainless Steel Structural Members,” except that load factors, load combinations and load combination factors shall be in accordance with Subsection 4.1.3.

A-4.3.6.1.(1)   Design Basis for Glass. The load factors in Tables 4.1.3.2.-A and 4.1.3.2.-B must be applied to the adjusted wind load before designing in accordance with the referenced standard. Additional information is given in the Commentary entitled Wind Load and Effects in the “Structural Commentaries (User's Guide – NBC 2020: Part 4 of Division B).”

A-4.4.2.1.(1)   Design Basis for Storage Garages and Repair Garages. Although the scope of CSA S413, “Parking structures,” is limited to structural steel and reinforced concrete (including prestressed and post-tensioned), the intent of Sentence 4.4.2.1.(1) is to require any type of material used in the construction of storage garages and repair garages to conform to the performance level outlined in the standard.

See the Commentary entitled Live Loads in the “Structural Commentaries (User's Guide – NBC 2020: Part 4 of Division B).”

Part 5

Environmental Separation

Section  5.1.   General

5.1.1. Scope

5.1.1.1. Scope

1)   This Part is concerned with

a)   the control of condensation

i)   in building components and assemblies, and

ii)   on building materials, components and assemblies, and

b)   the transfer of heat, air, moisture and sound through

i)   building materials, components and assemblies, and

ii)   interfaces between building materials, components and assemblies.

(See Note A-5.1.1.1.(1).)

5.1.2. Application

5.1.2.1. Exposure to Exterior Space or the Ground and Separation of Dissimilar Environments

1)   This Part applies, as described in Subsection 1.3.3. of Division A, to

a)   building materials, components and assemblies exposed to exterior space or the ground, including those separating interior space from exterior space or separating interior space from the ground,

b)   building materials, components and assemblies separating environmentally dissimilar interior spaces (see Note A-5.8.), and

c)   site materials, components, assemblies and grading that may affect environmental loads on building materials, components and assemblies exposed to exterior space or the ground.

(See Note A-5.1.2.1.(1).)

5.1.3. Definitions

5.1.3.1. Defined Words

1)   Words that appear in italics are defined in Article 1.4.1.2. of Division A.

5.1.4. Resistance to Loads and Deterioration

5.1.4.1. Structural and Environmental Loads

(See Note A-5.1.4.1.)

1)   Building materials, components and assemblies that separate dissimilar environments or are exposed to the exterior shall have sufficient capacity and integrity to resist or accommodate

a)   all environmental loads, and effects of those loads, that may reasonably be expected having regard to

i)   the intended use of the building, and

ii)   the environment to which the materials, components and assemblies are subject, and

b)   all structural loads, and effects of those loads, that may reasonably be expected.

2)   Where building materials, components or assemblies perform more than one function, they shall satisfy the requirements of all of those functions. (See Note A-5.1.4.1.(2).)

3)   Compliance with Clause (1)(a) shall be demonstrated by design complying with Subsection 5.2.1. and construction conforming to that design.

4)   Compliance with Clause (1)(b) shall be demonstrated by design complying with Subsection 5.2.2., and construction conforming to that design, with regard to

a)   materials, components and assemblies, and associated loads, that are identified in Part 4,

b)   air pressure loads imposed on air barrier systems,

c)   wind up-lift imposed on roofing, and

d)   hydrostatic pressure imposed on the means of protection from moisture in the ground.

5)   For materials, components, assemblies and loads to which Sentence (4) does not apply, compliance with Clause (1)(b) shall be demonstrated

a)   by design complying with Subsection 5.2.2. for individual applicable loads and construction conforming to that design, or

b)   in the case of common materials, components and assemblies, and their installation, by proven past performance over a period of several years for individual applicable loads.

(See Note A-5.1.4.1.(5).)

6)   Materials, components and assemblies separating dissimilar environments and assemblies exposed to the exterior, including their connections, that are subject to structural loads as defined in Article 5.2.2.1. shall

a)   transfer such loads to the building structure without adverse effects on the performance of other materials, components or assemblies,

b)   not deflect to a degree that adversely affects the performance of other materials, components or assemblies (see Note A-5.1.4.1.(6)(b) and (c)), and

c)   be designed, and constructed according to that design, to accommodate (see Note A-5.1.4.1.(6)(b) and (c))

i)   the maximum relative structural movement that may reasonably be expected, and

ii)   construction tolerances that may be reasonably expected.

(See Article 4.1.3.5., Sentence 4.1.3.3.(2) and Subsection 4.1.8. for information on different types of structural movements.) (See Note A-5.1.4.1.)

5.1.4.2. Resistance to Deterioration

(See Note A-5.1.4.2.)

1)   Except as provided in Sentence (2), materials used in building components and assemblies that separate dissimilar environments, or in assemblies exposed to the exterior, shall be

a)   compatible with adjoining materials, and

b)   resistant to any mechanisms of deterioration that may reasonably be expected, given

i)   the nature and function of the materials, and

ii)   the exposure and climatic conditions in which they will be installed.

2)   Material compatibility and deterioration resistance are not required where it can be shown that incompatibility or uncontrolled deterioration will not adversely affect any of

a)   the health or safety of building users,

b)   the intended use of the building, or

c)   the operation of building services.

5.1.5. Other Requirements

5.1.5.1. Requirements in Other Parts of the Code

1)   Structural and fire safety requirements in other Parts of the British Columbia Building Code shall apply.

Section  5.2.   Loads and Procedures

5.2.1. Environmental Loads and Design Procedures

5.2.1.1. Exterior Environmental Loads

1)   Above ground climatic loads shall be determined according to Subsection 1.1.3.

2)   Except as provided in Sentence (3), below ground exterior environmental loads not described in Subsection 1.1.3. shall be determined from existing geological and hydrological data or from site tests.

3)   Where local design and construction practice has shown soil temperature analysis to be unnecessary, soil temperatures need not be determined. (See Note A-5.2.1.1.(3).)

5.2.1.2. Interior Environmental Loads

1)   Interior environmental loads shall be determined in accordance with good practice as described in Sentence 6.2.1.1.(1) based on the intended use of the space. (See Note A-5.2.1.2.(1).)

5.2.1.3. Environmental Load and Transfer Calculations

1)   Calculations related to the transfer of heat, air and moisture and the transmission of sound shall conform to good practice such as that described in the ASHRAE Handbooks.

2)   For the purposes of any analysis conducted to indicate conformance to the thermal resistance levels required in Article 5.3.1.2., soil temperatures shall be determined based on annual average soil temperature, seasonal amplitude of variation and attenuation of variation with depth.

3)   Wind load calculations shall conform to Subsection 4.1.7.

5.2.2. Structural Loads and Design Procedures

5.2.2.1. Determination of Structural Loads and Effects

1)   Where materials, components or assemblies that separate dissimilar environments or are exposed to the exterior, or their connections, are required to be designed to withstand structural loads, these loads shall be determined in accordance with Part 4. (See also Subsection 2.2.5. of Division C.)

2)   Except as provided in Article 4.1.8.18., the structural loads referred to in Sentence (1) and their related effects shall include

a)   dead loads transferred from structural elements,

b)   wind, snow, rain, hydrostatic and earth pressures,

c)   earthquake effects for post-disaster buildings, depending on their intended function (see Note A-5.2.2.1.(2)(c)),

d)   live loads due to use and occupancy, and

e)   loads due to thermal or moisture-related expansion and contraction, deflection, deformation, creep, shrinkage, settlement, and differential movement.

3)   Where materials, components or assemblies that separate dissimilar environments or are exposed to the exterior, or their connections, can be expected to be subject to loads or other effects not described in this Subsection or in Part 4, such loads or effects shall be taken into account in the design based on the most current and applicable information available.

5.2.2.2. Determination of Wind Load

(See Note A-5.2.2.2.)

1)   This Article applies to the determination of wind load to be used in the design of materials, components and assemblies, including their connections, that separate dissimilar environments or are exposed to the exterior, where these are

a)   subject to wind load, and

b)   required to be designed to resist wind load.

2)   Except as provided in Sentence (3), the wind load referred to in Sentence (1) shall be 100% of the specified wind load determined in accordance with Article 4.1.7.1.

3)   Where it can be shown by test or analysis that a material, component, assembly or connection referred to in Sentence (1) will be subject to less than 100% of the specified wind load, the wind load referred to in Sentence (1) shall be not less than the load determined by test or analysis.

4)   Except as provided in Sentence (5), the wind uplift resistance of membrane roofing assemblies shall be determined in accordance with the requirements of CAN/CSA-A123.21, “Standard test method for the dynamic wind uplift resistance of membrane-roofing systems.” (See Note A-5.2.2.2.(4).)

5)   Membrane roofing assemblies with proven past performance for the anticipated wind loads need not comply with Sentence (4). (See Note A-5.1.4.1.(5).)

5.2.2.3. Design Procedures

1)   Structural design shall be carried out in accordance with Subsection 4.1.3. and other applicable requirements in Part 4.

Section  5.3.   Heat Transfer

(See Note A-5.3.)

5.3.1. Thermal Resistance of Assemblies

5.3.1.1. Required Resistance to Heat Transfer

(See Note A-5.3.1.1.)

1)   Except as provided in Sentence (2), where a building component or assembly will be subjected to an intended temperature differential, the component or assembly shall include materials to resist heat transfer or a means to dissipate transferred heat in accordance with the remainder of this Subsection.

2)   The installation of materials to resist heat transfer in accordance with the remainder of this Subsection is not required where it can be shown that uncontrolled heat transfer will not adversely affect any of

a)   the health or safety of building users,

b)   the intended use of the building, or

c)   the operation of building services.

5.3.1.2. Properties to Resist Heat Transfer or Dissipate Heat

(See Note A-5.3.1.2.)

1)   Taking into account the conditions on either side of the environmental separator, materials and components installed to provide the required resistance to heat transfer or the means implemented to dissipate heat shall provide sufficient resistance or dissipation,

a)   to minimize surface condensation on the warm side of the component or assembly,

b)   in conjunction with other materials and components in the assembly, to minimize condensation within the component or assembly,

c)   in conjunction with systems installed for space conditioning, to meet the interior design thermal conditions for the intended occupancy, and

d)   to minimize ice damming on sloped roofs.

(See Note A-5.3.1.2.(1).)

5.3.1.3. Location and Installation of Materials Providing Thermal Resistance

1)   Where a material required by Article 5.3.1.1. is intersected by a building assembly, penetrated by a high conductance component or interrupted by expansion, control or construction joints, and where condensation is likely to occur at these intersections, penetrations or interruptions, sufficient thermal resistance shall be provided so as to minimize condensation at these locations.

2)   Materials providing required thermal resistance shall have sufficient inherent resistance to airflow or be positioned in the assembly so as to prevent convective airflow through and around the material. (See Note A-5.3.1.3.(2).)

Section  5.4.   Air Leakage

5.4.1. Air Barrier Systems

(See Note A-5.4.1.)

5.4.1.1. Required Resistance to Air Leakage

(See Note A-5.4.1.1.)

1)   Where a building component or assembly separates interior conditioned space from exterior space, interior space from the ground, or environmentally dissimilar interior spaces, the properties and position of the materials and components in those components or assemblies shall be such that they control air leakage or permit venting to the exterior so as to

a)   provide acceptable conditions for the building occupants,

b)   maintain appropriate conditions for the intended use of the building,

c)   minimize the accumulation of condensation in and the penetration of precipitation into the building component or assembly,

d)   control heat transfer to roofs where ice damming can occur,

e)   minimize the ingress of airborne radon and other soil gases from the ground with an aim to controlling the indoor concentrations of these gases to an acceptable level, and

f)   not compromise the operation of building services.

2)   Except as provided in Sentence (7), an air barrier system shall be designed and constructed to provide the principal resistance to air leakage to meet the requirements of Sentence (1).

3)   The air barrier system shall incorporate air barrier assemblies that meet the appropriate Performance Class as defined in Table 5.4.1.1. (See Note A-5.4.1.1.(3).)

Table 5.4.1.1.

Maximum Air Leakage Rates for Air Barrier Assemblies

Forming Part of Sentences 5.4.1.1.(3) and (6) and 5.4.1.2.(1) and (2)

| Performance Class | Maximum Air Leakage Rate, L/(s×m2), at a Pressure Differential of 75 Pa |
| --- | --- |
| 1 | 0.05 |
| 2 | 0.10 |
| 3 | 0.15 |
| 4 | 0.20 |
| 5 | 0.50 |

4)   The air barrier system shall be designed and constructed to be continuous

a)   across construction, control and expansion joints,

b)   across junctions between different air barrier assemblies, and

c)   around penetrations through air barrier assemblies.

(See Note A-5.4.1.1.(4).)

5)   The structural design of air barrier assemblies, including junctions between air barrier assemblies, subject to air pressure loads shall comply with Article 5.1.4.1. and Subsection 5.2.2.

6)   The maximum air leakage rates specified in Table 5.4.1.1. are permitted to be increased where it can be shown that the higher rate will not adversely affect any of

a)   the health or safety of the building users,

b)   the intended use of the building, or

c)   the operation of building services.

7)   An air barrier system is not required where it can be shown that uncontrolled air leakage will not adversely affect any of

a)   the health or safety of building users,

b)   the intended use of the building, or

c)   the operation of building services.

(See Note A-5.4.1.1.(7).)

5.4.1.2. Air Barrier Assemblies

1)   Except as provided in Sentences (2) and (3), air barrier assemblies not in contact with the ground shall

a)   conform with CAN/ULC-S742, “Standard for Air Barrier Assemblies – Specification,” and

b)   meet the selected Performance Class of Table 5.4.1.1.

(See Note A-5.4.1.2.(1).)

2)   Air barrier assemblies not evaluated in accordance with CAN/ULC-S742, “Standard for Air Barrier Assemblies – Specification,” shall be designed and constructed

a)   to meet or exceed the selected Performance Class of Table 5.4.1.1., and

b)   with at least one air barrier material intended to provide the primary resistance to air leakage that meets the requirements of CAN/ULC-S741, “Standard for Air Barrier Materials – Specification.”

(See Note A-5.4.1.2.(2).)

3)   Air barrier assemblies covered in Subsections 5.9.2., 5.9.3. and 5.9.4. shall meet the air barrier performance criteria defined in those Subsections.

4)   Below-grade air barrier assemblies in contact with the ground shall minimize the ingress of airborne radon and other soil gases. (See Note A-5.4.1.2.(4).)

Section  5.5.   Vapour Diffusion

5.5.1. Vapour Barriers

5.5.1.1. Required Resistance to Vapour Diffusion

(See Note A-5.5.1.1.)

1)   Where a building component or assembly is subjected to differentials in temperature and water vapour pressure, the properties and position of the materials and components in those components or assemblies shall be such that they control vapour diffusion or permit venting to the exterior so as to minimize the accumulation of condensation in the building component or assembly.

2)   Except as provided in Sentence (3), a vapour barrier shall be installed to provide the principal resistance to water vapour diffusion.

3)   A vapour barrier is not required where it can be shown that uncontrolled vapour diffusion will not adversely affect any of

a)   the health or safety of building users,

b)   the intended use of the building, or

c)   the operation of building services.

5.5.1.2. Vapour Barrier Properties and Installation

(See Note A-5.3.1.2.)

1)   The vapour barrier shall have sufficiently low permeance and shall be positioned in the building component or assembly so as to

a)   minimize moisture transfer by diffusion, to surfaces within the assembly that would be cold enough to cause condensation at the design temperature and humidity conditions, or

b)   reduce moisture transfer by diffusion, to surfaces within the assembly that would be cold enough to cause condensation at the design temperature and humidity conditions, to a rate that will not allow sufficient accumulation of moisture to cause deterioration or otherwise adversely affect any of

i)   the health or safety of building users,

ii)   the intended use of the building, or

iii)   the operation of building services.

(See Note A-5.5.1.2.(1).)

2)   Coatings applied to gypsum board to provide required resistance to vapour diffusion shall conform to the requirements of Sentence (1) when tested in accordance with CAN/CGSB-1.501-M, “Method for Permeance of Coated Wallboard.”

3)   Coatings applied to materials other than gypsum board to provide required resistance to vapour diffusion shall conform to the requirements of Sentence (1) when tested in accordance with ASTM E96/E96M, “Standard Test Methods for Water Vapor Transmission of Materials,” by the desiccant method (dry cup).

Section  5.6.   Precipitation

5.6.1. Protection from Precipitation

5.6.1.1. Required Protection from Precipitation

(See Note A-5.6.1.1.)

1)   Except as provided in Sentence (2), where a building component or assembly is exposed to precipitation, the component or assembly shall

a)   minimize ingress of precipitation into the component or assembly, and

b)   prevent ingress of precipitation into interior space.

2)   Protection from ingress of precipitation is not required where it can be shown that such ingress will not adversely affect any of

a)   the health or safety of building users,

b)   the intended use of the building, or

c)   the operation of building services.

5.6.1.2. Installation of Protective Materials

1)   Where protective materials are applied to assemblies to provide the required protection from precipitation, they shall be installed so as to shed precipitation or otherwise minimize its entry into the assembly and prevent its penetration through the assembly. (See Note A-5.6.1.2.(1).) (See also Clause 5.3.1.2.(1)(d).)

2)   Where protective materials applied to assemblies to provide the required protection from precipitation are part of a vegetated roofing system, they shall be resistant to root and rhizome penetration when tested in accordance with ANSI/GRHC/SPRI VR-1, “Procedure for Investigating Resistance to Root or Rhizome Penetration on Vegetative Roofs.” (See Note A-5.6.1.2.(2).)

5.6.2. Sealing, Drainage, Accumulation and Disposal

5.6.2.1. Sealing and Drainage

(See Note A-5.6.2.1.)

1)   Except as provided in Sentence (2), materials, components, assemblies, joints in materials, junctions between components and junctions between assemblies exposed to precipitation shall be

a)   sealed to prevent ingress of precipitation, or

b)   drained to direct precipitation to the exterior.

2)   Sealing or drainage are not required where it can be shown that the omission of sealing and drainage will not adversely affect any of

a)   the health or safety of building users,

b)   the intended use of the building, or

c)   the operation of building services.

5.6.2.2. Accumulation and Disposal

1)   Where water, snow or ice can accumulate on a building, provision shall be made to minimize the likelihood of hazardous conditions arising from such accumulation.

2)   Where precipitation can accumulate on sloped or horizontal assemblies, provision shall be made for drainage conforming with Article 2.4.10.4. of Division B of Book II (Plumbing Systems) of this Code.

3)   Where downspouts are provided and are not connected to a sewer, provisions shall be made to

a)   divert the water from the building, and

b)   prevent soil erosion.

4)   Junctions between vertical assemblies, and sloped or horizontal assemblies, shall be designed and constructed to minimize the flow of water from the sloped or horizontal assembly onto the vertical assembly.

Section  5.7.   Surface and Ground Water

(See Note A-5.7.)

5.7.1. Site Factors

5.7.1.1. Application

1)   This Subsection applies to the location of buildings, the grading of building sites, the directing of water away from building assemblies, and the provision of means for drainage.

5.7.1.2. Required Protection

1)   The building shall be located, the building site shall be graded, or water shall be directed away from building assemblies so as to prevent or accommodate the accumulation of surface water against the building or adjacent buildings.

2)   Drainage shall be provided to direct water away from assemblies separating interior space from the ground, except

a)   where the assembly is designed in accordance with Subsection 5.7.2. to withstand continuous hydrostatic pressure, or

b)   where it can be shown that the lack of drainage will not adversely affect

i)   the health or safety of building users,

ii)   the intended use of the building, or

iii)   the operation of building services.

(See Note A-5.7.1.2.(2).)

5.7.2. Protection against Hydrostatic Pressure

5.7.2.1. Application

1)   This Subsection applies to waterproofing materials, components, assemblies and systems applied to building assemblies that separate dissimilar environments and are subjected to hydrostatic pressure.

5.7.2.2. Design of Building Elements Under Hydrostatic Loads

1)   Waterproofing materials, components, assemblies and systems described in Article 5.7.2.1. shall be designed in accordance with Subsection 5.1.4.

2)   Hydrostatic design loads shall be determined in accordance with Subsection 5.2.2.

5.7.2.3. Required Protection

1)   Waterproofing materials, components, assemblies and systems described in Article 5.7.2.1. shall comply with Article 5.7.3.2.

5.7.3. Protection against Ground Water

5.7.3.1. Application

1)   This Subsection applies to the protection of building assemblies that separate interior space from the ground.

5.7.3.2. Required Protection

1)   Except as provided in Sentence (2) and Article 5.7.3.4., building assemblies described in Article 5.7.3.1. shall be protected by waterproofing in accordance with Article 5.7.3.3. so as to prevent the ingress of water into the building or the accumulation of water against the building.

2)   Waterproofing is not required where it can be shown that

a)   a building is designed to accommodate the ingress or accumulation of water, or

b)   the ingress or accumulation of water will not negatively affect

i)   the health or safety of building users,

ii)   the intended use of the building, or

iii)   the operation of building services.

5.7.3.3. Waterproofing

1)   Waterproofing materials, components, assemblies, or systems installed to provide the required protection shall form a continuous and impervious barrier to the ingress of water and be capable of accommodating

a)   imperfections, construction joints, control joints and expansion joints (see Note A-5.7.3.3.(1)(a)),

b)   junctions between different building assemblies, and

c)   elements penetrating building assemblies.

5.7.3.4. Where Dampproofing is Permitted

1)   Vertical building assemblies that separate interior space from the ground are permitted to be dampproofed where

a)   such assemblies are not subjected to hydrostatic pressure,

b)   the substrate is cast-in-place concrete, and

c)   a drainage layer is installed between the building assembly and the soil.

(See Note A-5.7.3.4.(1).)

2)   Joints, junctions and penetrations shall be designed and constructed to maintain the continuity of the dampproofing.

Section  5.8.   Sound Transmission

(See Note A-5.8.)

5.8.1. Protection from Airborne Noise

5.8.1.1. Required Protection

1)   Except as provided in Sentence (2), a dwelling unit shall be separated from every other space in a building in which noise may be generated by

a)   a separating assembly and adjoining constructions, which, together, provide an apparent sound transmission class (ASTC) rating not less than 47, or

b)   a separating assembly that provides a sound transmission class (STC) rating of not less than 50 and adjoining constructions that conform to Article 9.11.1.4.

2)   Construction separating a dwelling unit from an elevator shaft or a refuse chute shall have an STC rating not less than 55.

5.8.1.2. Determination of Sound Transmission Ratings

(See Note A-5.8.1.2.)

1)   The STC ratings of separating assemblies shall be determined in accordance with ASTM E413, “Classification for Rating Sound Insulation,” using the results from measurements carried out in accordance with ASTM E90, “Standard Test Method for Laboratory Measurement of Airborne Sound Transmission Loss of Building Partitions and Elements.”

2)   The ASTC ratings of separating assemblies and adjoining constructions shall be

a)   determined in accordance with ASTM E413, “Classification for Rating Sound Insulation,” using the results from measurements carried out in accordance with ASTM E336, “Standard Test Method for Measurement of Airborne Sound Attenuation between Rooms in Buildings,” or

b)   calculated in accordance with

i)   the detailed method described in Article 5.8.1.4., or

ii)   the simplified method described in Article 5.8.1.5.

5.8.1.3. Compliance with Required Ratings

1)   Compliance with the required STC ratings shall be demonstrated through

a)   measurements carried out in accordance with Sentence 5.8.1.2.(1), or

b)   the construction of separating assemblies conforming to those presented in Table 9.10.3.1.-A or 9.10.3.1.-B, as applicable.

2)   Compliance with the required ASTC ratings shall be demonstrated through

a)   measurements or calculations carried out in accordance with Sentence 5.8.1.2.(2), or

b)   the construction of separating assemblies conforming to those presented in Table 9.10.3.1.-A or 9.10.3.1.-B, as applicable, that have an STC rating of not less than 50 in conjunction with flanking assemblies constructed in accordance with Article 9.11.1.4.

5.8.1.4. Detailed Method for Calculating ASTC

(See Note A-5.8.1.4.)

1)   The sound transmission loss measured in accordance with ASTM E90, “Standard Test Method for Laboratory Measurement of Airborne Sound Transmission Loss of Building Partitions and Elements,” shall be used in lieu of the sound reduction index required in ISO 15712-1, “Building Acoustics - Estimation of Acoustic Performance of Buildings From the Performance of Elements - Part 1: Airborne Sound Insulation Between Rooms.”

2)   The vibration reduction index for the junctions between separating assemblies shall be

a)   determined using the equations presented in Annex E of ISO 15712-1, “Building Acoustics - Estimation of Acoustic Performance of Buildings From the Performance of Elements - Part 1: Airborne Sound Insulation Between Rooms,” or

b)   measured in accordance with Parts 1 to 4 of ISO 10848-1, “Acoustics – Laboratory measurement of the flanking transmission of airborne and impact sound between adjoining rooms – Part 1: Frame document.”

3)   The normalized flanking level difference shall be measured in accordance with Parts 1 to 4 of ISO 10848-1, “Acoustics – Laboratory measurement of the flanking transmission of airborne and impact sound between adjoining rooms – Part 1: Frame document.”

4)   The direct sound reduction index for the separating assembly in situ shall be determined using Clause (a) or (b), depending on the type of construction:

a)   for a separating wall or floor assembly with lightweight wood or steel framing, the index shall be taken as equal to the sound transmission loss, without correction;

b)   for a separating wall or floor assembly that behaves like a homogeneous panel, the index shall be determined in accordance with the detailed method for structure-borne transmission presented in ISO 15712-1, “Building Acoustics - Estimation of Acoustic Performance of Buildings From the Performance of Elements - Part 1: Airborne Sound Insulation Between Rooms” (see Note A-5.8.1.4.(4)(b)).

5)   The flanking sound reduction index for each flanking path at each edge of the separating assembly shall be determined using Clause (a), (b) or (c), depending on the type of construction:

a)   for a separating wall or floor assembly with lightweight wood or steel framing and connected flanking assemblies with lightweight wood or steel framing, the index shall be taken as equal to the normalized flanking level difference re-normalized for the ASTC field situation in accordance with Annex F of ISO 15712-1, “Building Acoustics - Estimation of Acoustic Performance of Buildings From the Performance of Elements - Part 1: Airborne Sound Insulation Between Rooms,”

b)   for a separating wall or floor assembly that behaves like a homogeneous panel and connected flanking assemblies that behave like a homogeneous panel, the index shall be determined in accordance with the detailed method for structure-borne transmission presented in ISO 15712-1, “Building Acoustics - Estimation of Acoustic Performance of Buildings From the Performance of Elements - Part 1: Airborne Sound Insulation Between Rooms” (see Note A-5.8.1.4.(4)(b)),

c)   for a mixture of assemblies with lightweight wood or steel framing and assemblies that behave like a homogeneous panel, the index shall be determined in accordance with Clause (a) or (b) (see Note A-5.8.1.4.(4)(b)).

6)   Once the pertinent indices and measurements referred to in Sentences (1) to (5) have been determined based on the type of construction, the apparent sound reduction index shall then be determined in accordance with ISO 15712-1, “Building Acoustics - Estimation of Acoustic Performance of Buildings From the Performance of Elements - Part 1: Airborne Sound Insulation Between Rooms.”

7)   The ASTC shall be calculated in accordance with ASTM E413, “Classification for Rating Sound Insulation,” using the apparent sound reduction index determined in Sentence (6), which shall be treated as equivalent to the values of apparent sound transmission loss measured in accordance with ASTM E336, “Standard Test Method for Measurement of Airborne Sound Attenuation between Rooms in Buildings.”

5.8.1.5. Simplified Method for Calculating ASTC

(See Note A-5.8.1.4.)

1)   The STC rating shall be used in lieu of the weighted sound reduction index required in ISO 15712-1, “Building Acoustics - Estimation of Acoustic Performance of Buildings From the Performance of Elements - Part 1: Airborne Sound Insulation Between Rooms.”

2)   The vibration reduction index for the junctions between separating assemblies shall be

a)   determined using the equations presented in Annex E of ISO 15712-1, “Building Acoustics - Estimation of Acoustic Performance of Buildings From the Performance of Elements - Part 1: Airborne Sound Insulation Between Rooms,” or

b)   measured in accordance with Parts 1 to 4 of ISO 10848-1, “Acoustics – Laboratory measurement of the flanking transmission of airborne and impact sound between adjoining rooms – Part 1: Frame document.”

3)   The weighted normalized flanking level difference shall be determined in accordance with ASTM E413, “Classification for Rating Sound Insulation,” using the results from measurements carried out in accordance with Parts 1 to 4 of ISO 10848-1, “Acoustics – Laboratory measurement of the flanking transmission of airborne and impact sound between adjoining rooms – Part 1: Frame document.”

4)   The direct weighted sound reduction index for the separating assembly shall be taken as equal to the STC, without correction.

5)   The weighted flanking sound reduction index for each flanking path at each edge of the separating assembly shall be determined using Clause (a) or (b), depending on the type of construction:

a)   for a separating wall or floor assembly with lightweight wood or steel framing and connected flanking assemblies with lightweight wood or steel framing, the index shall be taken as equal to the weighted normalized flanking level difference re-normalized for the ASTC field situation in accordance with Annex F of ISO 15712-1, “Building Acoustics - Estimation of Acoustic Performance of Buildings From the Performance of Elements - Part 1: Airborne Sound Insulation Between Rooms” ;

b)   for a separating wall or floor assembly that behaves like a homogeneous panel and connected flanking assemblies that behave like a homogeneous panel, the index shall be determined in accordance with the simplified method for structure-borne transmission presented in ISO 15712-1, “Building Acoustics - Estimation of Acoustic Performance of Buildings From the Performance of Elements - Part 1: Airborne Sound Insulation Between Rooms” (see Note A-5.8.1.4.(4)(b)).

6)   Once the pertinent indices and measurements referred to in Sentences (1) to (5) have been determined based on the type of construction, the ASTC shall then be calculated in accordance with ISO 15712-1, “Building Acoustics - Estimation of Acoustic Performance of Buildings From the Performance of Elements - Part 1: Airborne Sound Insulation Between Rooms.”

Section  5.9.   Standards

5.9.1. Applicable Standards

5.9.1.1. Compliance with Applicable Standards

1)   Except as provided in Sentence (2) and elsewhere in this Part, materials and components, and their installation, shall conform to the requirements of the applicable standards in Table 5.9.1.1. where those materials or components are

a)   incorporated into environmental separators or assemblies exposed to the exterior, and

b)   installed to fulfill the requirements of this Part.

(See Note A-5.9.1.1.(1).)

2)   The requirements for flame-spread ratings contained in thermal insulation standards shall be applied only as required in Part 3.

Table 5.9.1.1.

Standards Applicable to Environmental Separators and Assemblies Exposed to the Exterior

Forming Part of Sentence 5.9.1.1.(1)

| Issuing Agency | Document Number | Title of Document |
| --- | --- | --- |
| ANSI | A135.6 | Engineered Wood Siding |
| ASME | B18.6.1 | Wood Screws (Inch Series) |
| ASTM | A123/A123M | Standard Specification for Zinc (Hot-Dip Galvanized) Coatings on Iron and Steel Products |
| ASTM | A153/A153M | Standard Specification for Zinc Coating (Hot-Dip) on Iron and Steel Hardware |
| ASTM | A653/A653M | Standard Specification for Steel Sheet, Zinc-Coated (Galvanized) or Zinc-Iron Alloy-Coated (Galvannealed) by the Hot-Dip Process |
| ASTM | C4 | Standard Specification for Clay Drain Tile and Perforated Clay Drain Tile |
| ASTM | C73 | Standard Specification for Calcium Silicate Brick (Sand-Lime Brick) |
| ASTM | C126 | Ceramic Glazed Structural Clay Facing Tile, Facing Brick, and Solid Masonry Units |
| ASTM | C212 | Standard Specification for Structural Clay Facing Tile |
| ASTM | C412M | Standard Specification for Concrete Drain Tile |
| ASTM | C444M | Standard Specification for Perforated Concrete Pipe |
| ASTM | C553 | Standard Specification for Mineral Fiber Blanket Thermal Insulation for Commercial and Industrial Applications |
| ASTM | C612 | Standard Specification for Mineral Fiber Block and Board Thermal Insulation |
| ASTM | C700 | Standard Specification for Vitrified Clay Pipe, Extra Strength, Standard Strength, and Perforated |
| ASTM | C726 | Standard Specification for Mineral Wool Roof Insulation Board |
| ASTM | C834(1) | Standard Specification for Latex Sealants |
| ASTM | C840 | Standard Specification for Application and Finishing of Gypsum Board |
| ASTM | C920(1) | Standard Specification for Elastomeric Joint Sealants |
| ASTM | C991 | Standard Specification for Flexible Fibrous Glass Insulation for Metal Buildings |
| ASTM | C1002 | Standard Specification for Steel Self-Piercing Tapping Screws for the Application of Gypsum Panel Products or Metal Plaster Bases to Wood Studs or Steel Studs |
| ASTM | C1177/C1177M | Standard Specification for Glass Mat Gypsum Substrate for Use as Sheathing |
| ASTM | C1178/C1178M | Standard Specification for Coated Glass Mat Water-Resistant Gypsum Backing Panel |
| ASTM | C1184(1) | Standard Specification for Structural Silicone Sealants |
| ASTM | C1280 | Standard Specification for Application of Exterior Gypsum Panel Products for Use as Sheathing |
| ASTM | C1311(1) | Standard Specification for Solvent Release Sealants |
| ASTM | C1330(1) | Standard Specification for Cylindrical Sealant Backing for Use with Cold Liquid-Applied Sealants |
| ASTM | C1396/C1396M(2) | Standard Specification for Gypsum Board |
| ASTM | C1658/C1658M(3) | Standard Specification for Glass Mat Gypsum Panels |
| ASTM | D1227/D1227M | Standard Specification for Emulsified Asphalt Used as a Protective Coating for Roofing |
| ASTM | D2178/D2178M | Standard Specification for Asphalt Glass Felt Used in Roofing and Waterproofing |
| ASTM | D3019/D3019M(4) | Standard Specification for Lap Cement Used with Asphalt Roll Roofing, Non-Fibered, and Fibered |
| ASTM | D4479/D4479M | Standard Specification for Asphalt Roof Coatings – Asbestos-Free |
| ASTM | D4637/D4637M | Standard Specification for EPDM Sheet Used In Single-Ply Roof Membrane |
| ASTM | D4811/D4811M | Standard Specification for Nonvulcanized (Uncured) Rubber Sheet Used as Roof Flashing |
| ASTM | D6878/D6878M | Standard Specification for Thermoplastic Polyolefin Based Sheet Roofing |
| ASTM | E2190 | Standard Specification for Insulating Glass Unit Performance and Evaluation |
| BNQ | BNQ 3624-115 | Polyethylene (PE) Pipe and Fittings for Soil and Foundation Drainage |
| CGSB | CAN/CGSB-11.3-M | Hardboard |
| CGSB | CAN/CGSB-12.1 | Safety Glazing |
| CGSB | CAN/CGSB-12.2-M | Flat, Clear Sheet Glass |
| CGSB | CAN/CGSB-12.3-M | Flat, Clear Float Glass |
| CGSB | CAN/CGSB-12.4-M | Heat Absorbing Glass |
| CGSB | CAN/CGSB-12.8 | Insulating glass units |
| CGSB | CAN/CGSB-12.9 | Spandrel glass |
| CGSB | 37-GP-9Ma | Primer, Asphalt, Unfilled, for Asphalt Roofing, Dampproofing and Waterproofing |
| CGSB | CAN/CGSB-37.50-M | Hot-Applied, Rubberized Asphalt for Roofing and Waterproofing |
| CGSB | CAN/CGSB-37.54 | Polyvinyl Chloride Roofing and Waterproofing Membrane |
| CGSB | CAN/CGSB-37.58-M | Membrane, Elastomeric, Cold-Applied Liquid, for Non-Exposed Use in Roofing and Waterproofing |
| CGSB | CAN/CGSB-41.24 | Rigid Vinyl Siding, Soffits and Fascia |
| CGSB | CAN/CGSB-51.32-M | Sheathing, Membrane, Breather Type |
| CGSB | CAN/CGSB-51.33-M | Vapour Barrier Sheet, Excluding Polyethylene, for Use in Building Construction |
| CGSB | CAN/CGSB-51.34-M | Vapour Barrier, Polyethylene Sheet for Use in Building Construction |
| CGSB | CAN/CGSB-93.1-M | Sheet, Aluminum Alloy, Prefinished, Residential |
| CGSB | CAN/CGSB-93.2-M | Prefinished Aluminum Siding, Soffits, and Fascia, for Residential Use |
| CSA | A23.1 | Concrete materials and methods of concrete construction |
| CSA | CAN/CSA-A82 | Fired masonry brick made from clay or shale |
| CSA | CAN3-A93-M | Natural Airflow Ventilators for Buildings |
| CSA | CAN/CSA-A123.2 | Asphalt-Coated Roofing Sheets |
| CSA | A123.3 | Asphalt Saturated Organic Roofing Felt |
| CSA | CAN/CSA-A123.4 | Asphalt for Constructing Built-Up Roof Coverings and Waterproofing Systems |
| CSA | A123.5 | Asphalt shingles made from glass felt and surfaced with mineral granules |
| CSA | CAN/CSA-A123.16 | Asphalt-coated glass-base sheets |
| CSA | A123.17 | Asphalt Glass Felt Used in Roofing and Waterproofing |
| CSA | A123.23 | Product specification for polymer-modified bitumen sheet, prefabricated and reinforced |
| CSA | A123.51 | Asphalt shingle application on roof slopes 1:6 and steeper |
| CSA | A165.1 | Concrete block masonry units |
| CSA | A165.2 | Concrete brick masonry units |
| CSA | A165.3 | Prefaced concrete masonry units |
| CSA | CAN/CSA-A179 | Mortar and Grout for Unit Masonry |
| CSA | CAN/CSA-A220 Series | Concrete Roof Tiles |
| CSA | CAN/CSA-A371 | Masonry Construction for Buildings |
| CSA | A3001 | Cementitious Materials for Use in Concrete |
| CSA | B182.1 | Plastic drain and sewer pipe and pipe fittings |
| CSA | G40.21 | Structural quality steel |
| CSA | CAN/CSA-G401 | Corrugated steel pipe products |
| CSA | CAN/CSA-O80 Series | Wood preservation |
| CSA | O118.1 | Western Red Cedar Shakes and Shingles |
| CSA | O118.2 | Eastern White Cedar Shingles |
| CSA | O121 | Douglas fir plywood |
| CSA | O141 | Softwood Lumber |
| CSA | O151 | Canadian softwood plywood |
| CSA | O153 | Poplar plywood |
| CSA | O325 | Construction sheathing |
| CSA | O437.0 | OSB and Waferboard |
| HPVA | ANSI/HPVA HP-1 | American National Standard for Hardwood and Decorative Plywood |
| ULC | CAN/ULC-S701.1 | Standard for Thermal Insulation, Polystyrene Boards |
| ULC | CAN/ULC-S702.1 | Standard for Mineral Fibre Thermal Insulation for Buildings, Part 1: Material Specification |
| ULC | CAN/ULC-S703 | Standard for Cellulose Fibre Insulation (CFI) for Buildings |
| ULC | CAN/ULC-S704.1 | Standard for Thermal Insulation, Polyurethane and Polyisocyanurate, Boards, Faced |
| ULC | CAN/ULC-S705.1 | Standard for Thermal Insulation – Spray Applied Rigid Polyurethane Foam, Medium Density – Material Specification |
| ULC | CAN/ULC-S705.2 | Standard for Thermal Insulation – Spray Applied Rigid Polyurethane Foam, Medium Density – Application |
| ULC | CAN/ULC-S706.1 | Standard for Wood Fibre Insulating Boards for Buildings |
| ULC | CAN/ULC-S710.1 | Standard for Bead-Applied One Component Polyurethane Air Sealant Foam, Part 1: Material Specification |
| ULC | CAN/ULC-S711.1 | Standard for Bead-Applied Two Component Polyurethane Air Sealant Foam, Part 1: Material Specification |
| ULC | CAN/ULC-S717.1 | Standard for Flat Wall Insulating Concrete Form (ICF) Units – Material Properties |

Notes to Table 5.9.1.1.:

(1) See Note A-Table 5.9.1.1.

(2) The flame-spread rating of gypsum board shall be determined in accordance with CAN/ULC-S102 in lieu of ASTM E84 as indicated in ASTM C1396/C1396M.

(3) The flame-spread rating of gypsum panels shall be determined in accordance with CAN/ULC-S102 in lieu of ASTM E84 as indicated in ASTM C1658/C1658M.

(4) For the purpose of compliance with Part 5, ASTM D3019/D3019M shall only apply to the non-fibered and non-asbestos-fibered types of asphalt roll roofing.

5.9.2. Windows, Doors and Skylights

5.9.2.1. General

1)   This Subsection applies to windows, doors and skylights, including their components, that separate

a)   interior space from exterior space, or

b)   environmentally dissimilar interior spaces.

2)   For the purpose of this Subsection, the term “skylight” refers to unit skylights, roof windows and tubular daylighting devices.

3)   Windows, doors and skylights, including their components, that are required to have a fire-protection rating need not conform to the requirements of this Subsection. (See Note A-5.9.2.1.(3).)

5.9.2.2. Applicable Standards

(See Note A-5.9.2.2.)

1)   Except as permitted in Sentences (5) and 5.9.2.3.(1), windows, doors, skylights, including their components, shall conform to the requirements in

a)   AAMA/WDMA/CSA 101/I.S.2/A440, “North American Fenestration Standard/Specification for windows, doors, and skylights” (Harmonized Standard), and

b)   except as permitted in Sentence (4), CSA A440S1, “Canadian Supplement to AAMA/WDMA/CSA 101/I.S.2/A440-, North American Fenestration Standard/Specification for windows, doors, and skylights.”

2)   Performance grades for windows, doors and skylights shall be selected according to the Canadian Supplement referenced in Clause (1)(b) so as to be appropriate for the conditions and geographic location in which the window, door or skylight will be installed.

3)   Windows, doors and skylights shall conform to the performance grades selected in Sentence (2) when tested in accordance with the Harmonized Standard referenced in Clause (1)(a).

4)   For the purposes of conformance with Clause (1)(b), loads and procedures from Section 5.2 may be used instead of the loads and procedures set out in the standard. (See Note 5.9.2.2.(4).)

5)   A door designated as a “Limited Water” door in accordance with the standard referenced in Clause (1)(a) shall not be used unless the door

a)   separates a dwelling unit from an unconditioned storage garage or a carport,

b)   is designed with a clear width, a clear and level space, a door-opening device and a door closer in conformance with Subsection 3.8.3. (see Article 3.8.3.6.), or

c)   meets the criteria in Sentence 9.27.3.8.(3) such that flashing would not be required.

5.9.2.3. Structural and Environmental Loads, Air Leakage and Water Penetration

1)   Windows, doors, skylights and their components that do not conform to Article 5.9.2.2. shall be designed and constructed in accordance with Subsection 5.1.4., Section 5.4. and Section 5.6.

(See Note A-5.9.2.3.(1).)

5.9.2.4. Heat Transfer

1)   Windows, doors and skylights shall meet the heat transfer performance requirements stated in Section 5.3. (See Note A-5.3.1.2.)

2)   Except as provided in Sentence (3), all metal-framed glazed assemblies separating interior conditioned space from interior unconditioned space or exterior space shall incorporate a thermal break to minimize condensation.

3)   Metal-framed glazed assemblies need not comply with Sentence (2) where these assemblies are

a)   storm windows or doors, or

b)   windows or doors that are required to have a fire-protection rating.

(See Note A-5.9.2.4.(3).)

5.9.3. Other Fenestration Assemblies

(See Note A-5.9.3.)

5.9.3.1. General

1)   For the purpose of this Subsection, the term “other fenestration assemblies” refers to curtain walls, window walls, storefronts and glazed architectural structures. (See Note A-5.9.3.1.(1).)

2) Other fenestration assemblies and their components that are required to have a fire-protection rating need not conform to the requirements of this Subsection. (See Note A-5.9.2.1.(3).)

5.9.3.2. Structural and Environmental Loads

1)   Other fenestration assemblies and their components shall be designed and constructed in accordance with Subsection  5.1.4. (See Note A-5.9.3.2.(1).)

5.9.3.3. Heat Transfer

1)   Other fenestration assemblies and their components shall meet the heat transfer performance requirements stated in Section 5.3. (See Note A-5.9.3.3.(1).)

2)   Other fenestration assemblies using metal framing that separate interior conditioned space from interior unconditioned space or exterior space shall incorporate a thermal break to minimize condensation.

5.9.3.4. Air Leakage

1)   Other fenestration assemblies and their components shall be designed and constructed in accordance with Section 5.4.

2)   Except as provided in Sentence (3), other fenestration assemblies and their components shall have an air leakage characteristic, measured at an air pressure difference of 75 Pa, when tested in accordance with ASTM E283, “Standard Test Method for Determining Rate of Air Leakage Through Exterior Windows, Curtain Walls, and Doors Under Specified Pressure Differences Across the Specimen,” that is not greater than

a)   0.2 L/(s×m2) for fixed portions, including any opaque portions, and

b)   1.5 L/(s×m2) for operable portions.

(See Note A-5.9.3.4.(2).)

3)   The following systems need not comply with Sentence (2):

a)   interior windows and interior doors that do not serve as environmental separators,

b)   vehicular access doors (garage doors),

c)   storm windows and storm doors,

d)   commercial entrance systems,

e)   revolving doors,

f)   smoke and relief air vents,

g)   site-built door systems, and

h)   commercial steel doors.

(See Note A-5.9.3.4.(3).)

5.9.3.5. Water Penetration

1)   Other fenestration assemblies and their components shall be designed and constructed in accordance with Section 5.6.

5.9.4. Exterior Insulation Finish Systems

5.9.4.1. Structural Loads, Heat Transfer, Air Leakage, Vapour Diffusion and Water Penetration

1)   Exterior insulation finish systems and their components shall comply with

a)    Subsection 5.1.4. and Sections 5.3. to 5.6., and

b)   CAN/ULC-S716.1, “Standard for Exterior Insulation and Finish Systems (EIFS) - Materials and Systems,” where covered in the scope of that standard.

(See Note A-5.9.4.1.(1).)

Section  5.10.   Objectives and Functional Statements

5.10.1. Objectives and Functional Statements

5.10.1.1. Attributions to Acceptable Solutions

1)   For the purpose of compliance with this Code as required in Clause 1.2.1.1.(1)(b) of Division A, the objectives and functional statements attributed to the acceptable solutions in this Part shall be the objectives and functional statements listed in Table 5.10.1.1. (See Note A-1.1.2.1.(1).)

Table 5.10.1.1.

Objectives and Functional Statements Attributed to the Acceptable Solutions in Part 5

Forming Part of Sentence 5.10.1.1.(1)

| Provision | Functional Statements and Objectives(1) |
| --- | --- |
| 5.1.4.1. Structural and Environmental Loads |  |
| (1) | (a) [F55,F61,F63-OH1.1,OH1.2,OH1.3] |
|  | [F20-OS3.1] Applies to snow fences and sloped glazing. |
|  | [F61-OH4] |
|  | (a) [F60,F61,F63-OS2.2,OS2.3] |
|  | (a) [F20,F51,F55-OS1.4] Applies where required life safety systems are incorporated in environmental separators. |
|  | (b) [F20-OS2.1] [F21,F22-OS2.3,OS2.4] |
|  | (b) [F20,F21,F22-OH1.1,OH1.2,OH1.3] |
|  | (b) [F20-OH4] |
| (4) | [F20-OS2.1] [F21,F22-OS2.3,OS2.4] |
|  | [F20,F21,F22-OH1.1,OH1.2,OH1.3] |
| (5) | (a) [F20-OS2.1] [F21,F22-OS2.3,OS2.4] |
|  | (a) [F20,F21,F22-OH1.1,OH1.2,OH1.3] |
|  | (b) [F20-OS2.1] [F21,F22-OS2.3,OS2.4] |
|  | (b) [F20,F21,F22-OH1.1,OH1.2,OH1.3] |
| (6) | [F20,F21,F22-OH1.1,OH1.2,OH1.3] |
|  | (a) [F20-OS2.1,OS2.3] (b),(c) [F21,F22-OS2.3] |
|  | (b),(c) [F22-OH4] |
| 5.1.4.2. Resistance to Deterioration |  |
| (1) | [F80,F81-OH1.1,OH1.2,OH1.3] |
|  | [F80,F81-OS3.1] Applies to floor assemblies. |
|  | [F80,F81-OH4] Applies to floor assemblies. |
|  | [F80,F81-OS2.3] |
|  | [F80,F81-OS1.4] Applies where required life safety systems are incorporated in environmental separators. |
| 5.2.1.1. Exterior Environmental Loads |  |
| (2) | [F40,F20-OH1.1] [F20-OH1.2,OH1.3] |
|  | [F20-OS2.1] |
| 5.2.1.2. Interior Environmental Loads |  |
| (1) | [F51,F55,F61,F63-OH1.1,OH1.2] |
|  | [F55,F61,F63-OS2.3] |
|  | [F51,F61,F63,F55-OS1.4] Applies where required life safety systems are incorporated in environmental separators. |
| 5.2.1.3. Environmental Load and Transfer Calculations |  |
| (1) | [F56-OH3.1] Applies to sound transmission calculations. |
|  | [F61,F51,F63,F55-OH1.1,OH1.2] [F51,F61-OH1.3] Applies to heat, air and moisture transfer calculations. |
|  | [F61,F51,F63-OS2.3] Applies to heat, air and moisture transfer calculations. |
| (3) | [F61,F63,F55-OH1.1,OH1.2] [F61,F55-OH1.3] |
|  | [F20-OS1.4] Applies where required life safety systems are incorporated in environmental separators. |
|  | [F20-OS2.1] |
| 5.2.2.1. Determination of Structural Loads and Effects |  |
| (1) | [F20-OS2.1] [F21,F22-OS2.3,OS2.4] |
|  | [F20,F21,F22-OH1.1,OH1.2,OH1.3] |
|  | [F20,F21,F22-OH4] |
| (3) | [F20-OS2.1] [F21,F22-OS2.3,OS2.4] |
|  | [F20,F21,F22-OH1.1,OH1.2,OH1.3] |
|  | [F20,F21,F22-OH4] |
| 5.2.2.2. Determination of Wind Load |  |
| (2) | [F20-OS2.1] [F22-OS2.3,OS2.4] |
|  | [F20,F22-OH1.1,OH1.2,OH1.3] |
|  | [F20,F22-OH4] |
| (3) | [F20-OS2.1] [F22-OS2.3,OS2.4] |
|  | [F20,F22-OH1.1,OH1.2,OH1.3] |
|  | [F20,F22-OH4] |
| (4) | [F20,F55,F61-OH1.1,OH1.2,OH1.3] |
|  | [F20,F55,F61-OS2.1,OS2.3] |
| 5.2.2.3. Design Procedures |  |
| (1) | [F20-OS2.1] [F22-OS2.3,OS2.4] |
|  | [F20,F22-OH1.1,OH1.2,OH1.3] |
|  | [F20,F22-OH4] |
| 5.3.1.1. Required Resistance to Heat Transfer |  |
| (1) | [F63-OH1.1] [F51,F63-OH1.2] |
|  | [F63-OS2.3] |
|  | [F51,F63-OS1.4] Applies where required life safety systems are incorporated in environmental separators. |
| 5.3.1.2. Properties to Resist Heat Transfer or Dissipate Heat |  |
| (1) | (a),(b) [F51,F63-OH1.1] (c) [F51-OH1.2] |
|  | (b),(d) [F51,F63-OS2.3] |
|  | (b) [F51,F63-OS1.4] Applies where required life safety systems are incorporated in environmental separators. |
|  | (d) [F30-OS3.1] |
| 5.3.1.3. Location and Installation of Materials Providing Thermal Resistance |  |
| (1) | [F51,F63-OH1.1] |
|  | [F63-OS2.3] |
| (2) | [F51,F63-OH1.1,OH1.2] |
|  | [F63-OS2.3] |
|  | [F51,F63-OS1.4] Applies where required life safety systems are incorporated in environmental separators. |
| 5.4.1.1. Required Resistance to Air Leakage |  |
| (1) | (a),(b),(f) [F51,F52,F54,F55-OH1.2] (a),(b),(c),(e) [F40,F55-OH1.1] (c) [F55,F61,F63-OH1.3] |
|  | (c),(d) [F61,F62,F63,F55-OS2.3] |
|  | (d) [F55,F62-OS3.1] |
|  | (f) [F55,F62-OS1.4] Applies where required life safety systems are incorporated in environmental separators. |
| (2) | [F40-OH1.1] [F52,F54-OH1.2] [F51,F55,F61,F63-OH1.1,OH1.2,OH1.3] |
|  | [F61,F63-OS2.3] |
|  | [F51,F55-OS1.4] Applies where required life safety systems are incorporated in environmental separators. |
| (3) | [F55-OH1.1,OH1.2,OH1.3] |
|  | [F55-OS2.3] |
|  | [F55-OS1.4] Applies where required life safety systems are incorporated in environmental separators. |
| (4) | [F61,F51,F63,F55-OH1.1,OH1.2] [F55,F61-OH1.3] |
|  | [F61,F63-OS2.3] |
|  | [F61,F51,F63-OS1.4] Applies where required life safety systems are incorporated in environmental separators. |
| 5.4.1.2. Air Barrier Assemblies |  |
| (1) | [F55-OH1.1,OH1.2,OH1.3] |
|  | [F55-OS2.3] |
|  | [F55-OS1.4] Applies where required life safety systems are incorporated in environmental separators. |
| (2) | [F55-OH1.1,OH1.2,OH1.3] |
|  | [F55-OS2.3] |
|  | [F55-OS1.4] Applies where required life safety systems are incorporated in environmental separators. |
| (4) | [F55-OH1.1] |
| 5.5.1.1. Required Resistance to Vapour Diffusion |  |
| (1) | [F63-OH1.1,OH1.2] |
|  | [F63-OS2.3] |
| (2) | [F63-OH1.1,OH1.2] |
|  | [F63-OS2.3] |
| 5.5.1.2. Vapour Barrier Properties and Installation |  |
| (1) | [F63-OH1.1,OH1.2] |
|  | [F63-OS2.3] |
| (2) | [F63-OH1.1,OH1.2] |
|  | [F63-OS2.3] |
| (3) | [F63-OH1.1,OH1.2] |
|  | [F63-OS2.3] |
| 5.6.1.1. Required Protection from Precipitation |  |
| (1) | [F61-OH1.1,OH1.2,OH1.3] |
|  | [F61-OS2.3] |
| 5.6.1.2. Installation of Protective Materials |  |
| (1) | [F61-OH1.1,OH1.2,OH1.3] |
|  | [F61-OS2.3] |
| (2) | [F61-OH1.1,OH1.2,OH1.3] |
|  | [F61-OS2.3] |
| 5.6.2.1. Sealing and Drainage |  |
| (1) | [F61,F62-OH1.1,OH1.2,OH1.3] |
|  | [F61,F62-OS2.3] |
| 5.6.2.2. Accumulation and Disposal |  |
| (1) | [F30-OS3.1] |
| (2) | [F61-OH1.1,OH1.2,OH1.3] |
|  | [F61-OS2.3] |
| (3) | [F61-OH1.1,OH1.2,OH1.3] |
|  | [F60-OS2.3] [F21-OS2.2] |
|  | (b) [F21-OP2.6] |
| (4) | [F61-OH1.1,OH1.2,OH1.3] |
|  | [F61-OS2.3] |
| 5.7.1.2. Required Protection |  |
| (1) | [F60-OH1.1,OH1.2,OH1.3] |
|  | [F60-OS2.3] |
| (2) | [F60-OH1.1,OH1.2,OH1.3] |
|  | [F60-OS2.2,OS2.3] |
| 5.7.3.2. Required Protection |  |
| (1) | [F61-OH1.1,OH1.2,OH1.3] |
|  | [F61-OS2.3] |
| 5.7.3.3. Waterproofing |  |
| (1) | [F61-OH1.1,OH1.2,OH1.3] |
|  | [F61-OS2.3] |
| 5.7.3.4. Where Dampproofing is Permitted |  |
| (1) | [F61-OH1.1,OH1.2,OH1.3] |
|  | [F61-OS2.3] |
| (2) | [F61-OH1.1,OH1.2,OH1.3] |
|  | [F61-OS2.3] |
| 5.8.1.1. Required Protection |  |
| (1) | [F56-OH3.1] |
| (2) | [F56-OH3.1] |
| 5.8.1.2. Determination of Sound Transmission Ratings |  |
| (1) | [F56-OH3.1] |
| (2) | [F56-OH3.1] |
| 5.8.1.4. Detailed Method for Calculating ASTC |  |
| (1) | [F56-OH3.1] |
| (2) | [F56-OH3.1] |
| (3) | [F56-OH3.1] |
| (4) | [F56-OH3.1] |
| (5) | [F56-OH3.1] |
| (6) | [F56-OH3.1] |
| (7) | [F56-OH3.1] |
| 5.8.1.5. Simplified Method for Calculating ASTC |  |
| (1) | [F56-OH3.1] |
| (2) | [F56-OH3.1] |
| (3) | [F56-OH3.1] |
| (4) | [F56-OH3.1] |
| (5) | [F56-OH3.1] |
| (6) | [F56-OH3.1] |
| 5.9.1.1. Compliance with Applicable Standards |  |
| (1) | [F20,F22,F51,F54,F55,F61,F63,F80-OH1.1,OH1.2] [F41,F55-OH1.1] [F55,F61,F80-OH1.3] |
|  | [F20,F80-OS2.1] [F20,F22,F51,F61,F63,F80-OS2.3] [F51-OS2.5] |
|  | [F20-OS2.2] [F80-OS2.3] |
|  | [F80,F61,F63-OS3.1] |
|  | [F80,F61,F63-OH4] Applies to floor assemblies. |
|  | (a) [F61,F63-OS1.4] Applies where required life safety systems are incorporated in environmental separators. |
|  | [F20,F80-OP2.1,OP2.3] [F22,F80-OP2.4] |
|  | [F42-OH2.5] |
| 5.9.2.2. Applicable Standards |  |
| (1) | [F20,F55,F61,F63-OH1.1,OH1.3] [F20,F55,F61,F63,F81-OH1.2] |
|  | [F20,F55,F61-OS2.3] |
|  | [F20,F55,F61-OP2.3] |
| 5.9.2.4. Heat Transfer |  |
| (2) | [F63-OH1.1,OH1.2] |
|  | [F63-OS2.3] |
| 5.9.3.3. Heat Transfer |  |
| (2) | [F63-OH1.1,OH1.2] |
|  | [F63-OS2.3] |
| 5.9.3.4. Air Leakage |  |
| (2) | [F55,F63-OH1.1,OH1.2,OH1.3] |
|  | [F55,F63-OS2.3] |
|  | [F55-OS1.4] Applies where required life safety systems are incorporated in environmental separators. |
| 5.9.4.1. Structural Loads, Heat Transfer, Air Leakage, Vapour Diffusion and Water Penetration |  |
| (1) | (b) [F61,F62-OH1.1,OH1.2,OH1.3] |
|  | (b) [F61,F62-OS2.3] |

Notes to Table 5.10.1.1.:

(1) See Parts 2 and 3 of Division A.

Notes to Part 5

Environmental Separation

A-5   Environmental Separation. The requirements provided in Part 5 pertain to the separation of environmentally dissimilar spaces. Most obvious is the need to separate indoor conditioned spaces from unconditioned spaces, the outdoors or the ground. There are also cases where separation is needed between interior spaces which are intended to provide different environments. (See also Notes A-5.1.1.1.(1) and A-5.1.2.1.(1).)

A-5.1.1.1.(1)   Scope. Part 5 provides explicit requirements related to the transfer of heat, air, moisture and sound in various forms. Control of the ingress of radon and other soil gases is addressed by the requirements related to air leakage.

A-5.1.2.1.(1)   Application. Subsection 1.3.3. of Division A specifies that Part 5 applies to all buildings except those within the scope of Part 2, Part 9 or the National Farm Building Code of Canada 1995. Because of their intended use, many buildings need only provide a limited degree of separation from the outdoor environment, the ground, or between interior spaces. The provisions in Part 5 are written to allow exemptions for these buildings.

Part 5 applies to building elements that separate dissimilar environments and to site conditions that may affect environmental loading on the building envelope.

The provisions address

•   the design and construction, or selection, of building components, such as windows and doors,

•   the design and construction of building assemblies, such as walls, floors and roofs,

•   the design and construction of the interfaces between the above-mentioned elements, and

•   the design or selection, and installation, of site materials, components and assemblies, such as backfill and drainage, and grading.

Part 5 applies not only to building elements that separate indoor space from outdoor space, but also to those elements that separate indoor space from the ground and that separate adjacent indoor spaces having significantly different environments.

Indoor spaces that require separation include interior conditioned spaces adjacent to indoor unconditioned spaces, and adjacent interior conditioned spaces that are intended to provide different environments. An extreme example of the last would be a wall that separates an indoor ice rink from a swimming pool.

Some building elements are exposed to exterior environmental loads but do not separate dissimilar environments. Solid guards on exterior walkways are one example. Such constructions are subject to the application of Part 5.

A-5.1.4.1.   Application of Structural Design to Other Building Elements. Part 4, as currently written, applies primarily to buildings as a whole and to structural members. Requirements defining structural loads and design to accommodate or resist those loads, however, apply not only to buildings as a whole and components that are traditionally recognized as structural members, but also apply to other elements of the building that are subject to structural loading. This is addressed to some extent in Part 4 by the requirements that pertain, for example, to wind loads on cladding. A range of structural loads and effects, as defined in Subsection 4.1.2., may be imposed on non-loadbearing elements such as backing walls, roofing, interior partitions and their connections. These must generally be addressed using the same load determination and structural design procedures as used for structural members.

Responsibility for the structural design of buildings as a whole and their structural members is commonly assigned to the engineer of record. The application of Part 4 reflects this, and as such, “non-structural” elements are not explicitly identified in the Part 4 provisions. Rather the application of Part 4 to these elements is specified in cross-references from other Parts of the Code, e.g. Part 5, which recognizes the fact that the structural design of these elements is often carried out by engineers other than the engineer of record.

Part 4 does not generally apply to the structural design of building services, such as heating, ventilating, air-conditioning, plumbing, electrical, electronic or fire safety systems, though these may be subject to structural loads. It does, however, apply to the design of the connections of building services to address earthquake loads (see Article 4.1.8.18.).

A-5.1.4.1.(2)   Materials, Components and Assemblies with Multiple Functions. Where materials, components or assemblies are used to fulfill multiple functions, the designer may have to take into account their function with regard to structural loads, heat transfer, air leakage, vapour diffusion, and protection from precipitation, surface and ground water, and sound transmission. Materials should be selected taking into account the environmental loads to which they will be subjected, their physical and chemical characteristics, and their installation. Design and construction details should satisfy all intended functions and ensure continuity within and between assemblies, without adversely impacting adjacent materials, components or assemblies. The designer should also anticipate unintended consequences when materials that may fulfill multiple functions are used. For example, building membranes consisting of modified bitumen compounds, which are commonly used to control both water ingress and air leakage, also typically have low vapour transmission characteristics. Similarly, extruded polystyrene boards, which are used as thermal insulation, may also act as a component of an air barrier assembly, thus requiring wind loads to be considered.

An increasing number of manufactured systems are being used to serve more than one (and sometimes all) of the functions of an environmental separator: examples include pre-engineered building systems, exterior insulation finish systems, insulated metal panel systems, windows, other fenestration assemblies, and insulated precast concrete wall panels. These systems consist of combinations of pre-manufactured and/or site-built components, which are supposed to be assembled in a prescribed manner.

Ensuring compliance with one Section of Part 5 may impact compliance with other Sections of Part 5: for example, air barriers that are integral to some systems may also act as vapour barriers and impact condensation control. By extension, ensuring compliance with the requirements of Part 5 may impact compliance with other Parts of the code: for example, increasing the thickness of the insulation to improve an assembly's thermal performance may impact its compliance with Part 3 with regard to fire resistance.

Compliance with a standard listed in Section 5.9. does not ensure that a system is appropriate for the intended application. The designer should consider all relevant criteria, beyond the standard tests, when selecting an appropriate product for a project.

A-5.1.4.1.(5)   Past Performance as Basis for Compliance with Respect to Structural Loads. As discussed in Note A-5.1.4.1., a range of structural loads and effects can be imposed on materials, components and assemblies in environmental separators and assemblies exposed to the exterior. In many instances, compliance with Sentence 5.1.4.1.(1) for structural loads must be determined based on the loads and calculation methods described in Part 4 as specified in Sentence 5.1.4.1.(3) and the referenced Subsection 5.2.2., e.g. for cladding. In practice, compliance for some materials, components or assemblies of environmental separators and assemblies exposed to the exterior is determined by relying on provisions governing the use of alternative solutions (such as Clause 1.2.1.1.(1)(b) of Division A).

For some very common building elements and installations, however, there is a very large body of evidence of proven performance over a long period of time. In these cases, imposing the degree of analysis, or documentation of performance, required by Part 4 or Section 2.3. of Division C would be unnecessary and onerous. Clause 5.1.4.1.(5)(b) is intended to address these particular cases. Because the constructions are so widely accepted throughout the industry and the body of evidence is so substantial (though not necessarily documented in an organized fashion), there should be no question that detailed analysis or documentation is unnecessary.

Whether compliance of a particular material, component or assembly may be determined based on past performance depends not only on the type of material, component or assembly, but also on its intended function, the particular loads to which it will be subject and the magnitude of those loads. Because the possible combinations and permutations are infinite, only guidelines can be provided as to when past performance is a reasonable basis for determining compliance.

In determining compliance based on past performance, the period of past performance considered should be a substantial number of years. For example, 30 years is often used to do life-cycle cost analysis of the viability of investments in building improvements. This period is more than long enough for most deficiencies to show up. There should be no question as to the structural adequacy of a material, component or assembly that has been successfully used in a given application for such a period.

The determination of compliance may be based on past performance only where the function of the material, component or assembly is identical to that of the materials, components or assemblies used as a reference, and where the expected loads do not exceed those imposed on the reference materials, components or assemblies. For example, the acceptance of gypsum board, and its fastening, to serve as part of the backing wall supporting cladding cannot be based on the performance of gypsum board that has served only as an interior finish.

The determination of compliance may be based on past performance only where the properties of the material, component or assembly are identical or superior to those of the materials, components or assemblies used as a reference. For example, where a component of a certain gauge of a particular metal has provided acceptable performance, the same component made of the same metal or a stronger one would be acceptable.

Compliance with respect to various loads may be determined individually. A particular material may have to be designed to Part 4 to establish acceptable resistance to wind or earthquake loads, for example, but past performance may be adequate to determine that the material and normal fastening will support the material's dead load and will resist loads imposed by thermal and moisture-related expansion and contraction.

Past performance is a reasonable basis for determining compliance for lighter materials, components or assemblies not subject to wind load; for example, semi-rigid thermal insulation installed in wall assemblies where other materials, components or assemblies are installed to resist air pressure loads.

Past performance is an appropriate basis for determining compliance for some smaller elements that will be subject to wind loads but are continually supported or fastened behind elements that are designed for wind loads, for example, standard flashing over wall penetrations.

It should be noted that this particular approach to demonstrating compliance pertains only to the resistance or accommodation of structural loads described in Part 4. The resistance or accommodation of environmental loads, resistance to deterioration, and material compatibility must still be addressed in accordance with Part 5.

A-5.1.4.1.(6)(b) and (c)   Accommodating Movement. It is well understood that the deflection of the backing assembly in a wall can have significant effects on the performance of the cladding. For example, CSA S304, “Design of masonry structures,” specifies the maximum deflection criteria for backing assemblies to masonry veneer. Clauses 5.1.4.1.(6)(b) and (c) are written in very general terms in recognition of the fact that not only can the deflection of cladding affect the performance of the backing assembly, but that the excessive deflection of any element has the potential to adversely affect the performance of any adjacent element. Similarly, inter-storey drift has the potential to adversely affect the performance of components and assemblies of environmental separators. CSA O86, “Engineering design in wood,” specifies a method for calculating building movement due to changes in moisture content. The effects of movement should be avoided or accommodated.

A-5.1.4.2.   Deterioration. Environmental loads that must be considered include but are not limited to: sound, light and other types of radiation, temperature, moisture, air pressure, acids and alkalis.

Mechanisms of deterioration include:

•   structural (impact, air pressure)

•   hygrothermal (freeze-thaw, differential movement due to thermal expansion and contraction, ice lensing)

•   electrochemical (oxidation, electrolytic action, galvanic action, solar deterioration)

•   biochemical (biological attack, intrusion by insects and rodents).

Information on the effects of deformations in building elements can be found in the Commentary entitled Effects of Deformations in Building Components in the “Structural Commentaries (User's Guide – NBC 2020: Part 4 of Division B).”

Resistance to deterioration may be determined based on rational analysis, such as hygrothermal modeling, field performance, accelerated testing, or compliance with guidelines provided by evaluation agencies recognized by the authority having jurisdiction. Designers of buildings covered in Part 5 can find design guidance in the NRC publication entitled “Guideline on Design for Durability of Building Envelopes,” and in CSA S478, “Durability in buildings,” which presents updated methodologies for analyzing resistance to deterioration that provide quantitative results to support informed design decisions.

It is noted that the effects of future climate change and their potential impact on the durability of buildings are not fully known and, as such, are still being researched and studied. How future climate change and the issues of climate resilience are incorporated in building design should be carefully considered within the context of existing Code provisions related to structural design, fire and life safety, etc.

It is also noted that CSA S478 contains requirements for actions beyond the scope of the British Columbia Building Code, which may not be the responsibility of the designer, builder or authority having jurisdiction. These include requirements relating to quality assurance, inspection, maintenance, minimum design service lives and potential impacts of climate change, which are not addressed in the Code. The reference herein to CSA S478 is not intended to imply that the designer, builder or authority having jurisdiction adopt, apply or enforce any of these requirements.

Building components should be designed with some understanding of the length of time over which they will effectively perform their intended function. Actual service life will depend on the materials used and the environment to which they are exposed. The design should take into consideration these factors, the particular function of the component and the implications of premature failure, the ease of access for maintenance, repair or replacement, and the cost of repair or replacement.

Many buildings are designed such that access for maintenance, repair or replacement is not possible without damaging—or seriously risking damaging—other building elements. This can become a considerable deterrent to proper maintenance thus compromising the performance of the subject materials, components and assemblies, or other elements of the building. In cases where it is known or expected that maintenance, repair or replacement is likely to be required for certain elements before such time as the building undergoes a major retrofit, special consideration should be given to providing easy access to those elements. Anchorage points for maintenance personnel should be considered during the design of multi-storey buildings, including those of wood-frame construction, as adding them post-construction can be difficult.

Where the use of a building or space, or the services for a building or space, are changed significantly, an assessment of the impact of the changes on the environmental separators should be conducted to preclude premature failures that could create hazardous conditions.

A-5.2.1.1.(3)   Soil Temperatures. In theory, soil temperatures are needed to determine the conformance of a design to the requirements related to heat transfer and vapour diffusion. In practice, standard construction in a particular area may have proven to perform quite adequately and detailed calculations of soil temperature are unnecessary. (See also Sentence 5.2.1.3.(2).)

A-5.2.1.2.(1)   Interior Environmental Loads. The interior environmental conditions required depend on the intended use of the spaces in the building as defined in the building program. Spaces in different types of buildings and different spaces within a single building may impose different loads on the separators between interior and exterior spaces and between adjacent interior spaces. The separators must be designed to withstand the expected loads.

A-5.2.2.1.(2)(c)   Determination of Structural Loads and Effects. As regards materials, components and assemblies and their interfaces that are installed in buildings to which Part 5 applies, the effects of earthquake loads on their ability to resist or accommodate environmental loads are generally only taken into account in the design of post-disaster buildings. For all other buildings, damage to building components during seismic events is anticipated and these buildings are not intended to be functional after the event. However, for post-disaster buildings, seismic effects must be taken into account in the design for environmental separation, as these buildings are required to have an adequate degree of functionality after the design event to meet their intended function (see Article 4.1.8.13. for deflections and drift limits for post-disaster buildings).

However, it is important to note that earthquake effects must be taken into account in the seismic design of all building materials, components and assemblies and their interfaces covered by Article 4.1.8.18. to address life safety and the structural protection of buildings.

A-5.2.2.2.   Resistance to Wind and Other Air Pressure Loads. The wind load provisions apply to roofing and other materials subject to wind-uplift loads.

Note that, although Article 5.2.2.2. is specifically concerned with wind loads and directly references only one Article from Part 4, Sentence 5.2.2.1.(1) references all of Part 4 and would invoke Article 4.1.7.10. for example, which is concerned with air pressure loads on interior walls and partitions.

A-5.2.2.2.(4)   Membrane Roofing Systems. Wind loads for membrane roofing systems must be calculated in accordance with Part 4. The tested uplift resistance and factored load should satisfy the requirements of the Commentary entitled Limit States Design in the “Structural Commentaries (User's Guide – NBC 2020: Part 4 of Division B).”

The test method described in CAN/CSA-A123.21, “Standard test method for the dynamic wind uplift resistance of membrane-roofing systems,” applies only to membrane roofing systems whose components' resistance to wind uplift is achieved by fasteners or adhesives. It does not apply to roofing systems that use ballasts, such as gravel or pavers, to secure the membrane against wind uplift.

In the case of membrane roofing systems in which the waterproof membrane is attached to the structural deck using mechanical fasteners, the wind-induced forces and the roofing system's response are time- and space-dependent and, thus, dynamic in nature. Further information on the design and evaluation of such systems can be found in “A Guide for the Wind Design of Mechanically Attached Flexible Membrane Roofs,” published by NRC.

The wind uplift resistance obtained from the test method in CAN/CSA-A123.21 is limited to configurations with specific fastener or adhesive patterns. To extrapolate the test data to non-tested configurations, refer to ANSI/SPRI WD-1, “Wind Design Standard Practice for Roofing Assemblies,” for a rational calculation procedure. However, in using this extrapolation procedure, wind loads should be calculated in accordance with the code. NRC's guide for wind design referenced above provides further guidance and examples of wind load calculations.

A-5.3.   Heat Transfer. In addressing issues related to health and safety, Section 5.3. calls up levels of thermal resistance needed to minimize condensation on or within environmental separators, and to ensure thermal conditions appropriate for the building use. Energy regulations, where they exist, specify levels of thermal resistance required for energy efficiency or call up energy performance levels, which relate to levels of thermal resistance. Where Part 5 calls for levels of thermal resistance higher than those required by the energy regulations, the requirements of Part 5 take precedence.

A-5.3.1.1.   Required Resistance to Heat Transfer. The control of heat flow is required wherever there is an intended temperature difference across the building assembly. The use of the term “intended” is important since, whenever interior space is separated from exterior space, temperature differences will occur.

The interior of an unheated warehouse, for example, will often be at a different temperature from the exterior due to solar radiation, radiation from the building to the night sky and the time lag in temperature change due to the thermal mass of the building and its contents. If this temperature difference is not “intended,” no special consideration need be given to the control of heat flow.

If the warehouse is heated or cooled, thus making the temperature difference “intended,” some consideration would have to be given to the control of heat flow.

It should be noted, however, that in many cases, such as with adjacent interior spaces, there will be an intended temperature difference but the difference will not be great. In these cases, the provisions to control heat flow may be little or no more than would be provided by any standard interior separator. That is, materials typically used in the construction of partitions may provide the separation needed to meet the requirements of Section 5.3. without adding what are generally considered to be “insulating” materials.

A-5.3.1.2.   Material and Component Properties and Condensation. Total prevention of condensation is generally unnecessary and its achievement is rarely a certainty at design conditions. Part 5, therefore, requires that condensation be minimized. The occurrence of condensation should be sufficiently rare, or the quantities accumulated should be sufficiently small and dry rapidly enough, to avoid material deterioration and the growth of mould and fungi.

The Harmonized North American Fenestration Standard, AAMA/WDMA/CSA 101/I.S.2/A440, “North American Fenestration Standard/Specification for windows, doors, and skylights,” identifies procedures to determine the condensation resistance and thermal transmittance of windows, doors and skylights though testing for condensation resistance is presented as optional in the standard. As such, a fenestration product that meets the standard's requirements on air leakage, water penetration, uniform load and other performance requirements may not meet the condensation resistance performance level needed for a given application. Only the physical test procedure presented in CSA A440.2, “Fenestration energy performance,” can be used to establish the temperature index (I) value, which denotes condensation resistance performance evaluation criteria. It is recommended that designers specify I values for a given application to minimize the potential for condensation. Further guidance on the selection of the correct I value is provided in CSA A440.3, “User guide to CSA A440.2:19, Fenestration energy performance.”

The scope of AAMA/WDMA/CSA 101/I.S.2/A440, which is referenced in Subsection 5.9.2., includes skylights and tubular daylighting devices (TDD). Where skylights and TDDs pass through unconditioned space, their wells and shafts may become the environmental separator and would therefore have to comply with the requirements of Part 5.

A-5.3.1.2.(1)   Use of Thermal Insulation or Mechanical Systems for Environmental Control. The level of thermal resistance required to avoid condensation on the warm side of an assembly or within an assembly (at the vapour barrier), and to permit the maintenance of indoor conditions appropriate for the occupancy depends on

•   the occupancy,

•   the exterior design air temperature,

•   the interior design air temperature and relative humidity,

•   the capacity of the heating system, and

•   the means of delivering heat.

To control condensation on the interior surface of an exterior wall, for example, the interior surface must not fall below the dew point of the interior air. If, for instance, the interior air is 20°C and 35% RH, the dew point will be 4°C. If the interior air is 20°C and 55% RH, the dew point will be 11°C.

Where the exterior design temperature is mild, such as in south coastal British Columbia, the interior RH during the heating season may well be around 55%. With an exterior temperature of -7°C, the materials in the environmental separator would have to provide a mere RSI 0.082 to avoid condensation on the interior surface. Depending on the specific properties of the material, this RSI might be provided by 10-mm plywood. Therefore, materials generally recognized as thermal insulation would not be required only to limit condensation on the warmer side of the building envelope.

In other areas of the Province, however, exterior design temperatures are much lower. In these cases, maintaining temperatures inboard of the vapour barrier above the dew point will require insulation or increased heat delivery to the environmental separator. Direct delivery of heat over the entire surface of the environmental separator is generally impractical. Indirect heat delivery may not be possible without raising the interior air temperatures above the comfort level. In any case, increased heat delivery would often entail excessive energy costs.

In addition to controlling condensation, interior surface temperatures must be warm enough to avoid occupant discomfort due to excessive heat loss by radiation. Depending on the occupancy of the subject spaces, this may require the installation of insulation even where it is not needed to control condensation.

A-5.3.1.3.(2)   Position of Materials Providing Thermal Resistance. For a material providing thermal resistance to be effective, it must not be short-circuited by convective airflow through or around the material. The material must therefore be either

•   the component of the air barrier system providing principal resistance to air leakage, or

•   installed in full and continuous contact with a continuous low air permeance component.

A-5.4.1.   Air Barrier Systems. An air barrier system is required in most buildings to control air movement through the environmental separator to minimize

•   the condensation of airborne moisture within the environmental separator,

•   discomfort from drafts,

•   the infiltration of dust, soil gases, and other pollutants,

•   interference in the performance of building services, such as HVAC and plumbing,

•   the infiltration of exterior precipitation, and

•   the loss of airborne heat energy.

The requirements for air barrier systems in Part 5 address all of these issues, except the loss of airborne heat energy, which is an energy performance issue and, as such, is addressed in the NECB. Failure to manage the issues addressed in Part 5 can lead to serious health or safety hazards.

The most significant issues are those with the potential to cause moisture-related material deterioration, such as rot and corrosion, which can lead to the failure of component connections. Where the environmental separator is subject to high moisture levels, mould can grow if spores and organic materials are present.

A-5.4.1.1.   Locations Where an Air Barrier System Is Required. Where the hygrothermal environments in adjacent interior spaces are sufficiently different, an air barrier system is required to control the airflow between the spaces in order to maintain the different environments. Examples of such adjacent spaces include skating arenas adjoining swimming pools, and industrial office spaces adjoining industrial production spaces.

An air barrier system is also required in building assemblies in contact with the ground to control the ingress of radon and other soil gases, such as methane.

In addition to an air barrier system, other measures may be required in certain regions to reduce the radon concentration to a level below the guideline specified by Health Canada. Further information on protection from radon ingress can be found in:

•   “Radon: A Guide for Canadian Homeowners” (CMHC/HC),

•   “Guide for Radon Measurements in Public Buildings (Schools, Hospitals, Care Facilities, Detention Centres)” (HC), and

•   EPA 625/R-92/016, “Radon Prevention in the Design and Construction of Schools and Other Large Buildings.”

A-5.4.1.1.(3)   Air Leakage Performance Classes for Air Barrier Assemblies. The selection of a Performance Class for an air barrier assembly is intended to ensure that the air leakage performance level of the assembly is sufficient to minimize condensation and reduce the uncontrolled movement of air across the environmental separator.

The accumulation of condensation within a building assembly as a result of air leakage through the environmental separator depends on the following:

•   the air leakage rate of the air barrier assembly,

•   the location of the accumulation of condensation within the building assembly, and

•   the drying potential of the building assembly (i.e., its ability to release moisture through vapour diffusion and surface evaporation, both inward and outward).

Critical to the rates of both drying and the accumulation of condensation is the location where moisture may occur within the building assembly. The location and amount of accumulation of condensation due to air leakage are influenced by the materials used in the building assembly and the temperatures within the assembly. The location of insulation within the building assembly is critical and can directly influence whether condensation occurs and how much moisture condensation actually accumulates.

The drying potential of the building assembly is dependent on the water vapour permeance of the various layers in the building assembly (e.g., exterior sheathing, sheathing membrane, unvented cladding, vapour barrier).

CAN/ULC-S742, “Standard for Air Barrier Assemblies – Specification,” contains requirements and test methods for air barrier assemblies used in high- and low-rise buildings. The standard classifies the air leakage performance of air barrier assemblies on the basis of air leakage rate, building height, and wind pressure loading. The approach in the standard is consistent with limit states design principles to allow for the direct incorporation of test results into the overall structural design of the building.

Unlike ASTM E2357, “Standard Test Method for Determining Air Leakage Rate of Air Barrier Assemblies,” CAN/ULC-S742 measures air leakage under two temperature conditions:

(1)   at ambient temperatures with no temperature differential across the test assembly, and

(2)   with the exterior side of the test assembly at a temperature of −20°C and the interior side at a temperature of +20°C (i.e., with a temperature differential of 40°C across the test assembly).

This difference makes the testing approach in CAN/ULC-S742 more appropriate for the climate in most regions of Canada.

CAN/ULC-S742 does not address the structural transfer of air pressure loads from air barrier assemblies to adjoining air barrier assemblies or the primary structure. Nevertheless, this transfer of loads must be addressed by the designer.

The Performance Class of an air barrier assembly is selected on the basis of the following:

•   the moisture loads on the building assembly due to the hygrothermal characteristics of the air,

•   the ability of the materials and components of the building assembly to absorb and distribute moisture,

•   the ability of the building assembly to dissipate moisture before it can lead to harm to the occupants or damage to the materials and components of the building assembly, and

•   the moisture tolerance of the materials from which the building assembly is constructed.

Air barrier assemblies with lower air leakage rates are typically necessary where the drying potential of the building assembly is low and/or the moisture sensitivity of components of the building assembly is high.

Before selecting the appropriate Performance Class, the designer should consider formal study, analysis and/or modeling to establish performance criteria for each air barrier assembly. Further guidance can be found in the NRC publication entitled “Guideline on Design for Durability of Building Envelopes.” This recommendation is particularly important for buildings with

•   higher than normal operating hygrothermal characteristics, e.g., museums, swimming pools and laboratories,

•   building assemblies made from materials and components with lower than normal moisture tolerances, e.g., wood and other organic materials, or

•   occupancies with a low tolerance for the potential health risks associated with condensation, e.g., hospitals, long-term care facilities and laboratories.

In such cases, Performance Classes with lower air leakage rates should be selected.

A-5.4.1.1.(4)   Continuity of Air Barrier Systems. An air barrier system can only function properly if all the materials, components and assemblies intended to provide the air barrier functions are continuously connected and structurally capable of resisting applied loads. Historically, most failures of air barrier systems in buildings have been directly related to improper or insufficient connections between adjacent air barrier materials, components and assemblies.

A-5.4.1.1.(7)   Locations Where an Air Barrier System Is Not Required. In Canada, there are few buildings intended for human occupancy where the interior space is conditioned but an air barrier system is not required. Any exemption from installing an air barrier system would depend on the level of interior conditioning provided, the ventilation level, the protection provided for the building's occupants, and the tolerance of the building's construction to the accumulation of condensation and potential precipitation ingress.

In some industrial buildings, limited conditioning (e.g., radiant heating) is provided, and ventilation levels are sufficient to reduce the relative humidity to a level at which condensation will not accumulate to an unacceptable degree. Conversely, some industrial buildings, due to the processes they contain, operate at very high temperatures and high ventilation levels. In such cases, the building envelope may be maintained at temperatures required to avoid condensation. In both of these examples, either the ventilation levels or protective means required in the work environment would protect the building's occupants from unacceptable levels of pollutants.

A-5.4.1.2.(1)   Low-Sloped Membrane Roof Assemblies.

For low-sloped membrane roof assemblies, CAN/ULC-S742, “Standard for Air Barrier Assemblies – Specification,” provides pre-tested prescriptive solutions that have an air leakage rate not exceeding 0.2 L/(s×m2). The air leakage rate of low-sloped membrane roof assemblies not identified in CAN/ULC-S742 should be determined in accordance with ASTM D8052/D8052M, “Standard Test Method for Quantification of Air Leakage in Low-Sloped Membrane Roof Assemblies.”

A-5.4.1.2.(2)   Air Barrier Assemblies Not Evaluated in Accordance with CAN/ULC-S742. Air barrier assemblies that have not been evaluated in accordance with CAN/ULC-S742, “Standard for Air Barrier Assemblies – Specification,” must nevertheless provide the air leakage performance required for the selected Performance Class. Field testing may be required to verify their performance.

Field assessment of the air leakage characteristics of both the primary air barrier assemblies and the connections between adjacent air barrier assemblies can be a useful tool in establishing whether the acceptable minimum performance level is met.

Field testing of installed air barrier assemblies can be conducted in accordance with test standards such as

•   ASTM E783, “Standard Test Method for Field Measurement of Air Leakage Through Installed Exterior Windows and Doors,” and

•   ASTM E1186, “Standard Practices for Air Leakage Site Detection in Building Envelopes and Air Barrier Systems.”

Even though some test standards are intended for specific types of air barrier assemblies (e.g., windows and doors), the test methodology used to assess air leakage rates may be acceptable for use with other types of air barrier assemblies. However, with this approach, it is important to establish rational acceptance criteria that reflect the test methodology and the types of air barrier assemblies being tested.

Qualitative testing can be used to identify locations in air barrier assemblies where air leakage is occurring so that field repairs can be made to improve the assembly's airtightness performance. ASTM E1186 provides guidance on a number of approaches for identifying locations of air leakage, including the following:

•   infrared scanning,

•   smoke tracer observation,

•   airflow measurement,

•   sound detection,

•   tracer gas detection, and

•   liquid leak detection.

Each of these techniques has benefits and limitations, as described in the standard. The most suitable approach for a particular situation is selected by the testing agency on the basis of their experience in relation to the type of construction being assessed and the weather conditions at the time of testing. Regardless of the approach selected, the testing of air barrier assemblies must be properly coordinated with the construction process so that any air leaks identified can be addressed without adversely affecting progress.

A-5.4.1.2.(4)   Testing of Below-Grade Air Barrier Assemblies. To ensure that they minimize the ingress of radon and other soil gases, below-grade air barrier assemblies in contact with the ground can be tested in accordance with CAN/ULC-S742, “Standard for Air Barrier Assemblies – Specification,” using the air leakage limit for Performance Class 1 or a more stringent limit. In such air barrier assemblies, as in all air barrier assemblies, penetrations and junctions are the most likely locations for air leakage. These points of weakness must be properly detailed and constructed to minimize the ingress of soil gases.

A-5.5.1.1.   Required Resistance to Vapour Diffusion. Resistance to vapour diffusion is required to reduce the likelihood of condensation within building assemblies, and the consequent potential for material deterioration and fungal growth. Deterioration such as rot and corrosion can lead to the failure of building components and connections, and interfere with the performance of building services. Some fungi can have very serious effects on health.

In Canada, relatively few buildings that are subject to temperature and vapour pressure differences would be constructed or operated in such a manner that the control of vapour diffusion would not need to be addressed in their design. Assemblies enclosing certain industrial spaces, as described in Note A-5.4.1.1.(7) for example, may be exempt.

For residential spaces, and most other spaces that are conditioned for human occupancy, a means of vapour diffusion control is generally agreed to be necessary, even in milder climates of the province. The questions in those cases pertain to the degree of control needed.

The word “minimize” is used in Sentence 5.5.1.1.(1) because not all moisture accumulation in an assembly need be of concern. Incidental condensation is normal but should be sufficiently rare and in sufficiently limited quantities, and should dry rapidly enough, to avoid material deterioration and the growth of mould or fungi. Here are some references regarding the effects of fungi on health:

•   “Fungal Contamination in Public Buildings: Health Effects and Investigation Methods,” Health Canada

•   “Guidelines on Assessment and Remediation of Fungi in Indoor Environments,” New York City Department of Health and Mental Hygiene (NYCDH)

A-5.5.1.2.(1)   Vapour Barrier Materials and Installation. In the summer, many buildings are subject to conditions where the interior temperature is lower than the exterior temperature. Vapour transfer during these periods is from the exterior to the interior. In general, in Canada, the duration of these periods is sufficiently short, the driving forces are sufficiently low, and assemblies are constructed such that any accumulated moisture will dissipate before deterioration will occur.

Buildings such as freezer plants, however, may operate for much of the year at temperatures that are below the ambient exterior temperature. In these cases, the “warm” side of the assembly would be the exterior and a detailed analysis on an annual basis is required.

Steady state heat transfer and vapour diffusion calculations may be used to determine acceptable permeance levels for the vapour barrier and to identify appropriate positions for the vapour barrier within the building assembly.

A-5.6.1.1.   Required Protection from Precipitation. Windows, cast-in-place concrete walls, and metal and glass curtain wall systems are examples of components and assemblies that, when properly designed and constructed, are expected to prevent the ingress of precipitation into a building. Assemblies such as roofs and veneer walls consist of materials specifically intended to screen precipitation.

Components and assemblies separating interior conditioned space from the exterior are generally required to provide protection from the ingress of precipitation. Components and assemblies separating interior unconditioned space from the exterior may or may not be required to provide protection from the ingress of precipitation. Buildings such as stadia, parking garages and some seasonally occupied buildings, for example, may not require complete protection from the ingress of precipitation. The degree of protection will depend to a large extent on the materials selected for the building elements that will be exposed to precipitation.

The word “minimize” is used in Sentence 5.6.1.1.(1) because not all moisture ingress or accumulation in an assembly need be of concern. The penetration of wind-driven rain past the cladding may not affect the long-term performance of the assembly, provided the moisture dries out or is drained away before it initiates any deterioration of building materials. When the design service life of a material or component is longer than the design service life of the overall assembly, taking into account the expected exposure to moisture, initiating deterioration of the material should not be of concern. That is to say, provided the material or component continues to provide the necessary level of performance for its intended service life and does not adversely affect the service life of the assembly of which it is a part, the deterioration of the material or component is not an issue.

A-5.6.1.2.(1)   Ice Damming. Water leakage through sloped roofs is often due to the formation of ice dams at the eaves, which can be limited by controlling the transfer of heat to the roof through a combination of insulation and venting to dissipate heat. See Clause 5.3.1.2.(1)(d).

A-5.6.1.2.(2)   Vegetated Roofing Systems. The integrity of some assemblies installed to provide the required protection from the ingress of precipitation in vegetated roofing systems can be compromised due to an inadequate resistance to the penetration of plant roots and rhizomes. Additional information on vegetated roofing systems and the performance of protective materials can be found in the German Landscape Research, Development and Construction Society's (FLL) “Guidelines for the Planning, Construction and Maintenance of Green Roofing” and in the National Roofing Contractors Association's “The NRCA Vegetative Roof Systems Manual.”

A-5.6.2.1.   Sealing and Drainage. A number of different design solutions can provide an environmental separator with the minimum performance level necessary to effectively control environmental and structural loads and their effects. An appropriate solution is selected on the basis of the applied load characteristics, the performance achieved by the solution, and its durability over the design service life. It is incumbent on the designer to balance the performance of a particular design solution against the required performance level, the risk of failure, and the consequences of failure for the building and its users.

Article 5.6.2.1. recognizes that acceptable solutions can use various strategies and single or multiple elements within the design to control precipitation. However, as indicated by research and the documentation of failures, some of these solutions are more effective than others.

One solution—a face-sealed assembly—relies on a continuous watertight surface on the outside of a building to control all precipitation over the life of the building; there is no redundancy in this design. The watertight surface can be difficult to both design and construct, and its long-term durability depends on proper preventive maintenance over its service life. This solution has a well-documented history of unsatisfactory performance in most regions of Canada.

A solution with redundancy in its design provides more effective and reliable resistance to water penetration. For example, in a rainscreen assembly, multiple water-resistive layers are combined with means to drain any water that has penetrated the outer layer and means to redirect this water to the exterior before it can affect moisture-sensitive materials within the assembly. Another solution—a mass wall assembly—accumulates and stores moisture, which is re-released to the exterior when conditions allow. Depending on the solution selected, means to facilitate the drying of materials may be incorporated in the assembly.

In selecting an acceptable solution for precipitation control, it is important to consider the structural and environmental loads that are referenced in Subsection 5.1.4. The resistance provided by the design solution must exceed these loads and their effects. The greater the intensity of the load, the higher the performance level required to provide the necessary resistance and an acceptable level of risk. Design considerations that should be addressed include the following:

•   intended building use(s),

•   building exposure during service life (height, orientation and surrounding terrain),

•   building exposure during construction,

•   current and future local climate characteristics affecting wetting and drying, including

–wind loads,

–precipitation loads (including wind-driven precipitation loads),

–relative humidity,

–temperature variations, and

–solar exposure,

•   imposed load intensity, both in isolation and in combination (type, number, magnitude, frequency and duration),

•   material types and moisture tolerances,

•   resistance to the mechanisms of deterioration,

•   effects of deformations, displacements and deflections of the building structure, and of materials, components and assemblies,

•   constructability of materials, components and assemblies,

•   expected construction tolerances,

•   level of maintenance required to maintain resistance to loads and deterioration,

•   intended service life of materials, components and assemblies, and

•   reliability of materials, components and assemblies.

All the materials in an environmental separator must be able to resist the mechanisms of deterioration that are expected to occur over the design service life of the separator. For example, with respect to deterioration caused by moisture, a material used in a design must not be exposed to moisture in sufficient quantity and/or for sufficient length of time to reduce its ability to perform its required function(s) to a level below the required performance level. This concern is particularly important for materials that are known to be susceptible to moisture deterioration.

An environmental separator must also be designed to be suitably resistant to failure caused by

•   uncertainty or variation in load intensity,

•   uncertainty in the effects of loads on materials, components and assemblies,

•   uncertainty in the predicted service lives of materials, components and assemblies, and

•   construction deficiencies that can reasonably be anticipated.

The building structure and the environmental separator are mutually dependent in managing precipitation. The choice of materials for the building structure and the structural support/backing for the environmental separator can influence the choice of materials, components and assemblies for the environmental separator. Materials, components and assemblies with higher performance levels may be required for the environmental separator where the building structure and the structural support/backing have lower material strengths, undergo higher in-service movements (e.g., shrinkage or deflection), or have lower resistance to deterioration.

The design and construction of details at penetrations, at joints and junctions between assemblies, and at transitions between planes are of critical importance to the long-term performance and durability of the environmental separator. Designers should provide sufficient detail on drawings to illustrate how the design solution for precipitation control is to be integrated into the building (see Subsection 2.2.5. of Division C).

A-5.7.   Protection from Interior Sources of Water. Protection similar to that prescribed in Section 5.7. may be required where interior assemblies are in contact with water (such as site-built showers, steam rooms, swimming pool areas) and where adjacent interior spaces need to be protected from the transfer of water through these assemblies.

A-5.7.1.2.(2)   Drainage. Water should be directed away from the building and, ultimately, to a municipal drainage system, drainage ditch, swale, or other acceptable water management means. This can be accomplished by setting the building grade higher than the surrounding grades, by sloping the grade away from the building, by installing a surface water drainage system, or by a combination of these approaches. The chosen approach should follow generally accepted guidelines, such as the Rational Method of Stormwater Design by David B. Thompson, or other design methods acceptable to the authority having jurisdiction.

A-5.7.3.3.(1)(a)   Imperfections. Examples of imperfections include shrinkage cracks, air holes, honeycombing, form-tie cone holes, and form joint ridges.

A-5.7.3.4.(1)   Dampproofing. Dampproofing refers to the application of a material or materials to an environmental separation assembly to protect it and the interior space against the transfer of moisture due to the mechanisms of water vapour transmission, capillary action and pressure differences other than hydrostatic pressure.

A dampproofed assembly should be designed such that it can provide short-term resistance to the ingress of water due to occasional hydrostatic pressure from ground water.

A-5.8.   Required Protection from Noise. Section 5.8. applies to the separation of dwelling units from other dwelling units and from spaces where noise may be generated with regard to sound transmission irrespective of Clause 5.1.2.1.(1)(b), which deals with the separation of dissimilar environments. It is understood that, at any time, there is the potential for sound levels to be quite different in adjoining dwelling units.

A-5.8.1.2.   Using ASTC in lieu of STC. A designer may choose to use an ASTC rating of equal or higher numerical value than the required STC to show compliance where STC ratings are required.

An ASTC measurement or calculation will always yield a value equal to or lower than the STC for the same configuration, as the ASTC includes flanking transmission.

A-5.8.1.4.   Methods of Calculating ASTC. The technical concepts, terminology, and calculation procedures relating to the detailed and simplified ASTC calculation methods are discussed in detail, with numerous worked examples, in the NRC publication entitled “Guide to Calculating Airborne Sound Transmission in Buildings.” This Guide includes references to readily-available sources of pertinent data.

For many common constructions, the calculations required by Article 5.8.1.4. can be performed using software tools, such as soundPATHS, which is available on the NRC's website.

The simplified calculation method may not always identify the prominent flanking paths. Furthermore, it corresponds more closely with the results of the detailed calculation method where the separating assembly and the flanking constructions are both constructed according to the same method, i.e. either both are lightweight construction (steel or wood framing) or both are heavyweight construction (masonry or concrete).

A-5.8.1.4.(4)(b)   Assemblies that Behave Like Homogeneous Panels. Examples of assemblies that behave like homogeneous panels include cast-in-place concrete, precast concrete, precast hollow-core concrete, concrete block masonry, and mass timber panels. For the purpose of calculating the ASTC rating for construction using mass timber panel walls or floor assemblies in accordance with the detailed method described in Sentence 5.8.1.4.(4), a mass timber panel behaves as a homogeneous panel, notwithstanding that it has an average structural loss factor greater than 0.03. Further information on the calculation of the ASTC rating for mass timber panel assemblies can be found in the NRC publication entitled “Guide to Calculating Airborne Sound Transmission in Buildings.”

A-5.9.1.1.(1)   Selection of Materials and Components and Compliance with Referenced Standards. It is important to note that Sentence 5.9.1.1.(1) is stated in such a way that the selection of materials and components is not limited to those traditionally recognized as serving particular functions or those for which a standard is identified in Table 5.9.1.1. This approach permits more flexibility than is provided by similar requirements in Part 9. As long as the selected material meets the performance requirements stated elsewhere in Part 5, the material may be used to serve the required function.

However, where the selected material or component, or its installation, falls within the scope of any of the standards listed in Table 5.9.1.1., the material, component or installation must comply with that standard. For example, if some resistance to heat transfer is required between two interior spaces and standard partition construction will provide the necessary resistance, the installation of one of the “thermal insulation” materials identified in the standard list is not required. If, on the other hand, one decides to install glass fibre insulation, the material must conform to CAN/ULC-S702.1, “Standard for Mineral Fibre Thermal Insulation for Buildings, Part 1: Material Specification.”

A-Table 5.9.1.1.   Selection and Installation of Sealants. Analysis of many sealant joint failures indicates that the majority of failures can be attributed to improper joint preparation and deficient installation of the sealant and various joint components. The following ASTM guidelines describe several aspects that should be considered when applying sealants in unprotected environments to achieve a durable application:

•   ASTM C1193, “Standard Specification for Use of Joint Sealants,” and

•   ASTM C1472, “Standard Guide for Calculating Movement and Other Effects When Establishing Sealant Joint Width.”

The sealant manufacturer's literature should always be consulted for recommended procedures and materials.

A-5.9.2.1.(3)   Airtightness and Watertightness of Windows, Doors, Skylights, Other Fenestration Assemblies and their Components Required to have a Fire-Protection  Rating. The airtightness and watertightness requirements are waived for these products when used in such an application, in recognition of the fact that the availability of assemblies that meet both the requirements of the applicable standards and the requirements for fire resistance may be limited. However, control of air and water leakage should not be ignored: measures should be taken to attempt to comply with applicable requirements.

A-5.9.2.2.   Manufactured Windows, Doors and Skylights.

Two Compliance Paths. It is intended that any fenestration product that conforms to this Subsection may choose to comply with either Article 5.9.2.2. or Article 5.9.2.3. Even if a product is in scope of the standards referenced in Article 5.9.2.2. (NAFS and the Canadian Supplement to NAFS), the compliance path in Article 5.9.2.3. may be used. However, it is not intended that the compliance path in Article 5.9.2.2. be used where fenestration products are not within the scope of the referenced standards.

Design Values

CSA A440S1, “Canadian Supplement to AAMA/WDMA/CSA 101/I.S.2/A440, North American Fenestration Standard/Specification for windows, doors, and skylights,” requires that the individual performance levels achieved by the product for structural resistance, water penetration resistance and air leakage resistance be reported on the product's performance label.

Storm Doors and Windows

Where storm doors and storm windows are not incorporated in a rated window or door assembly, they should be designed and constructed to comply with the applicable requirements of Part 5 regarding such properties as appropriate air leakage and structural loads.

Forced Entry Test

Even though the performance label on rated windows, doors and skylights does not explicitly indicate that the product has passed the forced entry resistance test, products are required to pass this test in order to be rated.

A-5.9.2.2.(4) Loads and Procedures. For windows within the scope of the “Canadian Supplement” referred to in Sentence 5.9.2.2.(1), structural and wind loads are included and may be calculated in accordance with that standard. As an alternative, structural and wind loads from Section 5.2. may be used to select fenestration products that are appropriate for the point of

installation. Values derived from the referenced standard, which uses a simplified calculation method, are typically higher than those derived from calculations done in conformance with Section 5.2.

A-5.9.2.3.(1)   Installation and Field Testing of Windows, Doors and Skylights.

Installation

The installation details of windows, doors, skylights and their components must be appropriately designed and implemented for the building envelope assembly to perform acceptably overall. The proper design of the installation details provides the information necessary to integrate the structure and air, vapour and moisture barrier functions of windows, doors and skylights into the overall design of the building envelope assembly. Construction should be carried out in accordance with these details to achieve an appropriate level of long-term performance. Further guidance on installation detailing can be found in CSA A440.4, “Window, door, and skylight installation.”

Field Testing

It is recommended that the performance of installed windows, doors and skylights be field tested early in the envelope construction phase so that any discontinuities can be readily identified and corrected before construction of the building envelope assembly is completed. Additional field testing during subsequent construction phases to monitor installation consistency is also recommended. Field test procedures should be carried out in accordance with test standards such as ASTM E783, “Standard Test Method for Field Measurement of Air Leakage Through Installed Exterior Windows and Doors,” and ASTM E1105, “Standard Test Method for Field Determination of Water Penetration of Installed Exterior Windows, Skylights, Doors, and Curtain Walls, by Uniform or Cyclic Static Air Pressure Difference.” Further guidance can be found in CSA A440.4, “Window, door, and skylight installation,” which also includes performance requirements developed in accordance with AAMA/WDMA/CSA 101/I.S.2/A440, “North American Fenestration Standard/Specification for windows, doors, and skylights,” to be used when performing field testing.

A-5.9.2.4.(3)   Heat Transfer through Fire-Rated Glazed Assemblies. Thermal bridging through fire-rated glazed assemblies should not be ignored; measures should be taken to minimize condensation consistent with the intent of Sentence 5.9.2.4.(2).

A-5.9.3.   Testing Standards for Other Fenestration Assemblies.  Subsection 5.9.3. references ASTM test methods. The following AAMA standards can also be used to evaluate the performance characteristics of other fenestration assemblies:

•   AAMA 501, “Methods of Test for Exterior Walls,”

•   AAMA 501.1, “Standard Test Method for Water Penetration of Windows, Curtain Walls and Doors Using Dynamic Pressure,”

•   AAMA 501.2, “Quality Assurance and Diagnostic Water Leakage Field Check of Installed Storefronts, Curtain Walls, and Sloped Glazing Systems,”

•   AAMA 501.4, “Recommended Static Test Method for Evaluating Curtain Wall and Storefront Systems Subjected to Seismic and Wind-Induced Inter-Story Drifts,”

•   AAMA 501.5, “Test Method for Thermal Cycling of Exterior Walls,” and

•   AAMA 501.6, “Recommended Dynamic Test Method for Determining the Seismic Drift Causing Glass Fallout from a Wall System.”

•   ASTM E 331, “Water Penetration of Exterior Windows, Skylights, Doors, and Curtain Walls by Uniform Static Air Pressure Difference.”

•   ASTM E 547, “Water Penetration of Exterior Windows, Skylights, Doors, and Curtain Walls by Cyclic Static Air Pressure Difference.”

A-5.9.3.1.(1)   Terminology for Other Fenestration Assemblies.

Curtain Wall

A curtain wall is considered to be a continuous wall cladding assembly (which may include fenestration and opaque portions) that is hung away from the edge of the primary floor structure. Curtain wall assemblies do not generally support vertical loads other than their own weight. Anchorage is typically provided by anchors that connect back to the floor structure. Curtain wall assemblies can be either “stick built,” meaning each main unit is assembled on-site, or a “unitized” system, meaning factory-assembled main units are installed and connected together on-site.

Window Wall

A window wall is considered to be a wall cladding assembly (which may include fenestration and opaque portions) that spans from the top of a primary floor structure to the underside of the next higher primary floor structure. Window wall assemblies do not generally support vertical loads other than their own weight. Primary provision for anchorage occurs at head and sill connections with the adjoining floor structure. Window wall assemblies may include separate or integral floor edge covers.

Storefront

A storefront is considered to be a non-residential assembly (which may include fenestration and opaque portions) consisting of one or more elements that could include doors, windows and curtain wall framing. Storefronts do not generally support vertical loads other than their own weight. Storefront profiles are typically narrow, rectilinear framing members that hold a combination of pocket glazing and applied glazing stops to securely retain the infills. Vertical framing members typically span the height of one floor or are retained within a structural punched opening.

Storefront assemblies are designed/selected to take into account the anticipated service and exposure conditions, which may be different than those for other portions of the building.

Glazed Architectural Structures

Glazed architectural structures are considered glazing assemblies that are supported in a non-traditional manner, such as corner-clamped, point-supported, linear-supported and edge-clamped glazing. Structural support systems can include, but are not limited to, tension cables, tension rods, steel and glass. Glazed architectural structures do not generally support vertical loads other than their own weight. These assemblies are designed/selected to take into account the anticipated service and exposure conditions, which may be different than those for other portions of the building.

Skylights that are not covered by AAMA/WDMA/CSA 101/I.S.2/A440, “North American Fenestration Standard/Specification for windows, doors, and skylights,” are considered glazed architectural structures.

A-5.9.3.2.(1)   Structural and Environmental Loads. The applicable laboratory test method for demonstrating adequate structural performance of other fenestration assemblies is ASTM E330/E330M, “Standard Test Method for Structural Performance of Exterior Windows, Doors, Skylights and Curtain Walls by Uniform Static Air Pressure Difference.”

A-5.9.3.3.(1)   Resistance to Condensation. Notwithstanding that other fenestration assemblies are not fully covered under the testing scope of CSA A440.2, “Fenestration energy performance,” the test method described therein can be used to evaluate their resistance to condensation, with technical modifications to accommodate differences in the size and configuration of the specimen. It is also common practice to use one cold cycle of AAMA 501.5, “Test Method for Thermal Cycling of Exterior Walls,” to assess the potential for condensation. Both methods can be used for mock-ups in laboratory performance evaluations, however, only the test method in CSA A440.2 should be used if a Temperature Index is required. In most cases, the project specification documents establish the hygrothermal conditions (i.e., exterior temperature, interior temperature, interior relative humidity) for which the potential for condensation should be minimized. Under these conditions, the aforementioned test methods can be used to aid in the selection of the appropriate system performance to minimize the potential for interior surface condensation. In all cases, care should be taken in the construction and configuration of the specimen, as these parameters may have an impact on its thermal performance and resistance to condensation. These parameters may include, without limitation, interior wall construction and finishes, heating systems, ventilation systems, etc., to simulate the actual in-service conditions as closely as practicable.

A-5.9.3.4.(2)   Air Leakage.

Air Leakage Rate and Test Pressure

A lower air leakage rate and/or higher differential test pressure can be selected for specific applications of other fenestration assemblies where tight control of airflow is required to prevent interstitial condensation (e.g., in concealed spaces), improve thermal comfort (e.g., in hospitals, seniors' residences), or prevent the migration of airborne contaminants (e.g., in food and drug research, manufacturing applications, biological laboratories). It is typical of other fenestration assemblies to be used as the sole building envelope component; where this is the case, a correspondingly higher degree of airtightness may be required.

In addition, higher test pressure differentials can be used to evaluate assemblies with low air leakage, such as non-operable or fixed fenestration systems whose air leakage rates are not easily measurable at the lower standard pressure differentials.

Standard Test Methods

The applicable laboratory test method for determining the rate of air leakage is ASTM E283, “Standard Test Method for Determining Rate of Air Leakage Through Exterior Windows, Curtain Walls, and Doors Under Specified Pressure Differences Across the Specimen.” If field testing for air leakage is to be conducted, the applicable test method is ASTM E783, “Standard Test Method for Field Measurement of Air Leakage Through Installed Exterior Windows and Doors.”

A-5.9.3.4.(3)   Systems Excluded from Air Leakage Requirements. The systems listed in Sentence 5.9.3.4.(3) perform different functions than other fenestration assemblies and are therefore exempted from complying with the air leakage requirements.

A-5.9.4.1.(1)   Exterior Insulation Finish Systems (EIFS). The reference to CAN/ULC-S716.1, “Standard for Exterior Insulation and Finish Systems (EIFS) - Materials and Systems,” in Clause 5.9.4.1.(1)(b) does not preclude the use of other component materials that may also meet the intent of the Code. For example, using mineral-fibre insulation in lieu of other rigid insulation types, mechanical fastening methods for the insulation component in lieu of adhesive, or a type of water-resistive barrier other than a liquid-applied water-resistive barrier could be acceptable.

The following two companion standards facilitate the application of and conformance with CAN/ULC-S716.1:

•   CAN/ULC-S716.2, “Standard for Exterior Insulation and Finish Systems (EIFS) - Installation of EIFS Components and Water Resistive Barrier,” and

•   CAN/ULC-S716.3, “Standard for Exterior Insulation and Finish System (EIFS) - Design Application.”

Additional information on EIFS design and installation can be found in the EIFS Council of Canada's “EIFS Practice Manual” and the manufacturer's literature.

EIFS Selection

CAN/ULC-S716.1 provides minimum performance criteria for EIFS materials and systems that are tested under specific laboratory test protocols identified in the standard. However, compliance with this standard does not ensure that a system is appropriate for all projects. When selecting an EIFS product, designers should consider all relevant criteria—not only those covered by the tests in CAN/ULC-S716.1—including, but not limited to,

•   building exposure

•   local climate characteristics (wind, precipitation, temperature variations, solar exposure)

•   intended building use

•   intended resistance to damage and deterioration

•   construction tolerances

•   constructability

Design and Construction of EIFS Drainage Cavity

The drainage capacity and thermal performance of the EIFS assembly can be affected by the dimensions and configuration of the EIFS drainage cavity.

EIFS are installed over other building materials such as sheathing and primary structural components, which have various construction installation tolerances. Designers should take into consideration the cumulative effects of construction tolerances and sequencing when specifying the drainage method and the cavity dimensions and configuration in order to ensure adequate drainage.

Designers should also take into account the impact of air movement, which varies depending on cavity size and the extent of venting, on the EIFS' thermal performance when reviewing the overall thermal performance of the building envelope. ASTM C1363, “Standard Test Method for Thermal Performance of Building Materials and Envelope Assemblies by Means of a Hot Box Apparatus,” presents one method for assessing the thermal performance of assemblies.

Part 6

Heating, Ventilating and Air-conditioning

Section  6.1.   General

6.1.1. Application

6.1.1.1. Scope

1)   The scope of this Part shall be as described in Subsection 1.3.3. of Division A.

6.1.1.2. Application

1)   This Part applies to systems and equipment for heating, ventilating and air-conditioning services.

6.1.2. Definitions

6.1.2.1. Defined Terms

1)   Words that appear in italics are defined in Article 1.4.1.2. of Division A.

6.1.3. Plans and Specifications

6.1.3.1. Required Plans and Specifications

1)   Plans, specifications and other information for heating, ventilating and air-conditioning systems shall conform to Subsection 2.2.6. of Division C.

Section  6.2.   Planning

6.2.1. General

6.2.1.1. Good Engineering Practice

(See Note A-6.2.1.1.)

1)   Heating, ventilating and air-conditioning systems, including mechanical refrigeration equipment, shall be designed, constructed and installed in conformance with good engineering practice such as that described in, but not limited to,

a)   the ASHRAE Handbooks and Standards,

b)   the HRAI Digest,

c)   the Hydronics Institute Manuals,

d)   the NFPA Standards,

e)   the SMACNA Manuals,

f)   the ACGIH manual entitled “Industrial Ventilation: A Manual of Recommended Practice for Design,”

g)   CSA B214, “Installation code for hydronic heating systems,”

h)   CAN/CSA-Z317.2, “Special requirements for heating, ventilation, and air-conditioning (HVAC) systems in health care facilities,”

i)   EPA 625/R-92/016, “Radon Prevention in the Design and Construction of Schools and Other Large Buildings,” and

j)   ASHRAE Guideline 12, “Minimizing the Risk of Legionellosis Associated with Building Water Systems.”

2)   Indoor design temperatures for residential buildings shall be those established in Article 9.33.3.1.

6.2.1.2. Outdoor Design Conditions

1)   The outdoor conditions to be used in designing heating, ventilating and air-conditioning systems shall be determined in conformance with Subsection 1.1.3. (See Note A-6.2.1.2.(1).)

2)   Reserved

3)   Reserved

6.2.1.3. Expansion, Contraction and System Pressure

1)   Heating and cooling systems shall be designed to allow for expansion and contraction of the heat transfer fluid and to maintain the system pressure within the rated working pressure limits of all components of the system.

6.2.1.4. Structural Movement

(See Note A-6.2.1.4.)

1)   Mechanical systems and equipment shall be designed and installed to accommodate the maximum relative structural movement provided for in the construction of the building.

6.2.1.5. Installation Standards

1)   Except as provided in Articles 6.9.4.2. and 6.3.1.4., the installation of heating and air-conditioning equipment, including mechanical refrigeration equipment, and including provisions for mounting, clearances and air supply, shall conform to the Safety Standards Act and pursuant regulations.

2) A solid-fuel burning boiler accepted for use under section 10 of the Safety Standards Act satisfies section 4.1 of CAN/CSA-B365, “Installation Code for Solid-Fuel-Burning Appliances and Equipment.”

6.2.1.6. Installation – General

1)   Equipment requiring periodic maintenance and forming part of a heating, ventilating or air-conditioning system shall be installed with provision for access for inspection, maintenance, repair and cleaning. (See Note A-6.2.1.6.(1).)

2)   Mechanical equipment shall be provided with guards so as to prevent injury.

3)   Heating, ventilating or air-conditioning systems shall be protected from freezing if they may be adversely affected by freezing temperatures.

6.2.1.7. Asbestos

1)   Asbestos shall not be used in HVAC systems and equipment.

6.2.2. Incinerators

6.2.2.1. Applicable Standard

1)   The design, construction, installation and alteration of every indoor incinerator shall conform to NFPA 82, “Standard on Incinerators and Waste and Linen Handling Systems and Equipment.”

6.2.3. Solid Fuel Storage

6.2.3.1. Solid Fuel Storage Bins

1)   A storage bin for solid fuel shall not be located above a sewer opening or drain opening.

2)   Storage bins for solid fuel shall be designed and constructed so that the air temperature in the bin or the surface temperature of any part of the floor or walls is below 50°C.

Section  6.3.   Ventilation Systems

6.3.1. Ventilation

6.3.1.1. Required Ventilation

1)   Except as provided in Sentence (4), all buildings shall be ventilated in accordance with this Section.

2)   Except in storage garages covered by Article 6.3.1.3., outdoor air shall be supplied to buildings for ventilation purposes in accordance with one of the following Sections of ANSI/ASHRAE 62.1, “Ventilation for Acceptable Indoor Air Quality,” as a minimum:

a)   Section 6.2, Ventilation Rate Procedure, excluding the exception stated in Section 6.2.7.1.2 and note H of Table 6.2.2.1,

b)   Section 6.3, Indoor Air Quality Procedure, or

c)   Section 6.4, Natural Ventilation Procedure, excluding residential occupancies.

3)   Except in storage garages covered by Article 6.3.1.3., exhaust ventilation shall be provided in accordance with Section 6.5, Exhaust Ventilation, of ANSI/ASHRAE 62.1, “Ventilation for Acceptable Indoor Air Quality,” as a minimum.

4)   Self-contained heating-season mechanical ventilation systems serving only one dwelling unit shall comply with Subsection 9.32.3.

5)   For suites in buildings conforming to Subsection 9.36.6. or 10.2.3., the outdoor air required by Sentence (2) shall be supplied directly to each suite by mechanical ventilation through ducting.  (See Note A-6.3.1.1.(5).)

6.3.1.2. Crawl Spaces and Attic or Roof Spaces

1)   Unconditioned and unoccupied crawl spaces and attic or roof spaces shall be ventilated by natural or mechanical means as required by Part 5. (See Note A-6.3.1.2.(1).)

6.3.1.3. Ventilation of Storage Garages

1)   Except as provided in Sentences (4) and (6), an enclosed storage garage for five or more motor vehicles shall have a mechanical ventilation system designed to

a)   limit the concentration of carbon monoxide to not more than 100 parts per million parts of air,

b)   limit the concentration of nitrogen dioxide to not more than 3 parts per million parts of air, where the majority of the vehicles stored are powered by diesel-fuelled engines, or

c)   provide, during operating hours, a continuous supply of outdoor air at a rate of not less than 3.9 L/s for each square metre of floor area (see Article 3.3.1.21.).

(See Note A-6.3.1.3.(1).) (See also Sentence 3.3.5.4.(4).)

2)   Mechanical ventilation systems provided in accordance with Clause (1)(a) shall be controlled by carbon monoxide monitoring devices, and systems provided in accordance with Clause (1)(b) shall be controlled by nitrogen dioxide or other acceptable monitoring devices. (See Note A-6.3.1.3.(2).)

3)   Mechanical ventilation systems provided in accordance with Sentence (1) shall be designed such that the pressure in the storage garage is less than the pressure in adjoining buildings of other occupancy, or in adjacent portions of the same building having a different occupancy.

4)   In storage garages subject to the requirements of Sentences (1) and (2), where motor vehicles are parked by mechanical means, the ventilation requirements may be reduced by one half.

5)   Except as provided in Sentence (6), ticket and attendant booths of storage garages shall be pressurized with a supply of uncontaminated air.

6)   The requirements of Sentences (1) to (5) shall not apply to open-air storeys in a storage garage.

6.3.1.4. Heat Recovery Ventilators

1)   Heat recovery ventilators with rated capacities of not less than 25 L/s and not more than 200 L/s shall be installed in accordance with Subsection 9.32.3.

6.3.1.5. Indoor Air Contaminants

(See Note A-6.3.1.5.)

1)   Air contaminants of concern within buildings shall

a)   be removed insofar as is possible at their points of origin, and

b)   not be permitted to accumulate in concentrations greater than those permitted by applicable provincial or territorial requirements or, in the absence of such requirements, by good engineering practice such as that described in the publications listed in Sentence 6.2.1.1.(1), measured using the methodology described therein.

2)   Systems serving spaces that contain sources of contamination and systems serving other occupied parts of the building but located in or running through spaces that contain sources of contamination shall be designed in such a manner as to prevent the spread of such contamination to other occupied parts of the building.

3)   Heating, ventilating and air-conditioning systems shall be designed to minimize the growth and spread of bio-contaminants.

6.3.1.6. Commercial Cooking Equipment

1)   Except as provided in Article 3.6.3.5., systems for the ventilation of commercial cooking equipment shall be designed, constructed and installed to conform to NFPA 96, “Standard for Ventilation Control and Fire Protection of Commercial Cooking Operations.”

6.3.2. Air Duct Systems

6.3.2.1. Application

1)   This Subsection applies to the design, construction and installation of air duct distribution systems serving heating, ventilating and air-conditioning systems other than those in dwelling units covered by Part 9.

6.3.2.2. Drain Pans

(See Note A-6.3.2.2.)

1)   HVAC systems that generate condensate or introduce liquid water into the airstream in the ducts shall be equipped with drain pans that are

a)   designed in accordance with Section 5.10, Drain Pans, of ANSI/ASHRAE 62.1, “Ventilation for Acceptable Indoor Air Quality,”

b)   provided with an outlet that is piped to the outside of the airstream in a location where condensate can be safely disposed of,

c)   installed so that water does not stagnate and drains from the pan, and

d)   designed and installed so as to be accessible for cleaning and maintenance.

2)   Drain pans and associated piping shall be constructed of corrosion-resistant, non-porous materials that do not promote the proliferation of disease-causing micro-organisms.

6.3.2.3. Materials in Air Duct Systems

1)   All ducts, duct connectors, associated fittings and plenums used in air duct systems shall be constructed of materials as described in Article 3.6.5.1.

2)   Ducts that are used in a location where they may be subjected to excessive moisture shall have no appreciable loss of strength when wet and shall be resistant to moisture-induced corrosion.

3)   All ductwork and fittings shall be constructed and installed as recommended in SMACNA Manuals and ASHRAE Standards.

4)   All duct materials shall be suitable for exposure to the temperature and humidity of the air being carried and shall be resistant to corrosion caused by contaminants in the air being conveyed in the duct.

6.3.2.4. Connections in Air Duct Systems

1)   Air duct systems shall have tight-fitting connections throughout.

6.3.2.5. Duct Coverings and Linings

(See Note A-6.3.2.5.)

1)   Coverings, linings and associated adhesives and insulation used in air ducts, plenums and other parts of air duct systems shall comply with Article 3.6.5.4.

2)   Duct linings shall be installed so that they will not interfere with the operation of volume or balancing dampers or of fire dampers, fire stop flaps and other closures.

6.3.2.6. Clearance of Ducts and Plenums

1)   The clearance of ducts and plenums from combustible materials shall comply with Article 3.6.5.6.

6.3.2.7. Interconnection of Systems

1)   In a care or residential occupancy, air from one suite shall not be circulated to any other suite or to a public corridor.

2)   Except as permitted by Sentences (3) and 6.3.2.10.(6), air duct systems serving storage garages shall not be directly interconnected with other parts of the building.

3)   Exhaust ducts referred to in Sentence 6.3.2.10.(10) are permitted to exhaust through an enclosed storage garage prior to exhausting to the outdoors, provided

a)   the storage garage's exhaust system runs continuously,

b)   the capacity of the storage garage's exhaust system is equal to or exceeds the volume of the exhaust entering the garage, and

c)   a leakage rate 1 smoke/fire damper rated in accordance with CAN/ULC-S112.1, “Standard for Leakage Rated Dampers for Use in Smoke Control Systems,” is provided near the duct outlet location in the storage garage to prevent air from the storage garage from entering the exhaust ductwork system in the event the building's exhaust fan is shut down.

6.3.2.8. Makeup Air

(See Note A-6.2.1.1.)

1)   In ventilating systems that exhaust air to the outdoors, provision shall be made for the admission of a supply of makeup air in sufficient quantity so that the operation of the exhaust system and other exhaust equipment or combustion equipment is not adversely affected.

2)   Makeup air facilities required by Sentence (1) shall be interlocked with the exhaust devices they serve so that both operate together.

3)   Where makeup air facilities are intended to introduce air directly from the outdoors to occupied parts of the building in winter, they shall incorporate means of tempering that air to maintain the indoor design temperature.

6.3.2.9. Supply, Return, Intake and Exhaust Air Openings

1)   Supply, return and exhaust air openings located less than 2 m above the floor in rooms or spaces in buildings shall be protected by grilles having openings of a size that will not allow the passage of a 15 mm diam sphere.

2)   Outdoor air intakes shall be located so that

a)   the quality of the air entering the building complies with Sentences 6.2.1.2.(2) and (3), and

b)   they are separated a minimum distance from sources of contaminants in accordance with Table 6.3.2.9.

Table 6.3.2.9.

Minimum Distances of Air Intakes from Sources of Contaminants

Forming Part of Sentence 6.3.2.9.(2)

| Source of Contaminants | Minimum Distance of Outdoor Air Intake, m |
| --- | --- |
| Garage entry of a garage for 5 or more motor vehicles, automobile loading area and drive-in queue | 4.5 |
| Truck loading area or dock, and bus parking | 7.6 |
| Driveway, street, and parking space | 1.5 |
| Thoroughfare, arterial road, freeway, and highway | 7.6 |
| Garbage storage/pick-up area and dumpsters | 4.5 |
| Discharge from evaporative heat rejection systems | 7.6 |
| Sanitary vent | 3.5 |
| Kitchen cooking exhaust | 3.0 |
| Vent for combustion products | 3.0 |

3)   Outdoor air intakes shall be installed not less than 0.3 m above roofs, landscape grades or other surfaces, taking into account anticipated snow accumulation levels.

4)   Exterior openings for outdoor air intakes and exhaust outlets shall be shielded from the entry of snow and rain and shall be fitted with corrosion-resistant screens of mesh having openings not larger than 15 mm, except where experience has shown that climatic conditions require larger openings to prevent the screen openings from icing over.

5)   Screens required in Sentence (4) shall be accessible for maintenance.

6)   Combustible grilles, diffusers and other devices covering supply, return, intake and exhaust openings shall comply with Article 3.6.5.7.

6.3.2.10. Exhaust Ducts and Outlets

1)   Except as provided in Sentence (2), exhaust ducts of non-mechanical ventilating systems serving separate rooms or spaces shall not be combined.

2)   Exhaust ducts of non-mechanical ventilating systems serving similar occupancies may be combined immediately below the point of final delivery to the outdoors, such as at the base of a roof ventilator.

3)   Exhaust ducts of ventilating systems shall have provision for the removal of condensation where this may be a problem.

4)   Exhaust outlets shall be designed to prevent backdraft under wind conditions.

5)   Except as permitted in Sentence (6), exhaust systems shall discharge directly to the outdoors. (See Note A-6.3.2.10.(5) and (6).)

6)   Exhaust systems are permitted to exhaust into a storage garage, provided

a)   they serve rooms that are accessible only from that storage garage,

b)   the exhaust contains no contaminants that would adversely affect the air quality in the storage garage (see Note A-6.3.2.10.(6)(b)), and

c)   they are designed in accordance with Sentence 6.3.2.7.(3).

(See Note A-6.3.2.10.(5) and (6).)

7)   Exhaust ducts connected to laundry-drying equipment shall be

a)   independent of other exhaust ducts,

b)   accessible for inspection and cleaning, and

c)   constructed of a smooth corrosion-resistant material.

(See Note A-6.3.2.10.(7) and (8).)

8)   Where collective venting of multiple installations of laundry-drying equipment is used, the ventilation system shall

a)   be connected to a common exhaust duct that is vented by one central exhaust fan,

b)   include an interlock to activate the central exhaust fan when laundry-drying equipment is in use, and

c)   be provided with make-up air.

(See Note A-6.3.2.10.(7) and (8).)

9)   Exhaust ducts or vents connected to laundry-drying equipment shall discharge directly to the outdoors.

10)   Except as provided in Sentence (12) and except for self-contained systems serving individual dwelling units, exhaust ducts serving rooms containing water closets, urinals, basins, showers or slop sinks shall be independent of other exhaust ducts.

11)   Except as provided in Sentence (12) and except for self-contained systems serving individual dwelling units, exhaust ducts serving rooms containing residential cooking equipment shall be independent of other exhaust ducts.

12)   Two or more exhaust systems described in Sentences (10) and (11) may be interconnected or connected with exhaust ducts serving other areas of the building, provided

a)   the connections are made at the inlet of an exhaust fan, and all interconnected systems are equipped with suitable back pressure devices to prevent the passage of odours from one system to another when the fan is not in operation, or

b)   the exhaust ducts discharge to a shaft that is served by an exhaust fan having a capacity that is equal to or greater than the combined capacity of the exhaust fans discharging to the plenum multiplied by the operation diversity factor, provided that the exhaust fan serving the shaft operates continuously (see Note A-6.3.2.10.(12)(b)).

13)   Where exhaust ducts containing air from conditioned spaces pass through or are adjacent to unconditioned spaces, the ducts shall be constructed to prevent condensation from forming on the inside or outside of the ducts.

6.3.2.11. Return-Air System

1)   Return-air systems shall comply with Article 3.6.5.8.

2)   Where a ceiling space is used as a return-air plenum, the requirements of Article 3.6.4.3. shall apply.

3)   A public corridor or exit shall not be used as a return-air plenum.

6.3.2.12. Underground Ducts

1)   Underground ducts shall

a)   be constructed and installed to provide interior drainage from and access to all low points,

b)   not be connected directly to a sewer, and

c)   be installed and constructed of materials recommended by ASHRAE and SMACNA Standards and HRAI Manuals.

2)   A clean-out or pump-out connection shall be provided in an underground duct system at every low point of the duct system.

6.3.2.13. Filters

1)   Air filters for air duct systems shall conform to the requirements for Class 2 air filter units as described in CAN/ULC-S111, “Standard Method of Fire Tests for Air Filter Units.”

2)   When electrostatic-type filters are used, they shall be installed so as to ensure that the electric circuit is automatically de-energized when filter access doors are opened or, in dwelling units, when the furnace circulation fan is not operating.

6.3.2.14. Reserved

6.3.2.15. Evaporative Heat Rejection Systems

1)   Evaporative heat rejection systems shall

a)   incorporate a drift eliminator or other means to minimize the dispersion of entrained water droplets, and

b)   have a design discharge velocity that does not exceed the maximum discharge velocity recommended by the manufacturer.

2)   Evaporative heat rejection systems shall be designed so that water continuously circulates through all parts of the system that are normally wetted when the system is operating.

3)   Evaporative heat rejection systems and their components shall be constructed of corrosion-resistant, non-porous materials that do not promote the proliferation of disease-causing micro-organisms and that are compatible with disinfectants, biocides and other cleaning agents.

4)   Evaporative heat rejection systems shall be installed such that

a)   no discharge air bypasses the drift eliminator or other means referred to in Clause (1)(a), and

b)   the systems are accessible for cleaning, inspection and maintenance.

5)   Except as provided in Sentence (6), air discharged from evaporative heat rejection systems shall discharge away from the building, so as to not re-enter it, to a distance not less than

a)   2.15 m above sidewalks and driveways,

b)   7.6 m from outdoor air intakes,

c)   3 m horizontally or vertically from exterior doors and operable windows, and

d)   3 m horizontally or vertically from occupiable outdoor spaces, excluding maintenance spaces.

(See Note A-6.3.2.15.(5) and (6).)

6)   Air discharged from evaporative heat rejection systems in health care facilities shall discharge away from the building in compliance with CAN/CSA-Z317.2, “Special requirements for heating, ventilation, and air-conditioning (HVAC) systems in health care facilities.” (See Note A-6.3.2.15.(5) and (6).)

7)   Air intakes of evaporative heat rejection systems shall incorporate protective measures to minimize the entrainment of vegetation and other organic matter.

8)   Make-up water connections shall be equipped with backflow prevention devices that conform to Article 2.6.2.1. of Division B of Book II, (Plumbing Systems), of this code. (See Note A-6.3.2.15.(8) and (9).)

9)   Water treatment systems and equipment for controlling the proliferation of disease-causing micro-organisms shall

a)   be provided in accordance with Section 7.6.2. of ASHRAE Guideline 12, “Minimizing the Risk of Legionellosis Associated with Building Water Systems,” and

b)   include means for drainage, dilution, cleaning, and application of chemicals for the control of scale, corrosion and biological contamination.

(See Note A-6.3.2.15.(8) and (9).)

10)   Drains, overflows and blow-downs shall be connected to the building's drainage system in accordance with Clause 2.4.2.1.(1)(e) of Division B of Book II, (Plumbing Systems), of this code.

11)   Evaporative heat rejection systems shall be provided with access openings, service platforms, fixed ladders and fall-restraint connections to allow inspection, maintenance and testing.

6.3.2.16. Evaporative Air Coolers, Misters, Atomizers, Air Washers and Humidifiers

1)   Evaporative air coolers, misters, atomizers, air washers and humidifiers shall be designed in accordance with Sections 8 and 9 of ASHRAE Guideline 12, “Minimizing the Risk of Legionellosis Associated with Building Water Systems.”

2)   Systems referred to in Sentence (1) shall

a)   be designed so that water continuously circulates through all parts of the system that are normally wetted when the system is operating, and

b)   incorporate a method of preventing water stagnation within the system itself and the internal plumbing when the system is not operating.

(See Note A-6.3.2.16.(2).)

3)   All components of systems referred to in Sentence (1), including filters and evaporation media, shall be constructed of corrosion-resistant, non-porous materials that do not promote the proliferation of disease-causing micro-organisms.

4)   Associated sumps shall

a)   be constructed of corrosion-resistant, non-porous materials that do not promote the proliferation of disease-causing micro-organisms,

b)   include auxiliary drains to prevent the overflow of water into ductwork, and

c)   be installed so that they can be flushed, drained, cleaned and disinfected.

5)   Where misters, atomizers or air washers are used in ductwork, the affected duct section shall be

a)   designed to ensure drainage of unevaporated and accumulated water, and

b)   constructed of corrosion-resistant, non-porous materials that do not promote the proliferation of disease-causing micro-organisms.

6)   Make-up water connections shall be equipped with backflow prevention devices that conform to Article 2.6.2.1. of Division B of Book II, (Plumbing Systems), of this code. (See Note A-6.3.2.16.(6).)

6.3.2.17. Fans and Associated Air-Handling Equipment

1)   Fans for heating, ventilating and air-conditioning systems shall be located and installed so that their operation

a)   does not adversely affect the draft required for proper operation of fuel-fired appliances, and

b)   does not allow the air in the duct system to be contaminated by air or gases from the boiler room or furnace room.

2)   Fans and associated air-handling equipment, such as air washers, filters and heating and cooling units, when installed on the roof or elsewhere outside the building, shall be of a type designed for outdoor use.

6.3.2.18. Vibration Isolation Connectors

1)   Vibration isolation connectors in air duct systems shall comply with Article 3.6.5.2.

6.3.2.19. Tape

1)   Tape used for sealing joints in air ducts, plenums and other parts of air duct systems shall comply with Article 3.6.5.3.

6.3.3. Chimneys and Venting Equipment

6.3.3.1. Requirement for Venting

1)   Except as provided in Articles 6.3.3.2. and 6.3.3.3., the products of combustion from oil-, gas- and solid-fuel-burning appliances shall be vented in conformance with the requirements in the applicable appliance installation standard listed in Article 6.2.1.5.

2)   Except as provided in Article 6.2.1.5., vented products of combustion, other than those referred to in Sentence (1), shall be discharged away from the building, so as not to re-enter it, to a distance not less than

a)   2.15 m above sidewalks and driveways,

b)   3 m from outdoor air intakes,

c)   3 m horizontally or vertically from doors and operable windows, and

d)   3 m horizontally or vertically from occupiable outdoor spaces, excluding maintenance spaces.

(See Note A-6.3.3.1.(2).)

6.3.3.2. Masonry or Concrete Chimneys

1)   Rectangular masonry or concrete chimneys not more than 12 m in height shall conform to Part 9 if they serve

a)   appliances with a combined total rated heat output of 120 kW or less, or

b)   fireplaces.

2)   Masonry or concrete chimneys other than those described in Sentence (1) shall be designed and installed in conformance with the appropriate requirements in NFPA 211, “Standard for Chimneys, Fireplaces, Vents, and Solid Fuel-Burning Appliances.”

6.3.3.3. Metal Smoke Stacks

1)   Single wall metal smoke stacks shall be designed and installed in conformance with NFPA 211, “Standard for Chimneys, Fireplaces, Vents, and Solid Fuel-Burning Appliances.”

6.3.3.4. Access Ladders

1)   Access ladders for chimneys, when provided, shall consist of steel or bronze rungs, built into the walls of the chimneys.

2)   Rungs for external ladders shall begin at not less than 2.5 m from ground level.

6.3.4. Ventilation for Laboratories

6.3.4.1. Application

1)   This Subsection applies to laboratories where dangerous goods, including flammable liquids and combustible liquids, are used in normal laboratory operations in quantities or in a manner that creates a fire or explosion hazard.

6.3.4.2. General Ventilation

1)   A laboratory shall be provided with continuous mechanical ventilation designed to ensure that dangerous goods vapours and particles

a)   do not accumulate in the laboratory,

b)   are prevented from migrating to other parts of the building,

c)   do not accumulate in the ventilation system,

d)   are exhausted to the outdoors, and

e)   are not returned to the building.

2)   A ventilation system required by this Subsection shall be provided with monitoring devices to

a)   indicate that the ventilation system is in operation, and

b)   sound an alarm if the ventilation system is malfunctioning.

3)   A ventilation system required by this Subsection shall be maintained in conformance with Article 5.5.4.1. of Division B of the British Columbia Fire Code.

6.3.4.3. Enclosure Exhaust Ventilation

1)   The ventilation system for a power-ventilated enclosure required by Sentence 5.5.4.2.(1) of Division B of the British Columbia Fire Code shall

a)   conform to NFPA 91, “Standard for Exhaust Systems for Air Conveying of Vapors, Gases, Mists, and Particulate Solids,”

b)   provide continuous exhaust ventilation at an air velocity sufficient to prevent the accumulation of combustible or reactive deposits in the power-ventilated enclosure and its exhaust duct system,

c)   confine dangerous goods vapours and particles to the area where they are generated and exhaust them to the outdoors,

d)   not return the exhausted air to the building, and

e)   be provided with well identified control switches that are

i)   located outside of the power-ventilated enclosure, and

ii)   readily accessible in case of an emergency.

6.3.4.4. Enclosure Construction

1)   The power-ventilated enclosure required by Sentence 5.5.4.2.(1) of Division B of the British Columbia Fire Code and its exhaust duct system shall

a)   except as provided in Sentences (2) and (3), be constructed of noncombustible materials compatible with and chemically resistant to the dangerous goods vapours and particles being exhausted, and

b)   be provided with access doors to permit inspection and maintenance of the fan assembly and exhaust ducts.

2)   Combustible materials are permitted in systems described in Clause (1)(a) if

a)   such materials are required by the corrosive or reactive properties of the dangerous goods being used, and

b)   their flame-spread rating is not more than 25.

3)   The flame-spread rating required by Sentence (2) is permitted to be greater than 25 if an automatic fire suppression system is provided inside the power-ventilated enclosure and its exhaust duct system.

Section  6.4.   Heating Systems

6.4.1. Heating Appliances, General

6.4.1.1. Location of Appliances

1)   Except for appliances installed in dwelling units, fuel-fired heating appliances shall be located, enclosed or separated from the remainder of the building in conformance with Section 3.6. (See also Subsection 9.10.10.)

6.4.1.2. Appliances Installed Outside the Building

1)   Fuel-fired appliances installed outside a building shall be designed and constructed for outdoor use.

6.4.2. Unit Heaters

6.4.2.1. Clearances

1)   Every unit heater using either steam or hot water as the heating medium shall be installed such that the clearances between the appliance and adjacent combustible material conform to Table 6.7.1.2.

6.4.3. Radiators and Convectors

6.4.3.1. Lining or Backing

1)   A noncombustible lining or backing shall be provided for every steam or hot water radiator and convector

a)   located in a recess or concealed space, or

b)   attached to the face of a wall of combustible construction or encapsulated mass timber construction.

2)   Every steam or hot water radiator and convector shall be installed so as to conform to the clearance requirements of Table 6.7.1.2.

Section  6.5.   Thermal Insulation Systems

6.5.1. Insulation

6.5.1.1. Insulation and Coverings

(See Note A-6.3.2.5.)

1)   Insulation and coverings on pipes shall comply with Article 3.6.5.5.

2)   Insulation and coverings on pipes shall be composed of material that will withstand deterioration from softening, melting, mildew and mould at the operating temperature of the system.

3)   Exposed piping or equipment subject to human contact shall be insulated so that the temperature of the exposed surface does not exceed 52°C. (See Note A-6.5.1.1.(3).)

Section  6.6.   Refrigeration and Cooling Systems

6.6.1. Refrigerating Systems and Equipment for Air-conditioning

6.6.1.1. Cooling Units

1)   Where a cooling unit is combined with a fuel-fired furnace in the same duct system, the cooling unit shall be installed

a)   in parallel with the heating furnace,

b)   upstream of the furnace provided the furnace is designed for such application, or

c)   downstream of the furnace provided the cooling unit is designed to prevent excessive temperature or pressure in the refrigeration system.

Section  6.7.   Piping Systems

6.7.1. Piping for Heating and Cooling Systems

6.7.1.1. Piping Materials and Installation

1)   Piping shall be made from materials designed to withstand the effects of temperatures and pressures that may occur in the system. (See Articles 3.1.5.19., 3.1.9.1., 9.10.9.6. and 9.10.9.7. for fire safety requirements.)

2)   Every pipe used in a heating or air-conditioning system shall be installed to allow for expansion and contraction due to temperature changes.

3)   Supports and anchors for piping in a heating or air-conditioning system shall be designed and installed to ensure that undue stress is not placed on the supporting structure.

6.7.1.2. Clearances

1)   Clearances between combustible material and bare pipes carrying steam or hot water shall conform to Table 6.7.1.2.

Table 6.7.1.2.

Clearance Between Steam or Hot Water Pipes and Combustible Material

Forming Part of Articles 6.4.2.1. and 6.7.1.2., and Sentence 6.4.3.1.(2)

| Steam or Water Temperature, °C | Minimum Clearance, mm |
| --- | --- |
| Up to 95 | No clearance |
| Above 95 to 120 | 15 |
| Above 120 | 25 |

6.7.1.3. Surface Temperature

1)   The exposed surface temperature of a steam or hot water radiator shall not exceed 70°C unless precautions are taken to prevent human contact. (See Note A-6.5.1.1.(3).)

6.7.1.4. Protection

1)   Where a pipe carrying steam or hot water at a temperature above 120°C passes through a combustible floor, ceiling or wall, the construction shall be protected by a sleeve of metal or other noncombustible material not less than 50 mm larger in diameter than the pipe.

6.7.1.5. Piping in Shafts

1)   Where piping for heating or air-conditioning systems is enclosed in a shaft, the requirements of Article 3.6.3.1. for shafts shall apply.

6.7.2. Storage Bins

6.7.2.1. Storage Bins

1)   Service pipes passing through a storage bin for solid fuel shall be protected or so located as to avoid damage to the pipes.

2)   Except for fuel-thawing pipes, every pipe designed to operate at a temperature of 50°C or above shall be located where solid fuel cannot be stored in contact with it.

Section  6.8.   Equipment Access

6.8.1. Openings

6.8.1.1. Access Openings

1)   Any covering of an access opening through which a person could enter shall be openable from the inside without the use of keys where there is a possibility of the opening being accidentally closed while the system or equipment is being serviced.

6.8.1.2. Openings in Air Duct Systems

1)   Air duct systems shall have no openings other than those required for the proper operation and maintenance of the system.

2)   Access openings shall be provided in duct systems to allow the removal of material that may accumulate in plenums and ducts.

6.8.1.3. Odour Removal Equipment

1)   When odour removal equipment of the adsorption type is used, it shall be

a)   installed to allow access so that adsorption material can be reactivated or renewed, and

b)   protected from dust accumulation by air filters installed on the inlet side.

2)   Facilities for flushing and drainage shall be provided where filters are designed to be washed in place.

Section  6.9.   Fire Safety Systems

6.9.1. General

6.9.1.1. Fire Safety Requirements

1)   The fire safety characteristics of heating, ventilating and air-conditioning systems shall comply with Subsection 3.6.5.

2)   Characteristics referred to in Sentence (1) include but are not limited to

a)   use of combustible materials in duct systems,

b)   flame-spread ratings and smoke-developed ratings of duct and pipe materials and coverings,

c)   installation of equipment relative to property lines, and

d)   requirements for fire dampers and fire stop flaps.

6.9.1.2. Hazardous Gases, Dusts or Liquids

1)   Except as provided in Subsection 6.3.4., systems serving spaces that contain hazardous gases, dusts or liquids shall be designed, constructed and installed to conform to the requirements of the applicable provincial or territorial regulations or municipal bylaws or, in the absence of such regulations or bylaws, to good engineering practice such as that described in the publications of the National Fire Protection Association and in the British Columbia Fire Code. (See Note A-6.9.1.2.(1).)

2)   When indoor piping for Class I flammable liquids is installed in a trench, the trench shall be

a)   provided with positive ventilation to the outdoors, or

b)   designed to prevent the accumulation of flammable vapours.

6.9.1.3. Commercial Cooking Equipment

1)   Fire protection systems for commercial cooking equipment referred to in Sentence 6.3.1.6.(1) using vegetable oil or animal fat shall conform to

a)   ANSI/CAN/UL/ULC 300, “Standard for Fire Testing of Fire Extinguishing Systems for Protection of Commercial Cooking Equipment,” or

b)   ULC/ORD-C1254.6, “Fire Testing of Restaurant Cooking Area Fire Extinguishing System Units.”

6.9.2. Dampers and Ductwork

6.9.2.1. Fire Dampers

1)   Fire dampers shall conform to Article 3.1.8.10.

6.9.2.2. Smoke Detectors

1)   Air handling systems shall incorporate smoke detectors where and as required by Article 3.2.4.12.

6.9.2.3. Exhaust Ducts and Outlets

1)   Where an exhaust duct system is used for smoke removal in a high building, the requirements of Article 3.2.6.6. shall apply.

2)   Where exhaust duct systems from more than one fire compartment are connected to an exhaust duct in a vertical service space, the requirements of Article 3.6.3.4. shall apply.

6.9.2.4. Ducts in Exits

1)   Where ducts penetrate fire separations separating exits from the remainder of the building, they shall be in accordance with Article 3.4.4.4.

6.9.3. Carbon Monoxide Alarms

6.9.3.1. Carbon Monoxide Alarms

1)   This Article applies to every building that contains an assembly occupancy, a care occupancy with individual suites or containing sleeping rooms or bed spaces not within a suite, a residential occupancy, a business and personal services occupancy, or a mercantile occupancy, and that

a)   is served by or contains a fuel-burning appliance, or

b)   contains a storage garage.

2)   Carbon monoxide (CO) alarms installed in a residential occupancy or a care occupancy as required by this Article shall

a)   conform to CSA 6.19, “Residential carbon monoxide alarming devices,”

b)   be equipped with an integral alarm that satisfies the audibility requirements of CSA 6.19, “Residential carbon monoxide alarming devices,”

c)   have no disconnect switch between the overcurrent device and the CO alarm, where the CO alarm is powered by the electrical system serving the suite (see Note A-6.9.3.1.(2)(c)), and

d)   be installed as recommended by the manufacturer.

3)   Except as permitted by Sentence (9), where a fuel-burning appliance is installed in a suite of residential occupancy or in a suite of care occupancy, a CO alarm shall be installed

a)   inside each sleeping room or bed space, or

b)   outside each sleeping room or bed space, within 5 m of each  door serving a sleeping room or bed space, measured following corridors and doorways.

4)   Except as permitted by Sentence (9), where a fuel-burning appliance serves a residential occupancy or a care occupancy and is installed in a service room that is not in a suite of residential occupancy nor in a suite of care occupancy, a CO alarm shall be installed

a)   either inside each sleeping room or bed space, or if outside, within 5 m of each door serving a sleeping room or bed space, measured following corridors and doorways, in every suite of residential occupancy or suite of care occupancy that shares a wall or floor/ceiling assembly with the service room, and

b)   in the service room.

5)   Except as permitted by Sentence (9), for each suite of residential occupancy or suite of care occupancy that shares a wall or floor/ceiling assembly with a storage garage or that is adjacent to an attic or crawl space to which the storage garage is also adjacent, a CO alarm shall be installed

a)   inside each sleeping room or bed space, or

b)   outside each sleeping room or bed space, within 5 m of each bedroom door serving a sleeping room or bed space, measured following corridors and doorways.

6)   CO alarms installed in an assembly occupancy, a business and personal services occupancy, or a mercantile occupancy as required by this Article shall conform to

a)   CAN/CSA-6.19, “Residential Carbon Monoxide Alarming Devices,” notwithstanding the scope of that standard,

b)   UL 2034, “Standard for Single and Multiple Station Carbon Monoxide Alarms,” notwithstanding the scope of that standard, or

c)   good engineering practice. (See Note A-6.9.3.1.(6).)

7)   Except as permitted by Sentence (9), where a fuel-burning appliance serves an assembly occupancy, business and personal services occupancy, or mercantile occupancy, a CO alarm shall be,

a)   where the fuel-burning appliance is part of a system that could circulate or distribute CO to a suite of assembly occupancy, business and personal services occupancy or mercantile occupancy, installed

i)   on each storey of each suite that may be exposed, and

ii)   in a suite containing an assembly major occupancy, each classroom and dedicated gathering room or space, and

b)   installed in the room or space in which the fuel-burning appliance is located. (See Note A-6.9.3.1.(7).)

8)   Except as permitted by Sentence (9), for each suite of assembly occupancy, business and personal services occupancy, or mercantile occupancy that shares a wall or floor/ceiling assembly with either a storage garage or a service room containing a fuel-burning appliance, or that is adjacent to either an attic or crawl space to which the storage garage or a service room containing a fuel-burning appliance is also adjacent, a CO alarm shall be installed

a)   on each storey of the adjacent suite,

b)   where the adjacent suite contains an assembly major occupancy, each classroom and dedicated room or space, and

c)   in each service room containing a fuel-burning appliance. (See Note A-6.9.3.1.(8).)

9)   CO detectors are permitted to be installed in lieu of CO alarms required by this Article provided the CO detectors

a)   sound audible signals within the location they serve, as described in Sentences (3) to (5), (7) and (8),

b)   are installed in conformance with CAN/ULC-S524, “Installation of Fire Alarm Systems,” and

c) form part of the fire alarm system.

6.9.4. Ash Storage

6.9.4.1. Ash Storage Bins

1)   Every ash storage bin shall be constructed of noncombustible material.

2)   Every opening in an ash storage bin shall be protected by a tight-fitting metal door with metal frame securely fastened to the bin.

6.9.4.2. Fireplaces

1)   Fireplaces shall conform to the requirements of Section 9.22.

Section  6.10.   Objectives and Functional Statements

6.10.1. Objectives and Functional Statements

6.10.1.1. Attributions to Acceptable Solutions

1)   For the purpose of compliance with this Code as required in Clause 1.2.1.1.(1)(b) of Division A, the objectives and functional statements attributed to the acceptable solutions in this Part shall be the objectives and functional statements listed in Table 6.10.1.1. (See Note A-1.1.2.1.(1).)

Table 6.10.1.1.

Objectives and Functional Statements Attributed to the Acceptable Solutions in Part 6

Forming Part of Sentence 6.10.1.1.(1)

| Provision | Functional Statements and Objectives(1) |
| --- | --- |
| 6.2.1.1. Good Engineering Practice |  |
| (1) | (a) to (e) [F31,F51-OP1.1] |
|  | (a) to (c),(e) to (i) [F40,F50,F51,F52,F54,F63-OH1.1] |
|  | (a) to (c),(e) to (h) [F50,F51,F52,F54,F63-OH1.2,OH1.3] |
|  | [F31,F50,F51,F52,F54,F63-OS3.2,OS3.4] |
|  | (d) [F01-OS1.1] |
| 6.2.1.2. Outdoor Design Conditions |  |
| (2) | [F40,F50-OH1.1] |
| (3) | [F40,F43,F44,F50-OH1.1] |
|  | [F44-OS3.4] |
| 6.2.1.3. Expansion, Contraction and System Pressure |  |
| (1) | [F20-OS3.2] |
| 6.2.1.4. Structural Movement |  |
| (1) | [F23-OS3.1] |
|  | [F51,F63,F50-OH1.1,OH1.2,OH1.3] |
| 6.2.1.5. Installation Standards |  |
| (1) | [F43-OS1.1] |
|  | [F43-OS3.4] |
|  | [F43-OP1.1] |
| 6.2.1.6. Installation – General |  |
| (1) | [F82-OS1.1] |
|  | [F82-OS3.4] |
|  | [F82-OP1.1] |
| (2) | [F31-OS3.1] |
| (3) | [F81-OS3.2,OS3.3,OS3.4] |
|  | [F81-OS1.1] |
| 6.2.1.7. Asbestos |  |
| (1) | [F43-OH1.1] |
| 6.2.2.1. Applicable Standard |  |
| (1) | [F81-OS1.1] |
| 6.2.3.1. Solid Fuel Storage Bins |  |
| (1) | [F30-OH2.1] |
| (2) | [F01-OS1.1] |
|  | [F01-OP1.1] |
| 6.3.1.1. Required Ventilation |  |
| (2) | [F50,F41,F52,F53,F63-OH1.1] |
| (3) | [F40,F41,F50,F52,F53,F63-OH1.1] |
| (5) | [F50-OH1.1] |
| 6.3.1.2. Crawl Spaces and Attic or Roof Spaces |  |
| (1) | [F61,F63,F41-OH1.1,OH1.3] |
| 6.3.1.3. Ventilation of Storage Garages |  |
| (1) | [F50,F44-OS3.4] |
| (2) | [F44-OS3.4] |
| (3) | [F44-OS3.4] |
| (4) | [F50,F44-OS3.4] |
| (5) | [F50,F44-OH1.1] |
|  | [F50,F44-OS3.4] |
| 6.3.1.5. Indoor Air Contaminants |  |
| (1) | [F44-OS3.4] |
|  | [F44-OH1.1] |
| (2) | [F44-OH1.1] |
| (3) | [F52-OH1.1] |
| 6.3.1.6. Commercial Cooking Equipment |  |
| (1) | [F01,F44-OS1.1] |
|  | [F01,F44-OP1.1] |
| 6.3.2.2. Drain Pans |  |
| (1) | [F41,F44,F50,F82-OH1.1] |
| (2) | [F40,F41,F44,F50-OH1.1] |
| 6.3.2.3. Materials in Air Duct Systems |  |
| (2) | [F20,F80-OH1.1,OH1.2] |
| (3) | [F81,F44-OS3.4] |
|  | [F81-OH1.1] |
| (4) | [F20,F80-OH1.1,OH1.2] |
| 6.3.2.4. Connections in Air Duct Systems |  |
| (1) | [F81-OH1.1,OH1.2] |
|  | [F81,F44-OS3.4] |
| 6.3.2.5. Duct Coverings and Linings |  |
| (2) | [F81-OH1.1,OH1.2] |
|  | [F81-OS1.1] |
|  | [F81-OP1.1] |
| 6.3.2.7. Interconnection of Systems |  |
| (1) | [F44-OS1.1] |
|  | [F40-OH1.1] |
| (2) | [F81,F44-OH1.1] |
|  | [F81,F44-OS1.1] |
|  | [F81,F44-OP1.1] |
| (3) | [F81,F44-OH1.1] |
| 6.3.2.8. Makeup Air |  |
| (1) | [F50,F81-OH1.1] |
|  | [F44,F81-OS3.4] |
| (2) | [F81-OH1.1] |
|  | [F81,F44-OS3.4] |
| (3) | [F81-OH1.2] |
| 6.3.2.9. Supply, Return, Intake and Exhaust Air Openings |  |
| (1) | [F30-OS3.1] |
|  | [F81-OH1.2] |
| (2) | [F81-OH1.1] |
|  | [F81,F44-OS3.4] |
|  | [F41,F44-OH1.1] |
| (3) | [F44,F81-OH1.1] |
|  | [F44,F81-OS3.4] |
| (4) | [F81-OH1.1] |
| (5) | [F82,F81-OH1.1] |
|  | [F82-OS3.4] |
| 6.3.2.10. Exhaust Ducts and Outlets |  |
| (1) | [F44-OH1.1] |
| (2) | [F44-OH1.1] |
| (3) | [F81-OH1.1] |
|  | [F81-OH1.2] |
| (4) | [F81-OH1.1] |
|  | [F81-OH1.2] |
| (5) | [F81-OH1.1] |
| (6) | [F81-OH1.1] |
| (7) | [F81-OS1.1] |
| (8) | [F52-OH1.1] |
|  | [F01-OS1.1] |
|  | [F01-OP1.1] |
| (9) | [F52-OH1.1] |
| (10) | [F81-OH1.1] |
| (11) | [F81,F44-OH1.1] |
|  | [F81,F44-OS1.1] |
| (12) | [F81,F44-OH1.1] |
| (13) | [F81-OH1.2] |
|  | [F81,F44-OH1.1] |
| 6.3.2.11. Return-Air System |  |
| (3) | [F10-OS1.5] |
| 6.3.2.12. Underground Ducts |  |
| (1) | (a) [F44,F81-OH1.2,OH1.3] |
|  | (b) [F44,F81-OH1.1] |
|  | (c) [F44,F81-OH1.1] |
| (2) | [F81-OH1.1,OH1.2,OH1.3] |
| 6.3.2.13. Filters |  |
| (1) | [F80-OS1.1] |
|  | [F80-OP1.1] |
| (2) | [F30-OS3.3] |
|  | [F81,F43-OH1.1] |
| 6.3.2.14. Cleaning Devices |  |
| (1) | [F40,F50-OH1.1] |
| (2) | [F40,F43,F44,F50-OH1.1] |
|  | [F44-OS3.4] |
| 6.3.2.15. Evaporative Heat Rejection Systems |  |
| (1) | [F40,F41,F50-OH1.1] |
| (2) | [F40,F41,F50-OH1.1] |
| (3) | [F40,F41,F50-OH1.1] |
| (4) | [F40,F41,F50-OH1.1] |
| (5) | [F40,F41-OH1.1] |
| (6) | [F40,F41-OH1.1] |
| (7) | [F40,F41-OH1.1] |
| (8) | [F46-OH2.2] |
| (9) | [F41,F44-OH1.1] |
| (10) | [F46,F81-OH2.1] |
| (11) | [F41,F82-OH1.1] |
|  | [F82-OS3.1] |
| 6.3.2.16. Evaporative Air Coolers, Misters, Atomizers, Air Washers and Humidifiers |  |
| (1) | [F44,F50-OH1.1] |
| (2) | [F40,F41,F50-OH1.1] |
| (3) | [F40,F41,F50-OH1.1] |
| (4) | [F40,F41,F50-OH1.1] |
|  | [F40,F41,F50,F82-OH1.1] |
| (5) | [F40,F41,F50-OH1.1] |
| (6) | [F46-OH2.2] |
| 6.3.2.17. Fans and Associated Air-Handling Equipment |  |
| (1) | [F81,F44-OH1.1] |
|  | [F81,F44-OS3.4] |
| (2) | [F81-OH1.1] |
| 6.3.3.1. Requirement for Venting |  |
| (2) | [F40,F44,F50-OH1.1] |
| 6.3.3.2. Masonry or Concrete Chimneys |  |
| (2) | [F01-OS1.1] |
|  | [F01-OP1.1] |
| 6.3.3.3. Metal Smoke Stacks |  |
| (1) | [F01-OS1.1] |
|  | [F01-OP1.1] |
| 6.3.3.4. Access Ladders |  |
| (1) | [F20,F80-OS3.1] |
| (2) | [F30-OS3.1] |
| 6.3.4.2. General Ventilation |  |
| (1) | [F01-OS1.1] |
|  | [F01-OP1.1] |
|  | [F02-OP1.2] |
|  | [F02-OS1.2] [F81,F82-OS1.1] |
| (2) | [F11,F81-OS1.1] |
| 6.3.4.3. Enclosure Exhaust Ventilation |  |
| (1) | (a),(c),(d) [F01-OS1.1] |
|  | (b) [F02-OP1.2] |
|  | (e) [F12-OP1.1,OP1.2] |
|  | (a) [F02-OP1.2] |
|  | (b) [F02-OS1.2] [F81-OS1.1] |
|  | (e) [F12-OS1.1,OS1.2] |
|  | (a) [F02-OS1.2] |
|  | (a) [F01-OS1.1] |
| 6.3.4.4. Enclosure Construction |  |
| (1) | (a) [F02-OS1.2] Applies to portion of Code text: “… be constructed of noncombustible materials …” |
|  | (b) [F02-OP1.2] |
|  | (a) [F02-OP1.2] Applies to portion of Code text: “… be constructed of noncombustible materials …” |
|  | (a) [F80-OS3.4] Applies to portion of Code text: “… be constructed of … materials … chemically resistant to the dangerous goods vapours and particles being exhausted …” |
|  | (b) [F02-OS1.2] [F82-OS1.1] |
|  | (a) [F80-OS1.1] Applies to portion of Code text: “… be constructed of … materials … chemically resistant to the dangerous goods vapours and particles being exhausted …” |
|  | (a) [F01-OS1.1] Applies to portion of Code text: “… be constructed of … materials compatible with … the dangerous goods vapours and particles being exhausted …” |
| (3) | [F02-OS1.2] |
|  | [F02-OP1.2] |
| 6.4.1.2. Appliances Installed Outside the Building |  |
| (1) | [F81-OP1.1] |
|  | [F81-OH1.1] |
|  | [F81-OS1.1] |
| 6.4.2.1. Clearances |  |
| (1) | [F01-OP1.1] |
|  | [F01-OS1.1] |
| 6.4.3.1. Lining or Backing |  |
| (1) | [F01-OS1.1] |
|  | [F01-OP1.1] |
| (2) | [F01-OS1.1] |
| 6.5.1.1. Insulation and Coverings |  |
| (2) | [F20,F30-OS3.2,OS3.4] |
| (3) | [F31-OS3.2] |
| 6.6.1.1. Cooling Units |  |
| (1) | [F43,F81-OS3.4] |
| 6.7.1.1. Piping Materials and Installation |  |
| (1) | [F20-OS3.2,OS3.4] |
| (2) | [F21-OH1.1] |
| (3) | [F20-OS2.2] |
| 6.7.1.2. Clearances |  |
| (1) | [F01-OS1.1] |
|  | [F01-OP1.1] |
| 6.7.1.3. Surface Temperature |  |
| (1) | [F31-OS3.2] |
| 6.7.1.4. Protection |  |
| (1) | [F01-OS1.1] |
|  | [F01-OP1.1] |
| 6.7.2.1. Storage Bins |  |
| (1) | [F30,F31,F43-OS3.2,OS3.4] |
| (2) | [F01-OS1.1] |
|  | [F01-OP1.1] |
| 6.8.1.1. Access Openings |  |
| (1) | [F36-OS3.6] |
| 6.8.1.2. Openings in Air Duct Systems |  |
| (1) | [F81-OH1.1,OH1.2] |
|  | [F81,F44-OS3.4] |
| (2) | [F82-OS1.1] |
| 6.8.1.3. Odour Removal Equipment |  |
| (1) | [F82-OH1.1] |
| (2) | [F82-OH1.1] |
| 6.9.1.2. Hazardous Gases, Dusts or Liquids |  |
| (1) | [F01-OP1.1] |
|  | [F01-OS1.1] |
| (2) | [F01-OS1.1] |
|  | [F01-OP1.1] |
| 6.9.1.3. Commercial Cooking Equipment |  |
| (1) | [F02,F81-OS1.2] |
|  | [F02,F81-OP1.2] |
| 6.9.3.1. Carbon Monoxide Alarms |  |
| (2) | (a),(b),(d) [F44-OS3.4] (c) [F81-OS3.4] |
| (3) | [F44-OS3.4] |
| (4) | [F44-OS3.4] |
| (5) | [F44-OS3.4] |
| 6.9.4.1. Ash Storage Bins |  |
| (1) | [F01-OS1.1] |
|  | [F01-OP1.1] |
| (2) | [F01-OS1.1] |
|  | [F01-OP1.1] |

Notes to Table 6.10.1.1.:

(1) See Parts 2 and 3 of Division A.

Notes to Part 6

Heating, Ventilating and Air-conditioning

A-6.2.1.1.   Good Engineering Practice.

Building Pressurization

New buildings tend to be considerably more airtight than older ones. Consequently, these buildings may have a reduced pressurization requirement compared to the normal requirement in order to limit drafts and provide a reasonable level of comfort.

The humidification and relative pressurization of buildings and individual spaces in buildings can be significant factors in compromising the ongoing performance of the building envelope and other environmental separators.

In new construction, HVAC designers should take this issue into consideration and confer with those responsible for the design of the environmental separators so as to limit unintended effects on the environmental separators. In existing buildings, the ability of the environmental separators to resist or accommodate increases in pressure differential or moisture loading should be considered before changes are made to the HVAC system.

Legionella Control

HVAC designers should either develop a water management plan or complete a formal risk and hazard assessment to determine what measures are required for the control of legionella. The risk and hazard assessment should include inspections of the building and its surroundings to locate potential sources of legionella and to identify equipment or systems that could promote the growth and spread of legionella. The assessment should also evaluate the risk to building occupants that is associated with any identified equipment or systems, taking into account their design, location and operating conditions.

Further information on minimizing the growth and spread of legionella can be found in the following publications:

•   ANSI/ASHRAE 188, “Legionellosis: Risk Management for Building Water Systems,”

•   “Developing a Water Management Program to Reduce Legionella Growth and Spread in Buildings” (U.S. Centers for Disease Control and Prevention, 2017),

•   “Legionella and Legionnaires' Disease: A Policy Overview” (European Agency for Safety and Health at Work, 2011),

•   “Legionella and the Prevention of Legionellosis” (World Health Organization, 2007),

•   “Legionnaires' Disease: Technical Guidance: Part 1: The Control of Legionella Bacteria in Evaporative Cooling Systems, and Part 3: The Control of Legionella Bacteria in Other Risk Systems” (U.K. Health and Safety Executive, 2013), and

•   “Recognition, Evaluation and Control of Legionella in Building Water Systems” (American Industrial Hygiene Association, 2015).

Radon Control

Measures may be necessary to reduce the radon concentration to a level below the guideline specified by Health Canada.

Further information on reducing the indoor concentration of radon can be found in the following Health Canada publications:

•   “Guide for Radon Measurements in Public Buildings (Schools, Hospitals, Care Facilities, Detention Centres),” and

•   “Radon: A Guide for Canadian Homeowners.”

A-6.2.1.2.(1) Outdoor Design Conditions. In the past, the practice of ventilating buildings with outdoor air assumed that the outdoor air was of better quality than the indoor air. It has become evident that the outdoor air in some areas of Canada may not be of an acceptable quality for ventilating buildings unless certain particles and gases are first removed or reduced. In order to manage the air quality of a building’s indoor environment, thus reducing the potential for adverse effects on occupants’ health, the quality of outdoor air for building ventilation purposes must be addressed.

A-6.2.1.4.   Structural Movement. This Article is intended to remind designers and installers of mechanical systems of one aspect of the “good engineering practice” referred to in Article 6.2.1.1.

In determining how to accommodate structural movement, there are two important principles to bear in mind:

•   The prime concern of the British Columbia Building Code is the safety of people in and around the building, as opposed to protection of the mechanical systems and equipment.

•   The nature of the accommodation will vary with the type of movement being considered, taking into account particularly how often the movement is likely to be encountered over the life of the building.

For example, a gas line supported on columns that also support a crane must be installed in such a way that the movement of the columns, which occurs many times daily, does not cause the lines to break, thus creating a hazard. Even if the gas line installation could somehow be designed to break in a non-hazardous manner, it would hardly be recognized as good engineering practice if movement that occurs so frequently could disrupt the operation of the mechanical system.

On the other hand, earthquakes occur far less frequently and it would not be surprising to have a non-critical mechanical system fail as a result of an earthquake. However, even in this situation, the failure must occur in a manner that does not create a hazard to building occupants. For example, heavy mechanical equipment should be properly anchored so that it does not topple on building occupants during an earthquake. The design of the anchors should take into account accelerations consistent with the seismic data given in Appendix C for the location of the building. Part 4 provides guidance on the calculation of the loads such equipment would exert on the building structure during an earthquake; these same loads can be used in designing the anchors.

Some mechanical equipment can be an important component of post-disaster life safety systems. In these cases, the measures needed to accommodate the movements caused by an earthquake become even more critical since failure of the equipment would not be acceptable.

Clearly, complying with this requirement will, in most cases, necessitate close coordination between the mechanical designer and the structural designer.

For additional information on the types of structural movement that may be encountered, see Article 4.1.3.5., Sentence 4.1.3.3.(2) and Subsection 4.1.8.

A-6.2.1.6.(1)   Installation – General. Ducts or pipes without dampers or valves are generally not considered to constitute “equipment” and are therefore not subject to this requirement.

A-6.3.1.1.(5) Ventilation Air Supplied to Suites. The indirect supply of required outdoor ventilation air to normally occupied spaces through corridor pressurization or other indirect systems is not permitted.

A-6.3.1.2.(1)   Ventilation and Venting of Crawl Spaces and Attic or Roof Spaces. The cross-reference to Part 5 pertains to unconditioned and unoccupied crawl spaces, and attic or roof spaces, which are effectively within the building envelope. That is, unconditioned and unoccupied attic or roof spaces are located between the roof deck and roofing above, and the insulation, air barrier system and vapour barrier below. Unconditioned and unoccupied crawl spaces are located between the ground cover below and the insulation, air barrier system and vapour barrier above. Venting of these spaces has implications for the performance of the building envelope rather than having direct effects on indoor conditions. The ventilation of conditioned or occupied crawl spaces and attic or roof spaces must comply with Part 6.

The requirements in Part 5 are stated in terms of loads that must be resisted rather than in terms of building elements. Thus, the Code user will not find explicit references in Part 5 to crawl spaces, or attic or roof spaces. Part 5 makes reference to the need for venting environmental separators, i.e., the dissipation of heat or moisture.

Sentence 6.3.1.2.(1) requires that crawl spaces be ventilated either by natural (above-grade only) or mechanical means. High moisture levels within the crawl space can lead to problems such as the formation of mould, lifting of flooring or long-term damage to structural components.

Crawl space ventilation cannot be expected to correct moisture-related problems caused by other factors like inadequate surface drainage from the foundation walls or improper protection against moisture from the ground. These conditions must be properly addressed so that crawl space ventilation can meet its intended objectives.

Several factors favour the use of mechanical ventilation rather than reliance on natural drafts. Local conditions, such as areas with high water tables, may dictate the need for mechanical ventilation to remove excessive moisture.

Crawl spaces should be maintained at a negative pressure relative to the conditioned area above to prevent the migration of moisture into occupied areas. This can be achieved through the use of an exhaust fan and relying on air transfer through floor penetrations, such as pipes.

A-6.3.1.3.(1)   Storage Garages. Car dealership showrooms are not considered as storage garages.

A-6.3.1.3.(2)   Ventilation of Storage Garages. Storage garages are ventilated to protect occupants from exposure to carbon monoxide and other vehicular exhaust fumes. In certain cases, such as small two- or three-bay storage garages that are used for occasional vehicle storage, and where occupants are not present, carbon monoxide or nitrogen dioxide monitoring devices may be omitted if the ventilation system is interlocked with a local light switch or other controls to ensure continuous system operation whenever the area is occupied. In any event, the ventilation system capacity must be designed to limit the concentrations of carbon monoxide or nitrogen dioxide at or below the prescribed values.

A-6.3.1.5.   Indoor Air Contaminants.

Contaminants of Concern

Indoor air can contain complex mixtures of contaminants of concern such as formaldehyde, legionella, mould and emissions from building materials. While some contaminants may be knowingly introduced—as in the case of processing and manufacturing environments—others may be unintentionally released into indoor environments. “Industrial Ventilation: A Manual of Recommended Practice for Design,” published by the ACGIH, and the “Exposure Guidelines for Residential Indoor Air Quality,” published by Health Canada, are useful references on the control of contaminants in industrial workplace environments and residential settings, respectively. These and other guidelines and manuals should be interpreted while keeping in mind the settings and purposes for which they were developed compared to those to which they will be applied. Note that such documents do not necessarily consider the interactions between various contaminants.

Minimizing the Growth and Spread of Bio-contaminants

Bio-contaminants, such as bacteria, mould, mildew, fungi, viruses, and pollen, can thrive in or be spread by sources like drain pans, spray-water air-washers, contaminated filters, poorly maintained cooling coils, water incursion into ductwork, high humidity and stagnant water, potentially causing a wide range of adverse health effects including respiratory allergic reactions, asthma, and diseases ranging from influenza to legionellosis.

Some of the control measures are as follows:

(a)   Air-handling equipment should be accessible for the maintenance of filters, cooling coils and condensate drain pans located below the cooling coils. Access doors should be large and easy to open to facilitate thorough and regular maintenance.

(b)   If moisture is added to building ventilation air to maintain humidity levels in a designated range, humidifiers that inject steam or water vapour into central air-handling units or main supply ducts are normally used. Injection nozzles should not be located in air-handling unit plenums or ductwork that is insulated with internal fibrous lining. If the lining becomes wet, conditions conducive to the growth and spread of bio-contaminants will result.

(c)   HVAC systems that generate condensate or introduce liquid water into the airstream in the ducts require adequate drainage of excess water and, in some cases, a means of capturing air-entrained water droplets. These measures reduce the potential for bio-contaminants, including legionella, to proliferate in stagnant water and for water droplets containing bio-contaminants to be introduced into the airstream and contaminate the indoor environment. (See also Article 6.3.2.2.)

The above only addresses built-in features of an HVAC system that can help to minimize the growth and spread of bio-contaminants. Even more important than the built-in features is a program of regular maintenance and cleaning of those portions of the system where such growth is likely to occur.

A-6.3.2.2.   Stagnant Water in Drain Pans. It is important to eliminate stagnant water as it can promote the proliferation of disease-causing micro-organisms, such as legionella.

Of particular concern is the potential for legionella bacteria in water to become airborne in water droplets or mist that can be inhaled by humans or can contaminate other water sources or systems.

A-6.3.2.5.   Duct Coverings and Linings. The TIAC “Mechanical Insulation Best Practices Guide” is a comprehensive source of information on the selection, installation and proper use of thermal insulation materials. (Note that Section 4 of this Guide is not included in the scope of this Note as it contains information on proprietary products, which are not within the mandate of the Code.)

A-6.3.2.10.(5) and (6)   Exhausting to Garages. A frequent practice in the design of ventilation systems serving buildings which have associated parking garages is to discharge exhaust air from the building to the garage in order to reduce the cost of heating the garage or reduce the length of the exhaust ducts. However, this practice entails a certain amount of risk since, when the exhaust system is not running, stack effect may turn the exhaust outlets into intakes and exhaust fumes (including carbon monoxide) can be drawn from the garage into the building. Incorporating a backdraft damper at the exhaust outlet provides some additional protection but backdraft dampers are generally not regarded as being very reliable. Therefore this practice is only permitted in very limited circumstances.

A-6.3.2.10.(6)(b)   Air Contaminants. For the purpose of Clause 6.3.2.10.(6)(b), washroom exhaust air is not considered to contain contaminants that would adversely affect the air quality in the storage garage.

A-6.3.2.10.(7) and (8)   Exhaust Ducts Connected to Laundry-Drying Equipment. Clothes dryers are a major cause of fires in buildings often due to a build-up of lint in the system, which then ignites or obstructs the venting or ventilation. Proper cleaning and regular maintenance of lint traps is directly proportional to the ease of access to the lint traps. It is therefore important to ensure that lint traps in multiple installations of laundry-drying equipment are installed in such a way as to allow easy access for inspection, maintenance, repair and cleaning.

A-6.3.2.10.(12)(b)   Operation Diversity Factor. The operation diversity factor has to be assessed for each specific application. Good engineering practice (see Article 6.2.1.1.) design guidelines can provide information on the subject. Figure A-6.3.2.10.(12)(b), which originates from ASHRAE handbooks, provides an example of factors that can be used for general applications.

Figure A-6.3.2.10.(12)(b)

Operation diversity factor

A-6.3.2.15.(5) and (6)   Minimum Distances. Ensuring adequate distance between the air discharge locations of evaporative heat rejection systems and certain outdoor spaces and building components minimizes the potential for contamination of the air of occupiable spaces. For example, if a building's ventilation air intake were located too close to an air discharge location of an evaporative heat rejection system, warm discharge air and associated drift, which could contain biological contaminants, could be introduced to the indoor environment through the air intake.

The minimum distances stated in Sentences 6.3.2.15.(5) and (6) may need to be increased where warranted by local conditions such as prevailing winds, adjacent structures, or special processes being carried out, any of which would make further analysis necessary. (See also Sentence 6.3.3.1.(2).)

A-6.3.2.15.(8) and (9)   Assessment of System and Make-Up Water. The chemical characteristics of the water in the evaporative heat rejection system and of the make-up water should be assessed to select a suitable water treatment system.

A-6.3.2.16.(2)   Prevention of Water Stagnation. Common strategies to prevent water stagnation include flushing, providing an inactivity drain, and periodic activation, even with no load.

A-6.3.2.16.(6)   Assessment of Make-Up Water. The chemical characteristics of the make-up water should be assessed to ensure that any chemicals added to a system referred to in Sentence 6.3.2.16.(1) for precipitation control, disinfection or another purpose will not adversely affect the system.

A-6.3.3.1.(2)   Requirement for Venting. Sentence 6.3.3.1.(2) requires that vented products of combustion from appliances be discharged a minimum distance away from certain outdoor spaces and building components in cases where the vented products could contaminate the air of occupiable spaces. These minimum distances may need to be increased due to local conditions such as prevailing winds, adjacent structures, special processes being carried out, specific contaminants or effluent discharges, all of which would require further analysis.

“Occupiable outdoor spaces” refers to areas that could be occupied for a duration of more than fifteen minutes at any time, but does not include maintenance spaces. Occupiable outdoor spaces are located adjacent to an indoor space and are considered to be an extension of this indoor space: e.g. main entries, balconies, patios, decks, green roofs and other public assembly areas. Although sidewalks and driveways are mentioned in the provision, these areas are not considered as occupiable outdoor spaces since they are used as transport routes to and from the building, and people are not expected to remain there for extended periods of time.

The requirements of Sentence 6.3.3.1.(2) are not meant to override similar requirements found in the installation standards referenced in Article 6.2.1.5. that address identical situations.

A-6.5.1.1.(3)   Temperature of Exposed Piping. Piping carrying steam, high-temperature hot water, or another heat transfer fluid at high temperature is usually insulated to reduce heat losses as an economy measure. Above a temperature of approximately 52°C, however, a bare pipe can cause a burn to human skin coming in contact with the pipe. According to ASTM C1055, “Standard Guide for Heated System Surface Conditions that Produce Contact Burn Injuries,” skin can be in contact with a surface at a temperature of 52°C for up to 60 s without experiencing irreversible damage. If pipes above this temperature are normally out of reach of all persons other than maintenance personnel or are properly guarded, it would be expected that no insulation would be needed for public safety.

A-6.9.1.2.(1)   NFPA Publications Pertaining to the Heating, Ventilating and Air-Conditioning of Spaces Containing Hazardous Gases, Dusts or Liquids.

NFPA 30, “Flammable and Combustible Liquids Code”

NFPA 30A, “Code for Motor Fuel Dispensing Facilities and Repair Garages”

NFPA 32, “Standard for Drycleaning Facilities”

NFPA 33, “Standard for Spray Application Using Flammable or Combustible Materials”

NFPA 34, “Standard for Dipping, Coating, and Printing Processes Using Flammable or Combustible Liquids”

NFPA 35, “Standard for Manufacture of Organic Coatings”

NFPA 36, “Standard for Solvent Extraction Plants”

NFPA 40, “Standard for the Storage and Handling of Cellulose Nitrate Film”

NFPA 51, “Standard for the Design and Installation of Oxygen-Fuel Gas Systems for Welding, Cutting, and Allied Processes”

NFPA 51A, “Standard for Acetylene Cylinder Charging Plants”

NFPA 55, “Compressed Gases and Cryogenic Fluids Code”

NFPA 61, “Standard for the Prevention of Fires and Dust Explosions in Agricultural and Food Processing Facilities”

NFPA 68, “Standard on Explosion Protection by Deflagration Venting”

NFPA 69, “Standard on Explosion Prevention Systems”

NFPA 85, “Boiler and Combustion Systems Hazards Code”

NFPA 86, “Standard for Ovens and Furnaces”

NFPA 88A, “Standard for Parking Structures”

NFPA 91, “Standard for Exhaust Systems for Air Conveying of Vapors, Gases, Mists, and Particulate Solids”

NFPA 96, “Standard for Ventilation Control and Fire Protection of Commercial Cooking Operations”

NFPA 204, “Standard for Smoke and Heat Venting”

NFPA 303, “Fire Protection Standard for Marinas and Boatyards”

NFPA 307, “Standard for the Construction and Fire Protection of Marine Terminals, Piers, and Wharves”

NFPA 409, “Standard on Aircraft Hangars”

NFPA 415, “Standard on Airport Terminal Buildings, Fueling Ramp Drainage, and Loading Walkways”

NFPA 484, “Standard for Combustible Metals”

NFPA 654, “Standard for the Prevention of Fire and Dust Explosions from the Manufacturing, Processing, and Handling of Combustible Particulate Solids”

NFPA 655, “Standard for Prevention of Sulfur Fires and Explosions”

NFPA 664, “Standard for the Prevention of Fires and Explosions in Wood Processing and Woodworking Facilities”

NFPA “Fire Protection Guide to Hazardous Materials”

A-6.9.3.1.(2)(c)   Carbon Monoxide Alarms. Battery-powered carbon monoxide alarms are acceptable provided that they are installed as recommended by the manufacturer.

A-6.9.3.1.(6) Carbon Monoxide Devices. Although the scope of CAN/CSA-6.19, “Residential Carbon Monoxide Alarming Devices,” and UL 2034, “Standard for Single and Multiple Station Carbon Monoxide Alarms,” is limited to carbon monoxide alarms for residential applications, their use may be appropriate in some other locations where they are not subject to excessive contaminants or risk of damage, such as in classrooms and meeting spaces. The designer is also given the option to follow good engineering practice. For example, some carbon monoxide devices used in storage garages may be suitable for use in other applications.

A-6.9.3.1.(7) Spaces Served by a Fuel-Burning Appliance. Where a fuel-burning appliance such as a furnace circulates or distributes air to a space there is the potential for leakage of combustion products into the duct system which could then circulate combustion products including carbon monoxide (CO) to that space, so a CO alarm is required to protect occupants of that space. Fuel-burning appliances such as a boiler do not have the same potential of the system circulating or distributing CO to the spaces served via the piping system. In both examples of a fuel-burning furnace and a fuel-burning boiler, a CO alarm is required in the service room containing the appliances.

A-6.9.3.1.(8) Adjacent Suites. Suites that share a common attic or crawl space with a storage garage or service room, as well as suites that share a common wall or floor/ceiling assembly with a storage garage or service room are considered adjacent for the application of Sentence (8).

Part 7

Plumbing Services

Section  7.1.   General

7.1.1. Scope

7.1.1.1. Scope

1)   The scope of this Part shall be as described in Subsection 1.3.3. of Division A.

7.1.1.2. Application

1)   This Part applies to the design, construction, extension, alteration, renewal or repair of plumbing systems.

7.1.2. Design and Installation

7.1.2.1. Conformance

1)   Every plumbing system shall be designed and installed in conformance with the British Columbia Building Code Book II (Plumbing Systems), that being the National Plumbing Code of Canada.

2)   References to the following documents in the British Columbia Building Code Book II (Plumbing Systems) shall be replaced as follows:

a)   references to the National Building Code of Canada and the National Energy Code of Canada for Buildings shall be replaced with the British Columbia Building Code, and

b)   references to the National Fire Code of Canada shall be replaced with the British Columbia Fire Code.

3)   Compliance with the British Columbia Building Code Book II (Plumbing Systems) may be achieved using alternative solutions as described in Clause 1.2.1.1.(1)(b) of Division A of this Code, using the objectives and functional statements attributed to the applicable acceptable solutions in Division B of the British Columbia Building Code Book II (Plumbing Systems).

4)   Notwithstanding Sentence (1), a water closet with a dual flush cycle of 6.0 L and 4.1 L or less is deemed to comply with Sentence 2.6.1.6.(3) and Table 2.6.2.6. of Division B of the British Columbia Building Code Book II (Plumbing Systems).

7.1.3. Required Facilities

7.1.3.1. All Buildings Except Dwelling Units

1)   Buildings shall be equipped with plumbing facilities as required in Subsection 3.7.2. and Article 3.8.2.8.

7.1.3.2. Dwelling Units

1)   Dwelling units shall be equipped with plumbing facilities as required in Section 9.31.

7.1.4. Definitions

7.1.4.1. Defined Terms

1)   Words that appear in italics are defined in Article 1.4.1.2. of Division A.

Section  7.2.   Objectives and Functional Statements

7.2.1. Objectives and Functional Statements

7.2.1.1. Attributions to Acceptable Solutions

1)   For the purpose of compliance with this Code as required in Clause 1.2.1.1.(1)(b) of Division A, the objectives and functional statements attributed to the acceptable solutions in this Part shall be the objectives and functional statements listed in Table 7.2.1.1. (See Note A-1.1.2.1.(1).)

Table 7.2.1.1.

Objectives and Functional Statements Attributed to the Acceptable Solutions in Part 7

Forming Part of Sentence 7.2.1.1.(1)

| Provision | Functional Statements and Objectives(1) |
| --- | --- |
| 7.1.2.1. Conformance with Regulations or National Plumbing Code |  |
| (1) | [F30-OS3.1] [F31-OS3.2] [F43-OS3.4] |
|  | [F70-OH2.2] [F72-OH2.1] |

Notes to Table 7.2.1.1.:

(1) See Parts 2 and 3 of Division A.

Part 8

Safety Measures at Construction and

Demolition Sites

Section  8.1.   General

8.1.1. Scope

8.1.1.1. Scope

1)   The scope of this Part shall be as described in Subsection 1.3.3. of Division A.

2)   This Part applies to fire safety and the protection of the public during the construction, alteration or demolition of every building, including any incompleted or abandoned building.

3)   Fire safety at construction and demolition sites shall conform to Section 5.6. of Division B of the British Columbia Fire Code.

8.1.1.2. Definitions

1)   Words that appear in italics are defined in Article 1.4.1.2. of Division A.

8.1.1.3. Demolition Procedures

1)   Measures shall be taken during demolition to protect the public in conformance with Section 5.6. of Division B of the British Columbia Fire Code.

8.1.2. Application

8.1.2.1. Application

1)   Where a building is undergoing construction, alteration or demolition, measures shall be taken at the building site in conformance with this Code. (See Note A-8.1.2.1.(1).)

8.1.2.2. Protection from Risk

1)   Precautions shall be taken to ensure that no person is exposed to undue risk.

Section  8.2.   Protection of the Public

8.2.1. Fencing and Barricades

8.2.1.1. Covered Way Exceptions

1)   Where the construction may constitute a hazard to the public, work shall not commence on the construction, alteration or repair of a building until a covered way has been provided as described in Article 8.2.1.2. to protect the public, except where

a)   the work is done within a solid enclosure,

b)   the building is at a distance of 2 m or more from a public way used by pedestrians, or

c)   site conditions warrant a distance greater than provided in Clause (b).

8.2.1.2. Covered Way Construction

1)   A covered way shall

a)   have a clear height of not less than 2.5 m,

b)   have a clear width of not less than 1.5 m or the width of the public way, whichever is the lesser,

c)   be designed and constructed to support safely all loads that may be reasonably expected to be applied to it, but in no case less than 2.4 kPa on the roof,

d)   have a weathertight roof sloped towards the site or, if flat, be equipped with a splash board not less than 300 mm high on the street side,

e)   be totally enclosed on the site side with a structure having a reasonably smooth surface facing the public way,

f)   have a railing 1 070 mm high on the street side where the covered way is supported by posts on the street side, and

g)   be adequately lighted when the public way is lighted.

8.2.1.3. Fencing, Boarding or Barricades

1)   When a construction or demolition activity may constitute a hazard to the public and is located 2 m or more from a public way, a strongly constructed fence, boarding or barricade not less than 1.8 m high shall be erected between the site and the public way or open sides of a construction site.

2)   Barricades shall have a reasonably smooth surface facing the public way and shall be without openings, except those required for access.

3)   Access openings through barricades shall be equipped with gates that shall be

a)   kept closed and locked when the site is unattended, and

b)   maintained in place until completion of the construction or demolition activity.

8.2.1.4. Special Hazards

1)   Where any special hazard exists from which it is not possible to protect the public by other means, persons shall be employed to prevent the public from entering the danger zone at any time of the day or night.

8.2.1.5. Work Shutdown

1)   When work on a construction site is suspended or ceases so that it will not be occupied during normal working hours, the hazardous part of the construction site shall be protected by

a)   covering all windows, doors and other openings located within 3 m of the ground which may give access to the building with a securely fastened barricade, or

b)   a fence or barricade constructed according to the requirements of Article 8.2.1.3.

8.2.2. Excavation

8.2.2.1. Water Removal

1)   Excavations shall be kept reasonably clear of water.

8.2.2.2. Protection of Adjoining Property

1)   If the stability of adjoining buildings may be endangered by the work of excavating, adequate underpinning, shoring and bracing shall be provided to prevent

a)   damage to, or movement of, any part of the adjoining building, and

b)   the creation of a hazard to the public.

8.2.3. Use of Streets or Public Property

8.2.3.1. Safe Passage Past Site

1)   Except as provided in Article 8.2.3.2., provisions shall be made at all times for the safe passage of pedestrian and vehicular traffic past the site.

2)   Material or equipment shall not be placed on any street or other public property except as authorized.

3)   Except as provided in Sentence (4), where a sidewalk exists adjacent to the site it shall be kept clear of obstructions at all times.

4)   Where construction operations necessitate the obstruction of a sidewalk, a temporary sidewalk shall be provided and it shall be kept clear of obstruction at all times.

8.2.3.2. Overhead Activities

1)   Operations such as the hoisting of major components onto a tall building or other overhead activities that constitute a hazard to pedestrians below from which the public cannot be protected by barricades, covered ways or similar means shall not be carried out until the street or other public way is closed.

8.2.3.3. Barricades

1)   Excavations in streets or public property shall

a)   be adequately barricaded, and

b)   have warning signs or lights installed on each section of the barricades referred to in Clause (a).

8.2.3.4. Restoration and Repair

1)   All sidewalks, streets or other public property that have been damaged shall be restored to a safe condition.

2)   All obstructions on sidewalks, streets or other public property shall be removed when the need for such obstructions is ended.

8.2.3.5. Warning Lights

1)   Warning lights shall be placed and shall be in operation during the hours of darkness at all obstructions on streets or other public ways.

8.2.4. Direction of Vehicular Traffic

8.2.4.1. Hazards to Vehicular Traffic

1)   Where a hazard to vehicular traffic on a public way is created by work on a construction site, the following shall be provided to direct the traffic:

a)   one or more workers,

b)   warning signs,

c)   barriers,

d)   lane control devices, or

e)   flashing lights or flares located at a suitable distance from the hazard.

8.2.4.2. Flags Used for Directing Traffic

1)   A flag used to direct traffic shall be

a)   red,

b)   not less than 450 mm by 500 mm,

c)   mounted on a staff not less than 1 m long, with the long side of the flag attached securely to the staff along its entire length, and

d)   maintained in a clean and untorn condition when being used.

8.2.4.3. Signs Used for Directing Traffic

1)   A sign used to direct traffic shall be

a)   diamond-shaped and of material not less rigid than 6 mm thick plywood,

b)   not less than 450 mm by 450 mm in size and mounted at one corner on a substantial pole not less than 1.2 m long,

c)   red on one side with black corner areas so that the red area is a regular 8-sided figure, and with the word “STOP” in clearly distinguishable white letters not less than 150 mm high located centrally on the sign,

d)   yellow on the other side with the word “SLOW” in clearly distinguishable black letters not less than 150 mm high located centrally on the sign, or symbols recognized by the International Traffic Code, and

e)   maintained in a clean condition when being used.

8.2.4.4. Worker Directing Traffic

1)   A worker who is directing traffic shall

a)   be equipped as required by Article 8.2.4.5.,

b)   be instructed in the signals to be used in controlling traffic,

c)   be provided with a copy of written instructions on the correct methods for traffic direction, and

d)   direct traffic by using either a flag or sign.

8.2.4.5. Clothing While Directing Traffic

1)   A worker while directing traffic shall wear the following clothing which shall be fluorescent and coloured either blaze orange or red:

a)   a vest, or

b)   sleeves that extend from above the elbow to the wrist.

8.2.5. Waste Material

8.2.5.1. Control of Waste Material

1)   Waste material or other material shall not be permitted to fall freely from one storey to another.

8.2.5.2. Removal of Waste Material

1)   Waste material shall be removed as quickly as possible by means of

a)   appropriate containers,

b)   an enclosed shaft or chute conforming to Sentence 8.2.5.4.(1), or

c)   a hoisting apparatus if large pieces or objects are involved.

8.2.5.3. Enclosures for Waste Material

1)   Waste material cleared as provided in Sentence 8.2.5.2.(1) shall be deposited in an enclosure

a)   so arranged as to prevent waste material from being projected beyond the confines of the enclosure, and

b)   not accessible to the public.

8.2.5.4. Chutes for Waste Material

1)   The chute described in Clause 8.2.5.2.(1)(b) shall be closed if it is inclined more than 45° to the horizontal.

Section  8.3.   Objectives and Functional Statements

8.3.1. Objectives and Functional Statements

8.3.1.1. Attributions to Acceptable Solutions

1)   For the purpose of compliance with this Code as required in Clause 1.2.1.1.(1)(b) of Division A, the objectives and functional statements attributed to the acceptable solutions in this Part shall be the objectives and functional statements listed in Table 8.3.1.1. (See Note A-1.1.2.1.(1).)

Table 8.3.1.1.

Objectives and Functional Statements Attributed to the Acceptable Solutions in Part 8

Forming Part of Sentence 8.3.1.1.(1)

| Provision | Functional Statements and Objectives(1) |
| --- | --- |
| 8.1.1.3. Demolition Procedures |  |
| (1) | [F01-OS1.1] |
|  | [F30-OS5.1,OS5.3,OS5.8] [F34-OS5.5] [F31,F32,F43,F44-OS5.6] |
| 8.1.2.2. Protection from Risk |  |
| (1) | [F01-OS1.1] |
|  | [F30-OS5.1,OS5.3,OS5.8] [F34-OS5.5] [F31,F32,F43,F44-OS5.6] |
| 8.2.1.2. Covered Way Construction |  |
| (1) | (a),(b),(d) to (g) [F30-OS5.1,OS5.2] [F34-OS5.5] |
|  | (c) [F20-OS5.7] |
| 8.2.1.3. Fencing, Boarding or Barricades |  |
| (1) | [F30-OS5.1,OS5.3,OS5.6] [F34-OS5.5] |
| (2) | [F34-OS5.5] [F30-OS5.3] |
| (3) | [F34-OS5.5] |
| 8.2.1.4. Special Hazards |  |
| (1) | [F34-OS5.5] |
| 8.2.1.5. Work Shutdown |  |
| (1) | [F34-OS5.5] |
| 8.2.2.1. Water Removal |  |
| (1) | [F60-OS5.8] |
|  | [F60-OS5.4] |
| 8.2.2.2. Protection of Adjoining Property |  |
| (1) | (a) [F21-OP4.1] |
|  | (b) [F21-OS5.8] |
| 8.2.3.1. Safe Passage Past Site |  |
| (1) | [F30-OS5.1,OS5.3,OS5.2] |
| (2) | [F30-OS5.3,OS5.2] |
| (3) | [F30-OS5.3,OS5.2] |
| (4) | [F30-OS5.3,OS5.2] |
| 8.2.3.2. Overhead Activities |  |
| (1) | [F30-OS5.1] |
| 8.2.3.3. Barricades |  |
| (1) | [F30-OS5.1,OS5.3,OS5.2] [F34-OS5.5] |
| 8.2.3.4. Restoration and Repair |  |
| (1) | [F30-OS5.3] |
| (2) | [F30-OS5.3,OS5.2] |
| 8.2.3.5. Warning Lights |  |
| (1) | [F30-OS5.3,OS5.2] |
| 8.2.4.1. Hazards to Vehicular Traffic |  |
| (1) | [F30-OS5.2] |
| 8.2.4.2. Flags Used for Directing Traffic |  |
| (1) | [F30-OS5.2] |
| 8.2.4.3. Signs Used for Directing Traffic |  |
| (1) | [F30-OS5.2] |
| 8.2.4.4. Worker Directing Traffic |  |
| (1) | [F30-OS5.2] |
| 8.2.4.5. Clothing While Directing Traffic |  |
| (1) | [F30-OS5.2] |
| 8.2.5.1. Control of Waste Material |  |
| (1) | [F30-OS5.1] |
| 8.2.5.2. Removal of Waste Material |  |
| (1) | [F30-OS5.1,OS5.3] |
| 8.2.5.3. Enclosures for Waste Material |  |
| (1) | [F30-OS5.1,OS5.3] [F34-OS5.6] |
| 8.2.5.4. Chutes for Waste Material |  |
| (1) | [F30-OS5.1] |

Notes to Table 8.3.1.1.:

(1) See Parts 2 and 3 of Division A.

Notes to Part 8

Safety Measures at Construction and

Demolition Sites

A-8.1.2.1.(1)   Application. The use of streets or public property and vehicular traffic during construction or demolition is normally controlled by regulations of authorities other than the building department (e.g., police department).